BUILDING CONSTRUCTION DEPARTMENT

BIHAR PATNA

Housekeeping, Operation and Maintenance of Type A & B Premises, Gardanibagh, Patna for 5 years

MODEL SCOPE OF WORK CUM OPERATIONAL MANUAL

(Technical Specifications, Field Execution Guidelines, and Service Level Agreement (SLA) Penalty Framework)

Operational Enforcement Summary

This Integrated Facility Management Services Operational Manual outlines the post-award technical execution standards required under this contract. The operational instructions, task matrices, response windows, and specific penalty schedules contained herein shall be strictly enforced by the Engineer-in-Charge to audit performance and determine monthly service payments.

Contents

SECTION 1	:	Housekeeping Services for Outdoor Campus & Common

Areas

SECTION 2	:	Comprehensive Operation and Maintenance of STP and

WTP

SECTION 3	:	Security Services, Front Desk, & Tower Caretaking

Management.

SECTION 4	:	Comprehensive Horticulture & Landscape Management

SECTION 5	:	Comprehensive Pest Control & Vector Management Services

SECTION 6	:	Operation & Maintenance of Firefighting & Fire Alarm

Systems.

SECTION 7	:	Technical Maintenance Services, Manpower Deployment &				Statutory Framework

SECTION 8	:	Comprehensive Electrical Substation, Power Distribution &				Housing Electrification Management

SECTION 1

Housekeeping Services for Outdoor Campus & Common Areas

1.1 	Scope of Work

The contractor shall execute comprehensive, mechanized cleaning, sanitization, and waste management operations across all outdoor campus spaces and common areas residential building elements. The technical and physical boundaries of this scope comprise:

- Peripheral & Transit Infrastructure: All peripheral roads, interlocking paver pathways, pedestrian footpaths, stormwater drains, box culverts, basement & external open parking bays, driveways, perimeter walls, and gate plazas.

- Tower Common Building Elements: Tower ground lobbies, lift entrance bays, security reception desks, lift cars (interior stainless-steel walls, car ceilings, floors, mirror surfaces, control panels, exhaust fan vents), multi-floor common corridors, fire escape staircases, main staircases, mid-landings, fire-refuge balconies, service utility rooms, vertical engineering utility shaft ducts, and common horizontal open terrace roofs.

- Basement Infrastructure: Covered basements, transition approach ramps, drainage collection sumps, storage bays, and utility sub-stations.

- Public Restrooms & Washing Facilities: Restrooms within the estate administrative office, guard houses, community centres, drivers' lounges, common washing bays, and utility pump rooms.

- Centralized Solid Waste Operations: Emptying waste from all public bins, manual sorting into separate wet organic and dry recyclable streams, and moving segregated garbage to the estate’s centralized waste yard for municipal clearing.

1.2 	Operational Execution Guidelines

Do's

- Mechanized Standards: Clean common tower lobbies using high-speed commercial single-disc scrubbing machines. Clean large outdoor roads and basement floors using manual means or automatic scrubbers.

- Color-Coded Implements: Enforce color-coded microfiber tools to prevent cross-contamination: Red exclusively for toilet bowls and urinals; Yellow for washbasins, bathroom mirrors, and restroom walls; Blue for common area glass panels, partition windows, and high-gloss panels; Green for general common area hard floor surfaces, shelves, and handrails.

- Standard Chemical Lines: Use eco-friendly, non-acidic cleaning chemicals that comply with existing environmental guidelines:

  - Surface Disinfectant (Floor & Multi-surface): Industrial neutral floor cleaner at 20 ml/L dilution for manual mopping and automated machine scrubbing.

  - Glass Cleaner: Concentrated glass cleaner for all architectural glass, internal glazing, and mirrors.

  - Wood Cleaner/Polish: Oil-in-water furniture emulsion to polish panelling and wooden counters.

  - Toilet Bowl Sanitizer: Acidic toilet descaler for removing hard-water rings and uric acid scale from vitreous sanitary fixtures.

- Safety Signalling: Place highly visible "Wet Floor / Work in Progress" A-frame safety signs at both entry points of a corridor, staircase, or lobby before starting any wet cleaning.

- Clear Emergency Access: Keep all fire escape staircases, vertical shaft access panels, lift landing paths, and building egress paths completely clear of cleaning carts, equipment, or collected debris.

Don'ts

- Prohibit Abrasive Material: Never use steel wire brushes, coarse steel wool, or unbuffered abrasive cleaning pads on marble, granite, or vitrified tiles to avoid scratching and dulling the finish.

- Prohibit Raw Acidic Chemicals: Do not use raw, unbuffered hydrochloric acid or industrial-grade bleaching powders on stone surfaces or stainless-steel bathroom fittings to prevent chemical burns and blackening.

- Prohibit Indoor Dry Sweeping: Avoid dry broom sweeping inside building interiors, common lobbies, and residential corridors. Use electrostatic dust-attracting acrylic mops to prevent dust from becoming airborne and settling on walls.

- Prohibit Standing Water Hazards: Do not leave puddles or standing water on common area floors, staircase steps, or lift landings. Squeegee and damp-mop surfaces completely dry to eliminate slipping hazards.

1.3 	Granular Task Frequency Matrix

| Area | Activity | Frequency | Execution Methodology | Quality Standard |
| --- | --- | --- | --- | --- |
| Peripheral Roads & Paver Paths | Sweeping & collection of loose debris. | Daily (Morning) | Use long-handled road brooms for initial sweeping; pick up leaves, dust, and litter with wide collection bins. | Surface must be free of loose soil, dead leaves, plastic trash, and visible dust mounds. |
| Common Multi-Floor Corridors | Dust-mopping and localized damp-mopping. | Daily sweeping; Weekly deep washing | Run electrostatic dry mops along corridors; spot-clean stains using flat mops and dual-bucket wringer trolleys. | Zero dust borders along wall skirtings; uniform surface texture. |
| Staircases & Mid-landings | Sweeping, handrail sanitization, and washing. | Daily sweeping; Weekly deep washing | Sweep down with hair brooms; wipe handrails with sanitizer cloth; weekly washing with water jets and wet vacuums. | Stair treads free of grit; handrails grease-free with no sticky film or cobwebs. |
| Common Toilets & Washrooms | Deep scrubbing, descaling, and restocking. | Two times daily | Scrub WC bowls; clean tiles; polish fixtures; restock paper, tissues, and liquid soap. | Total absence of urine or musty odours; stain-free sanitary ware. |
| Basements & Covered Parking | Mechanized floor scrubbing and washing. | Weekly (Sundays) | Pre-treat oil patches with industrial degreasers; run ride-on automatic scrubbers across the entire floor. | Zero standing water or grey slurry layers; elimination of tire track marks. |
| Horizontal Terraces & Roofs | Debris extraction and drainage cleaning. | Weekly (Mondays) | Manually gather biomass, soil silt, and plastic trash; clear all rainwater down-take pipe gratings. | Zero water stagnation risks during heavy rain; clear down-take pipes. |
| Glass Windows & Facades (Low Reach) | Squeegee wash and structural frame wiping. | Monthly | Spray solution; pull dry with professional window squeegees; wipe aluminium frames with damp cloths. | Streak-free clarity; zero watermark spots or bird droppings on glass surfaces. |

1.4 	Grievance Redressal

Definitions of Bad Execution / Service Failure

- Presence of loose litter, dead leaves, or overflowing public trash bins beyond specified execution hours.

- Accumulation of dust, cobwebs, smudge marks, or chewing tobacco stains on staircase handrails, walls, or lift panels.

- Foul odour emanating from common toilets, dirty washbasins, or missing hand soaps/tissues during audits.

- Water tracking or pooling on lobby floors without caution signage or immediate dry-mopping.

- Failure to sort municipal solid waste into distinct streams at the centralized yard.

Response & Resolution Windows

- Critical Faults (Spills, blocked restroom drainage, overflowing trash): Acknowledgment within 1 hour; full resolution within 4 hours.

- Routine Faults (Corridor dust borders, dirty terrace drains, unpolished fixtures): Acknowledgment within 4 hours; full resolution within 24 hours.

Itemized Payment Deduction Schedule

- Failure to clear a reported critical spill/blockage within stipulated time: Deduct ₹500 per instance per hour of continued delay.

- Missed daily sweeping or mopping cycle in a building tower (per floor/corridor): Deduct ₹1,500 per tower per day from the monthly running bill.

- Audit finding of dirty sanitary fixtures or persistent odour in public washrooms: Deduct ₹1,000 per washroom per day.

- Failure to provide mandated caution signage during floor mopping cycles: Deduct ₹300 per incident.

- Improper sorting or storage of municipal solid waste at the transit yard: Deduct ₹2,000 per daily occurrence.

SECTION 2

Comprehensive Operation and Maintenance of STP and WTP

2.1 	Scope of Work

The contractor shall manage the round-the-clock (24*7) operation, diagnostic analysis, chemical dosing adjustments, preventive servicing, and emergency repair of the Sewage Treatment Plant (STP) and Water Treatment Plant (WTP). The technical scope of the plants includes:

- STP Processing Units: Bar screen inlet chambers, grease/oil separation traps, equalization tanks, sewage transfer pumps, biological aeration tanks, air blowers, clarifier settling mechanisms, sludge storage tanks, filter feed systems, Multi-Grade Sand Filters (MGF), Activated Carbon Filters (ACF), and treated effluent storage networks.

- WTP Processing Units: Raw groundwater intake systems, chemical pre-treatment units (Alum/Anti-scalant dosing), coagulation/settling units, pressure filtration beds, ultrafiltration networks, water softeners, chemical regeneration systems, and clean water distribution lines.

- Quality & Environmental Parameters:

  - STP Output Effluent: Adheres strictly to existing government guidelines for landscaping and flushing use (BOD<10mg/L, COD<50mg/L, TSS<10mg/L, pH between 6.5 and 8.5).

  - WTP Potable Supply: Adheres to domestic supply guidelines (IS:10500 standards, with residual chlorine maintained at 0.2-0.5\ppm).

2.2 	Operational Execution Guidelines

Do's

- Maintain Detailed Logs: Record suction/delivery pressures, current draw (amperage), line voltage, cumulative flow totalizers, and pump running hours in the plant logbook every two hours.

- Control Aeration Dissolved Oxygen: Maintain the dissolved oxygen (DO) concentration in the biological aeration tank strictly between 2.0 and 3.0mg/L. Regulate DO levels by adjusting the air output valves on the rotary blowers.

- Follow Filter Cleaning Procedures: Perform a full backwash and rinse cycle on the sand and carbon filters daily, or whenever the differential pressure gauge across a filter bed exceeds 0.5kg/cm.

- Enforce Safety Equipment Rules: Require plant operators to wear appropriate personal protective equipment (PPE)—including face shields, thick nitrile chemical gloves, rubber boots, and aprons—when mixing or handling water treatment chemicals.

- Complete Regular Lab Tests: Take monthly treated water samples from the plant and submit them to a NABL-accredited or BSPCB-approved laboratory for independent chemical testing.

Don'ts

- No Bar Screen Bypasses: Do not bypass the inlet bar screen or allow raw, unscreened sewage directly into the equalization tank, as large debris can damage downstream pumps.

- Avoid Pump Dry-Running: Never run horizontal centrifugal or vertical multistage pumps dry. Test low-level float switches in supply tanks regularly to ensure automatic cut-offs function correctly.

- No Untreated Sludge Dumping: Do not dump wet biological sludge into municipal stormwater lines or open campus grounds. Process all sludge through the filter press to create dried cakes suitable for landscaping fertilizer.

- Avoid Excess Chemical Dosing: Do not add too much sodium hypochlorite to the system. Keep residual chlorine levels below 0.5ppm to prevent pipe corrosion and resident complaints about strong chemical odours.

2.3 	Granular Task Frequency Matrix

| Component | Activity | Frequency | Execution Methodology | Quality Standard |
| --- | --- | --- | --- | --- |
| STP Bar Screens | Manual raking and solid waste extraction. | Thrice Daily | Use stainless-steel rakes to pull trapped debris up the screen grid; place waste into sealed bags for immediate removal. | Screen grid must be clear of blockages; raw sewage must flow smoothly with no backup in the sewer lines. |
| Pumps & Electric Motors | Diagnostic tracking and surface cleaning. | Every 2 Hours | Read and log voltage/current metrics; check for excessive motor vibration and measure bearing housing temperatures. | Current draw must be within faceplate ratings; zero overheating or erratic noise. |
| Sand & Carbon Filters | Backwash, rinse, and forward filtration setup. | Daily | Reverse flow water through filter vessels to flush out trapped particulates; rinse until the sight glass shows clear water. | Differential pressure stabilized below 0.2kg/cm; treated water turbidity< 1NTU. |
| Chemical Dosing Stations | Solution mixing and stroke rate adjustment. | Daily | Mix specified amounts of Sodium Hypochlorite or Alum with soft water in dosing tanks; check pump stroke rates. | Continuous chemical delivery matched to water inflow rates; no air locks in lines. |
| Plant Process Testing | Field testing of pH, TDS, and chlorine levels. | Daily | Take water samples from raw, intermediate, and treated lines; analyse using calibrated portable electronic meters. | Records must be updated daily; residual chlorine maintained at 0.2-0.5ppm. |
| Biological Aeration Tank | Mixed Liquor Suspended Solids (MLSS) evaluation. | Twice Weekly | Take a 1litre sample from the aeration tank; measure the sludge settling volume after 30 minutes (V30). | MLSS maintained at 2500-3500mg/L; SV30 ratio between 30 and 45%. |
| Sludge Filter Press | Dewatering and dry cake processing. | Twice Weekly | Pump concentrated sludge from the holding tank into the plate press; compress until dry cakes form; extract the cakes. | Moisture content of sludge cakes low enough to prevent dripping; clean filtrate returned to the system. |
| Effluent Lab Analysis | Complete environmental parameter audit. | Monthly | Collect water samples in sterile containers; ship under refrigeration to an independent lab for BOD/COD/TSS testing. | Lab certificate must show parameters well within current BSPCB discharge guidelines. |

2.4 	Grievance Redressal

Definitions of Bad Execution / Service Failure

- Interruption of domestic or flushing water supply to residential towers caused by operational failure or human error.

- Water sample failures (high turbidity, low/high residual chlorine, faecal coliform presence, bad odour).

- Aeration tank biological shock caused by inadequate oxygen management or chemical dosing errors.

- Overflowing sludge or untreated wastewater leaking into the surrounding environment or surface stormwater lines.

- Missing statutory operational entries, missing chemical logbooks, or keeping low inventories of dosing chemicals (<15days).

Response & Resolution Windows

- Critical Faults (Total tower supply breakdown, sewage leak, biological shock): Immediate response within 15 minutes; temporary backup water activated within 1 hour; full technical resolution within 4 hours.

- Routine Faults (Faulty secondary dosing unit, gauge line leak, clogged screen frame): Acknowledgment within 45 minutes; full technical resolution within 12 hours.

Itemized Payment Deduction Schedule

- Downtime in tower domestic water supply due to operator failure: Deduct ₹5,000 per hour of supply failure.

- Discharging treated water with parameters outside BSPCB guidelines: Deduct ₹10,000 per day of non-compliance, plus the contractor must cover any regulatory fines.

- Failure to perform daily sand/carbon filter backwashing loops: Deduct ₹3,000 per missed cycle.

- Allowing sewage or sludge to overflow from plant process vessels: Deduct ₹4,000 per incident.

- Operating with less than a 15-day inventory of essential water treatment chemicals: Deduct ₹2,500 per day of low stock.

SECTION 3

Security Services, Front Desk, & Tower Caretaking Management

3.1 	Scope of Work

The contractor shall deploy a trained security, reception, and caretaking team to manage access control, protect property assets, coordinate visitor logistics, and monitor emergencies across the entire residential campus. The operational boundaries include:

- Perimeter Access Control Points: Main vehicular gate structures, emergency exits, pedestrian access paths, mechanical boom barriers, etc.

- Tower Reception Desks: Ground floor reception lobbies, physical key cabinets, intercom stations, and visitor registration systems.

- Patrolling Paths: Boundary wall walkways, dark zones, basement parking areas, electrical substations, engineering pump rooms, etc.

- Tower Caretaking Operations: Monitoring individual residential towers to inspect executed work & related errors, maintain visitor register correctly, check lift errors, and assist residents.

3.2 	Operational Execution Guidelines

Do's

- Verify All Visitors: Require all non-resident visitors, commercial vendors, and delivery personnel to register via the digital visitor management application or physical logbooks before entering.

- Perform Vehicle Searches: Inspect the undercarriages of all incoming commercial and vendor vehicles using inspection mirrors, and search car trunks before allowing access.

- Confirm Materials with Gate Passes: Match all incoming and outgoing bulk materials with formal gate passes signed by authorized estate officers.

- Use Electronic Patrol Tracking: Ensure night patrolling guards carry electronic tracking wands and scan every RFID tag mounted along the perimeter wall sequence at specified intervals.

- Maintain Uniform Standards: Ensure all security and caretaking staff wear uniform uniforms, displaying their identity cards, carrying high-powered flashlights for night shifts, and keeping whistles accessible.

Don'ts

- No Unattended Security Posts: Security personnel must never leave an assigned gate or lobby reception desk unattended. Staff must perform formal face-to-face handovers during shift changes.

- Prohibit Vehicle Tailgating: Do not allow multiple vehicles to pass through automated boom barriers together. Every vehicle must be verified and logged individually.

- Zero Tolerance for Sleeping on Duty: Sleeping during a shift is a critical security breach. The contractor must immediately remove the individual from the premises and face contract penalties.

- No Unconfirmed Floor Access: Do not allow ad-hoc commercial service providers or strangers up to residential floors without receiving confirmation from the resident via the intercom or digital system.

3.3 	Granular Task Frequency Matrix

| Security Post | Activity | Frequency | Execution Methodology | Quality Standard |
| --- | --- | --- | --- | --- |
| Main Vehicle Gates | Access control, vehicle screening, and barrier operation. | Continuous (24/7) | Verify resident RFID badges; inspect commercial vehicle trunks and undercarriages; log vehicle license numbers. | Zero unauthorized vehicle entries; traffic clear of main road obstructions. |
| Front Reception Desk | Visitor data entry and visitor pass management. | Continuous (08:00 to 20:00) | Greet visitors; verify their entry with residents via intercom; enter details; issue passes. | 100% accurate visitor records; professional and polite communication. |
| Perimeter Boundary Walls | Security foot patrols along campus edges. | Every Hour (From 22:00 to 06:00) | Walk the perimeter path with security batons and flashlights; scan electronic patrol tags at checkpoints. | Incorruptible electronic patrol logs showing timely checkpoint scans. |
| Screening Infrastructure | Functional testing of scanning tools. | Daily (At start of each shift) | Pass standard metal test objects through door-frame metal detectors and across handheld metal detectors to check calibration. | Equipment must consistently detect test metals; battery power levels kept >80%. |
| Tower Ground Lobbies | Access monitoring and caretaking watch. | Continuous (24/7) | Monitor the ground floor entry doors; prevent tailgating by pedestrians; handle intercom calls. | Zero loitering in common lobbies; polite assistance provided to residents. |
| Tower Lift Cars | Emergency system audits and structural checks. | Thrice Daily (Once per shift) | Ride elevators floor-by-floor; test the emergency intercom button, verify exhaust fan function, and check mirror conditions. | Communication link to control room must be functional; smooth floor alignment. |
| Common Escape Routes | Staircase walkthroughs and fire door audits. | Twice Daily (Morning /Evening) | Walk down staircase paths; ensure fire doors are unbolted and close fully; check that layout pathways are clear. | Fire doors must latch shut automatically; zero storage debris in staircases. |
| Security Log Centre | Consolidating data logs and shift handovers. | Daily (At shift transitions) | Summarize daily visitor counts, material gate passes, and unusual incidents into the master ledger; sign off on handovers. | Complete data records with no omitted sections or un-logged shift events. |

3.4 	Grievance Redressal

Definitions of Bad Execution / Service Failure

- Security guard found sleeping, intoxicated, or missing from an assigned gate, reception desk, or lobby check post.

- Allowing a commercial or vendor vehicle onto the premises without formal registration or trunk inspection.

- Failure to perform night boundary wall patrol loops, or missed RFID checkpoint tags on the patrol log.

- Failure to crosscheck delivery logs or material gate passes against outbound items.

- Rude behaviour, unprofessional language, or arguments with residents, guests, or administrative staff.

Response & Resolution Windows

- Critical Faults (Intrusion alarm, guard missing from main gate, unauthorized group entry): Immediate deployment of supervisor within 5 minutes; full technical containment or replacement within 15 minutes.

- Routine Faults (Intercom line issue, missing visitor clipboard, slow gate barrier response): Acknowledgment within 15 minutes; full operational resolution within 2 hours.

Itemized Payment Deduction Schedule

- Guard found sleeping or absent from an assigned post during audits: Deduct ₹2,500 per instance, and the individual must be replaced within 2 hours.

- Allowing a commercial or vendor vehicle onto the premises without registration: Deduct ₹1,500 per unverified vehicle.

- Failure by night guards to complete scheduled perimeter patrol loops: Deduct ₹2,000 per missed shift log.

- Allowing material to exit the property without an authorized gate pass: Deduct ₹5,000 per instance, plus the contractor faces full legal liability for any missing property.

- Rude behaviour or uniform compliance issues by security staff during audits: Deduct ₹1,000 per reported incident.

SECTION 4

Comprehensive Horticulture & Landscape Management

4.1 	Scope of Work

The contractor shall provide agronomic care, landscape preservation, seasonal garden design, and nursery management to maintain the estate's green infrastructure. The physical boundaries of this scope cover:

- Lawn & Turf Infrastructures: Central lawns, recreational green spaces, embankment turf, and decorative turf grass borders.

- Campus Plant Arrangements: Ornamental shrub beds, shaped hedges, architectural topiaries, flowering groundcovers, and perimeter tree lines.

- Nursery & Potted Infrastructure: Interior potted arrangements in common lobbies, veranda planter boxes, hanging baskets, and the estate’s plant propagation nursery.

- Soil Nutrient & Protection Operations: Digging and preparing flower beds, breaking up soil clots, applying organic vermicompost, implementing chemical fertilization programs, applying targeted pesticides, and shredding green waste for compost.

4.2 	Operational Execution Guidelines

Do's

- Schedule Systematic Watering: Water lawns and shrub beds early in the morning (before 08:00) or late in the evening (after 17:30) to reduce water loss from evaporation and protect leaves from sun damage.

- Maintain Uniform Lawn Mowing: Cut lawn turf regularly using motorized lawnmowers with sharp, well-adjusted blades. Maintain a consistent grass height and trim borders cleanly using manual edging shears.

- Aerate Soil Frequently: Loosen the top 2 inches of soil around flower beds, hedges, and tree basins (hoeing) every week to improve root aeration and water absorption.

- Apply Balanced Soil Nutrition: Use well-decomposed organic vermicompost and aged manure as primary nutrients. Supplement with chemical NPK formulations based on seasonal growth requirements.

- Follow Potted Plant Rotation Rules: Move indoor potted decorative plants out to the sun-lit nursery every 14 days for recovery, replacing them with fresh, healthy plants.

Don'ts

- Avoid Turf Scalping: Do not adjust mower blades too low. Cutting grass too close to the soil (scalping) damages the turf roots and allows weeds to take over.

- Prohibit Unregulated Pesticides: Never use unapproved or highly toxic chemical pesticides. Apply only approved, low-toxicity targeted systemic insecticides or fungicides.

- Prohibit Burning Landscape Waste: Do not burn dried leaves, lawn clippings, or pruned branches on campus grounds. Transport all green waste to designated on-site composting pits.

- Avoid Creating Waterlogged Conditions: Do not overwater or allow mud to pool in lawns or flower beds, as standing water cuts off oxygen to roots and encourages fungal root rot.

4.3 	Granular Task Frequency Matrix

| Area | Activity | Frequency | Execution Methodology | Quality Standard |
| --- | --- | --- | --- | --- |
| Central Lawns & Turf | Uniform watering using sprinklers or hoses. | Daily (Adjusted for rainfall) | Connect canvas hoses to the treated water lines; run automated impact sprinklers to ensure deep water penetration into the soil. | Soil must be evenly moist down to 2 inches; zero dry brown patches or waterlogged mud spots. |
| Turf Grids | Motorized lawn mowing and edge trimming. | Every 10 to 14 Days | Clean the lawn of stones; run walk-behind motorized mowers in straight lines; trim sidewalk edges with manual grass shears. | Consistent grass height between 2.5 and 3.5 inches; clean, uniform lawn surface. |
| Flowering Shrub Beds | Manual de-weeding and topsoil aeration. | Weekly | Pull out weeds by their roots; loosen the top 2 inches of compacted soil around plants using hand forks. | Beds must be completely free of wild weeds; loose, aerated topsoil layer. |
| Decorative Hedges | Shrub pruning and geometric shaping. | Monthly | Set guide strings along hedge rows; trim overgrown shoots using electric or manual hedge shears to maintain uniform dimensions. | Geometric alignments; clean pathways with no branches blocking walkways or camera lines. |
| Campus Trees & Palms | Safety pruning and dead-wood removal. | Bi-Annually | Cut away dead, diseased, or low-hanging branches using pole saws; apply copper oxychloride paste to cut surfaces. | Clean tree frames with no hazardous branches; clear views for streetlights and security cameras. |
| All Landscaped Zones | Fertilizer application and composting. | Monthly | Spread vermicompost (500g/sqm) or custom chemical NPK blends around plant root zones; rake into the soil and water immediately. | Dark green foliage, healthy plant growth, and vibrant flower blooms. |
| Seasonal Flower Beds | Complete soil prep and sapling planting. | Twice Yearly | Dig out old seasonal plants; turn soil down to 6 inches; mix in organic manure; plant new winter or monsoon saplings at high density. | Bright, active flower displays maintained across seasons with no bare dirt patches. |
| Lobby Potted Plants | Plant rotation and leaf cleaning. | Fortnightly | Wipe dust off plant leaves using damp microfiber cloths; move indoor pots back to the nursery and bring fresh pots inside. | Vibrant, dust-free foliage inside lobbies; zero wilting or yellowing leaves. |
| Landscape Waste Yard | Organic green waste composting. | Semi-Weekly | Collect all lawn clippings and branch trimmings; run through a mechanical shredder; layer into composting pits. | Clean campus grounds with no piled green waste left outside designated composting zones. |

4.4 	Grievance Redressal

Definitions of Bad Execution / Service Failure

- Patches of dry, brown, or dead grass across central lawns caused by missing watering cycles.

- Overgrown lawn heights (>4.5 inches) or ragged hedge borders blocking pathways or sidewalks.

- Accumulation of wild weeds in ornamental shrub beds or un-hoed tree bases.

- Dying, wilting, or yellowing indoor potted plants left inside lobbies without being rotated.

- Piling up cut branches, grass clippings, or green waste in open common areas for more than 24 hours.

Response & Resolution Windows

- Critical Faults (Fallen tree branch blocking transit roads, broken irrigation main pipe): Acknowledgment within 20 minutes; branch cleared or main water valve closed within 2 hours.

- Routine Faults (Overgrown turf, weed patches, delayed pot rotation): Acknowledgment within 2 hours; full technical resolution within 48 hours.

Itemized Payment Deduction Schedule

- Fallen tree components or large pruning debris left blocking walkways for over 12 hours: Deduct ₹1,500 per day per location.

- Dying or withered ornamental shrubs caused by a lack of regular watering: Deduct ₹300 per dead plant penalty, plus the contractor must replace the plant at their own cost.

- Failure to mow lawns within the maximum 14-day window, leading to overgrown common turf: Deduct ₹2,000 per zone per week.

- Allowing wild weeds to cover more than 10% of a designated flower bed surface: Deduct ₹1,000 per bed per week.

- Failure to rotate indoor potted plants, resulting in dust accumulation or wilting: Deduct ₹400 per neglected pot.

SECTION 5

Comprehensive Pest Control & Vector Management Services

5.1 	Scope of Work

The contractor shall implement an integrated pest management program combining mechanical traps, biological controls, and targeted chemical applications to eliminate pests from common areas. The technical scope covers:

- Crawling Insect Management: Eradicating cockroaches, silverfish, ants, and spiders from common areas, utility ducts, electrical shafts, drainage lines, lift pits, and waste stations.

- Rodent Control Networks: Managing an external perimeter rodent baiting network, subterranean burrow treatments, and mechanical traps near buildings and electrical rooms.

- Flying Vector Control: Managing mosquito and fly populations across open lawns, basements, and surface drains using thermal fogging and larvicides.

- Specialized Extermination Operations: Investigating and treating subterranean termite infestations in common area structures, and safely removing active stinging wasp or hornet nests.

5.2 	Operational Execution Guidelines

Do's

- Apply Approved Chemicals Only: Use public health insecticides approved by the Central Insecticides Board (CIB). Apply chemical products like Deltamethrin, Cyfluthrin, and Lambda-cyhalothrin at specified dilutions.

- Secure External Bait Stations: Secure all tamper-resistant rodent bait stations firmly to the ground along perimeter walls. Label each box clearly with safety warnings and track bait consumption in a log.

- Time Thermal Fogging Operations: Conduct outdoor thermal smoke fogging during peak mosquito activity hours—either at dusk (17:30 to 19:30) or dawn (05:30 to 07:30).

- Provide Chemical Safety Equipment: Ensure pest control operators wear complete chemical safety equipment, including full-face respirators with organic vapor cartridges, nitrile gloves, safety goggles, and protective coveralls during mixing and application.

- Notify Residents in Advance: Post notices in common areas at least 24 hours before conducting major chemical spraying or thermal fogging operations to inform residents.

Don'ts

- No Loose or Unprotected Baits: Never place loose rodenticide pellets or open chemical baits in public common areas where children, residents, or domestic pets can reach them.

- No Indoor Thermal Fogging: Do not use thermal smoke fogging inside enclosed tower corridors, elevator cars, or residential lobbies. Use cold ULV (Ultra-Low Volume) misting or localized gel baits instead.

- No Spraying Near Water Storages: Do not apply chemical pesticides or larvicides within 15 meters of domestic water storage tanks, open pump wells, or water treatment plant components.

- Avoid Chemical Resistance Buildup: Do not use the same chemical class continuously. Rotate pesticide groups regularly to prevent insects from developing resistance.

5.3 	Granular Task Frequency Matrix

| Category | Activity | Frequency | Execution Methodology | Quality Standard |
| --- | --- | --- | --- | --- |
| Common Service Shafts | Residual chemical spraying for crawling insects. | Monthly | Spray internal walls of electrical and plumbing shafts using a compression sprayer filled with an approved deltamethrin mix. | Total absence of active cockroach trails or ant lines in utility ducts. |
| Estate Perimeter Walls | Rodent bait station auditing and maintenance. | Fortnightly | Inspect bait boxes; document consumption logs; replace old or eaten Bromadiolone wax blocks; clear out dead leaves. | Intact, anchored bait boxes; zero active rat burrows along building foundations. |
| Open Grounds & Basements | Thermal smoke fogging for adult mosquitoes. | Twice Weekly (Increased during outbreaks) | Run industrial thermal fogging machines using an approved chemical mixture, walking slowly through basements and basins. | Visible knockdown of adult mosquito populations; zero dense swarms in common areas. |
| Stormwater Surface Drains | Anti-larval chemical application. | Weekly | Apply Temephos liquid or biological larvicide oil into standing water pools and surface drains using manual knapsack sprayers. | Zero swimming mosquito larvae found in dip samples from treated drainage lines. |
| Tower Building Structures | Termite inspection and spot-injection. | Bi-Annually | Inspect common area wooden doors, electrical cabinets, and masonry joints; drill and inject Imidacloprid fluid if active mud galleries are found. | Complete eradication of termite mud tubes; zero structural wood damage. |
| Lobbies & Service Desks | Electronic fly catcher maintenance. | Weekly | Clean the collection trays of UV fly traps; test electrical grid arcs; replace UV tubes annually. | Trays kept clean of insect remains; functional UV lights with no flickering. |
| Common Walls & Roofs | Stinging insect nest eradication. | On-Demand | Spray wasp or hornet nests from a safe distance using high-pressure knockdown sprays at night, then remove and dispose of the nest structure. | Full removal of active nests within 24 hours of being reported by residents. |
| Central Waste Storage | Intensive larvicidal and disinfection spraying. | Semi-Weekly | Spray waste dump structures with high-concentration disinfectants and larvicides to control fly and vector breeding. | Minimal fly counts around waste zones; zero maggot infestations in collection bins. |

5.4 	Grievance Redressal

Definitions of Bad Execution / Service Failure

- Missing a scheduled vector control cycle (thermal fogging or anti-larval drain treatments).

- Active infestations of cockroaches, silverfish, or rodents found inside building common spaces or electrical rooms during audits.

- Bait stations found unanchored, damaged, or left without rodenticide wax blocks during field inspections.

- Applying unapproved or agricultural-grade chemicals that present health hazards to residents.

- Failing to safely remove reported hornet or wasp nests within the required timeframe, creating safety risks.

Response & Resolution Windows

- Critical Faults (Active hornet nest near tower door, rodent inside electrical panel, disease vector outbreak): Acknowledgment within 15 minutes; full technical containment or removal within 2 hours.

- Routine Faults (Clogged fly-catcher tray, missed spot spray in shaft, broken bait station cover): Acknowledgment within 2 hours; full technical resolution within 24 hours.

Itemized Payment Deduction Schedule

- Missing a scheduled thermal smoke fogging cycle during peak vector seasons: Deduct ₹3,000 per missed loop, and the contractor must complete a makeup cycle within 24 hours.

- Failure to remove a reported stinging insect nest within the 2-hour window: Deduct ₹2,000 per delayed hour.

- Damaged, empty, or unanchored rodent bait stations left unserved after an inspection: Deduct ₹500 per neglected box.

- Audit detection of active crawling insect trails in building electrical utility shafts: Deduct ₹1,000 per building floor branch.

- Using unapproved or un-registered public health chemicals during treatments: Deduct ₹15,000 per occurrence, and the contractor faces potential contract termination.

SECTION 6

Operation & Maintenance of Firefighting & Fire Alarm Systems

6.1 	Scope of Work

The contractor shall provide engineering operations, routine diagnostic testing, and preventive maintenance to ensure the readiness of the campus fire life safety infrastructure. The technical systems include:

- Fire Pumping Installations: Main electric hydrant pumps, diesel engine backup pumps, electric jockey pumps, automated control panels, pressure switches, suction/delivery valves, and diesel fuel storage networks.

- Water Distribution Infrastructure: Main wet-riser pipelines, yard hydrants, internal fire hose cabinets, canvas fire hoses, branch pipe nozzles, and automatic wet sprinkler systems.

- Electronic Detection & Alarms: Central Fire Alarm Control Panels (FACP), localized zone panels, addressable smoke sensors, thermal heat sensors, manual call points (MCP), line break monitors, and evacuation hooters.

6.2 	Operational Execution Guidelines

Do's

- Maintain Wet-Riser Line Pressure: Keep the wet-riser pipeline network pressurized at a constant minimum level of 7.0kg/cm. Configure the electric jockey pump for automatic startup to manage minor pressure drops.

- Run Scheduled Engine Tests: Run the standby diesel fire pump weekly for at least 10 minutes to verify the battery crank, starter motor health, cooling water flow, and engine oil pressure.

- Keep Backup Fuel Supplies: Keep the primary diesel fuel storage tank for the backup engine filled to at least 75% capacity at all times.

- Monitor Main Alarm Panel: Monitor the main fire alarm control panel constantly. Investigate any open-loop warnings or ground faults immediately to ensure system readiness.

- Test System Triggers Regularly: Test individual manual call points (MCP) and smoke detectors on a rotating schedule using specialized test keys or aerosol smoke canisters.

Don'ts

- Never Leave Pumps in Manual Mode: Do not leave the control switches for the main fire pumps or jockey pump in "Manual" mode. They must remain in "Auto" mode to ensure immediate emergency response.

- Do Not Block Fire Infrastructure: Do not block access to yard hydrants, fire department connections, or internal hose cabinets with landscape plants, parked vehicles, or common area signage.

- Do Not Paint Sprinkler Heads: Ensure sprinkler heads are never covered or painted over during building maintenance. Clean off any accidental paint or dust splatters immediately.

- Avoid Long Alarm Isolations: Do not leave an addressable detection loop isolated on the control panel for more than 4 hours. Deploy an electrician immediately to locate and repair the loop wiring fault.

6.3 	Granular Task Frequency Matrix

| Component | Activity | Frequency | Execution Methodology | Quality Standard |
| --- | --- | --- | --- | --- |
| Fire Pump Station | Wet-riser line pressure and jockey pump testing. | Daily | Read and log the pipeline pressure gauge; bleed a small amount of water from the test line to confirm the jockey pump starts automatically. | Pipeline pressure must stay above 7.0kg/cm2; automated pump startup functional. |
| Fire Alarm Panel (FACP) | Electronic diagnostic loop monitoring. | Daily | Run panel diagnostic routines; check power status lights; verify that battery backup charging currents are within spec. | Clear panel status screen with zero active fault codes or unaddressed loop errors. |
| Standby Diesel Pump | Scheduled operational run testing. | Weekly | Turn the selector to manual; crank the diesel engine and run for 10 minutes; monitor water cooling, oil pressure, and fuel levels. | Engine must start within 10 seconds of cranking; stable operating oil pressure. |
| Detection Electronics | Addressable loop sensor testing. | Monthly (Test 10% of total sensors monthly) | Spray aerosol smoke into selected smoke detectors; verify that the correct zone and device address register on the main control panel. | Confirmed signal delivery to the FACP; correct text mapping displays on the screen. |
| Manual Call Points (MCP) | Alarm trigger and hooter validation. | Monthly | Activate a manual call point using the test key; confirm that all localized evacuation hooters sound across adjacent floors. | Hooters must sound clearly >75dB at floor boundaries); panel registers fire state. |
| Hand Extinguishers | Structural and pressure gauge audits. | Monthly | Inspect every common area CO2, DCP, and water extinguisher; verify the safety seal is intact and check the pressure needle. | Pressure indicator needles must rest firmly within the green zone; inspection tags updated. |
| Yard Hydrant Valves | Valve mechanical servicing and lubrication. | Quarterly | Open and close hydrant landing valves to prevent seizing; clean and apply high-temperature grease to the connection threads. | Handwheel must turn smoothly with no binding; zero fluid leaks around the valve packing glands. |
| Fire Hose Cabinets | Full unspooling and canvas integrity reviews. | Quarterly | Unroll canvas hoses completely; check for dry rot or fabric cracks; inspect brass couplings and verify that nozzles attach securely. | Hoses must be clean and dry, with no fabric damage; hose reel rolls out smoothly. |
| Pipeline Networks | Complete system flushing and descaling. | Bi-Annually | Open the end-of-line drain valves on top floors to flush out accumulated rust, silt, and mineral scale from the pipelines. | Flushing discharge must run clear within 5 minutes; zero pipe blockages. |

6.4 	Grievance Redressal

Definitions of Bad Execution / Service Failure

- Riser network system pressure dropping below the required 7.0kg/cm2 threshold due to leaks or jockey pump failures.

- Leaving the main electrical fire pump panels or standby diesel selectors turned to "Manual" mode instead of "Auto".

- Main Fire Alarm Control Panel displaying unresolved wiring ground faults, shorted loops, or unaddressed sensor failures for over 24 hours.

- Missing, un-serviced, low-pressure, or un-weighted portable fire extinguishers in common corridors.

- Frozen, rusted, or seized hydrant landing valves that cannot be operated by hand during random inspections.

Response & Resolution Windows

- Critical Faults (Riser pipeline rupture, FACP system failure, main pump starter malfunction): Acknowledgment within 15 minutes; technical team dispatched immediately; temporary bypass completed within 2 hours; full technical resolution within 6 hours.

- Routine Faults (Isolated sensor failure, broken glass window on fire hose cabinet, missing valve tag): Acknowledgment within 1 hour; full technical resolution within 24 hours.

Itemized Payment Deduction Schedule

- Standby diesel fire pump failing to start automatically due to operator neglect or low fuel: Deduct ₹10,000 per day until the engine is functional.

- Leaving any main fire suppression pump selector switched to "Manual" mode: Deduct ₹5,000 per shift instance.

- Leaving an electronic fire alarm control panel non-functional or disconnected: Deduct ₹4,000 per day.

- Missing or expired fire hoses, or low-pressure fire extinguishers left unserviced: Deduct ₹2,000 per missing or expired item.

- Seized yard hydrant landing valves found during a system audit: Deduct ₹3,000 per seized valve unit.

## SECTION 7

## Technical Maintenance Services, Manpower Deployment & Statutory Framework

### 7.1 	Scope of Work & Technical Definition

The contractor shall operate an on-site, multi-disciplinary technical engineering and supervisory workforce to perform comprehensive day-to-day operation, preventive upkeep, and rapid breakdown remediation.

#### Demarcation of Civil, PHE, and Electrical Responsibilities

This contract enforces a strict demarcation of physical boundaries between the property common areas/campus and the interiors of individual private houses/flats.

- Common Areas and Campus (Full Agency Liability): The agency is completely responsible for providing all technical manpower, comprehensive tools, specialized testing gear, and all material/replacement part costs for the property grounds, streetlights, basements, utility panels, external plumbing grids, structural roofs, and tower public pathways.

- Private Houses and Private Flats (Manpower Assistance Only): Comprehensive maintenance or routine remodelling of flat interiors is explicitly excluded. However, the agency must provide qualified on-site technical manpower (Electrician, Plumber, Carpenter) during standard working hours to perform labour and technical assistance only within private residential units.

- Private Unit Material Policy: The agency shall cover zero material costs, replacement item fees, or consumption expenditures for installations inside private residential units. All raw replacement parts, switches, wiring lengths, taps, or fittings required inside an individual flat must be purchased and provided directly by the respective resident, owner, or administrative allottee.

#### Exhaustive Categorization of Minor Repair Scope

The on-site labour assistance for private units, as well as routine common area maintenance, is restricted to an explicit catalogue of minor repairs. Any major structural replacement or circuit overhaul falls outside this baseline tier and must be escalated to the building authority:

- Minor Electrical Maintenance Works: Localized diagnostics and direct replacement of standard small electrical accessories, including incandescent/LED light bulbs, tube light fittings, inline fuses, basic modular switches, plugs, electronic chokes, power sockets, ceiling fan regulators, calls/doorbells, and localized insulation tape dressing to repair split single-phase wires.

- Minor Plumbing and Public Health Engineering (PHE) Works: Repairing localized leaks and structural replacements of standard terminal water accessories, including loose bib cocks, basin pillar taps, worn rubber washers, damaged health faucets, PVC flushing cistern internal dual-valves, kitchen sink strainers, mirror brackets, and complete commode seat replacements. This also includes using manual drain-snakes or hand-pumps to clear localized sink, washbasin, or floor-trap choke-ups.

- Minor Civil and Carpentry Works: Patch plaster touch-ups, localized alignment or re-cementing of loose interlocking paver blocks along paths, fixing creaky or sticking wooden doors, realigning cabinetry hinges, replacing standard tower glass window panes, and adjusting surface hardware like door closers, magnetic catches, and safety tower bolts.

### 7.2 	Operational Execution Guidelines

#### Do's

- Validate On-Site Qualifications: Ensure that all deployed technicians carry calibrated insulation multimeters, plumbing wrench kits, and insulated hand tools. Electricians must carry and display their official electrical wireman licenses.

- Adhere to Clear Flat Boundaries: Instruct plumbers, electricians, and carpenters to inspect the resident-provided parts for matching specifications before executing labour assistance inside a private home.

- Enforce Strict LOTO Rules: Mandate the use of industrial Lock-Out/Tag-Out (LOTO) padlocks on breaker switches whenever technicians are performing minor repair works on common area sub-distribution boards.

- Isolate Potable Water Systems: Ensure that vertical water shafts or rising mains are isolated valve-by-valve to minimize distribution supply downtime during common pipeline joint weld patches.

- Maintain Dynamic Bihar Wages: Calculate and pay monthly staff payrolls to match or exceed the updated dynamic minimum wage benchmarks published for highly skilled, skilled, and semi-skilled classifications by the Department of Labour, Government of Bihar.

#### Don'ts

- No Material Purchases for Private Units: Do not purchase, supply, or bill any raw replacement parts, tap spindles, or breaker items destined for private homes using agency funds.

- No Unregulated Cash Handling: Strictly prohibit on-site technicians from accepting direct tip cash, material procurement commissions, or independent payments from residents for household labour assistance.

- No Dangerous Circuit Alterations: Never bypass internal distribution board residual current circuit breakers (RCCB) or introduce unauthorized wire jumpers to mask single-phase line grounding faults.

- No Heavy Structural Modifications: Do not hammer out structural concrete wall frames, break load-bearing slab corners, or execute deep modifications during common line piping path changes without written approval from the Engineer-in-Charge.

- No Cash Payouts to Labour Crew: Do not process monthly staff salaries through physical cash handovers or direct untraceable hand vouchers. All employee disbursements must be completed via electronic bank transfer.

### 7.3 	Technical Crew Deployment & Granular Task Frequency Matrix

#### Technical Positions & Qualifications Matrix

The contractor shall station an explicit technical crew on-site, fulfilling the qualifications and operational mandates dictated below:

| Position | Certifications & Experience | Operational Mandate |
| --- | --- | --- |
| Manager (Overall In-Charge) [Highly Skilled] | University Degree or Engineering Diploma; minimum 5 years of verified institutional property management experience. | Single point of contact (SPOC). Manages labour registers, directs daily task logs, audits compliance, and coordinates with the Engineer-in-Charge. |
| Electrician [Skilled] | State ITI Trade Certificate plus an active, valid wireman/electrical license; minimum 3 years of panel experience. | Audits common switchgear panels, balances line phases, services streetlights, and delivers on-site minor flat assistance. |
| Electrician Helper [Semi-Skilled] | Technical vocational training background; minimum 1 year of assistant electrical wireman experience. | Assists with ladder setups, handles wire reels, pulls cables, and vacuums dust out of de-energized sub-panel boxes. |
| Plumber [Skilled] | State ITI Trade Certificate in Plumbing/Sanitation; minimum 3 years of residential high-pressure plumbing network experience. | Tracks rising water mains, maintains common pumps, repairs distribution line joints, and delivers home labour assistance. |
| Plumber Helper [Semi-Skilled] | Documented field experience assisting commercial or municipal pipe fitters for a minimum of 1 year. | Assists with technical tools, manages pipe threaders, and cleans vertical shaft debris during line clearings. |
| Carpenter [Skilled] | Documented trade apprenticeship or ITI vocational certificate; minimum 3 years of structural carpentry/hardware experience. | Services common lobby openings, replaces floor springs, realigns fire doors, and assists residents with minor wood fixes. |
| Carpenter Helper [Semi-Skilled] | Documented workshop experience assisting timber finishing or building door layout installers for a minimum of 1 year. | Carries timber panels, holds heavy doors during hinge replacements, and cleans sawdust or debris from working areas. |

#### Operational & Maintenance Frequency Cadence

| Target | Task | Frequency | Operating Methodology |
| --- | --- | --- | --- |
| Campus Lighting Networks | Inspection and replacement of fused lamps. | Daily (Evening sweeps) | Check perimeter paths, streetlights, and tower corridor lighting fixtures; replace any non-functional lamps immediately using agency stock. |
| PHE Delivery Systems | Water tank indicator and lift pump diagnostics. | Thrice Daily | Check water level charts; activate transfer pumps; monitor current draw metrics and check for bearing friction. |
| Residential Helpdesk | Handling minor private unit tickets (Labour only). | Continuous (working hours) | Dispatch plumbers, electricians, or carpenters to units to perform minor labour assistance using resident-supplied parts. |
| Main Distribution Panels | Cable termination auditing and panel vacuuming. | Monthly | Isolate sections using LOTO padlocks; vacuum out dust accumulation; check cable terminations for hot spots or loose wires. |
| Tower Access Openings | Hydraulic closure arm and floor spring servicing. | Monthly | Check fire door closing alignment; adjust hydraulic sweep valves; lubricate heavy door hinge pins. |
| Paver Road Networks | Levelling shifting interlocking blocks. | Weekly Inspection | Pull up sunken paver blocks; re-level the bedding sand layer; tamp paver tiles back into place and seal joints with fine sand. |
| Potable Storage Tank Pools | Drainage, scrub down, and chlorine washing. | Quarterly | Drain storage tanks; scrub tile walls with mechanical brushes; spray food-grade sodium hypochlorite; flush and refill. |
| Electrical Ground Systems | Ground pit grid resistance testing. | Bi-Annually | Isolate the reference earth electrode; measure grounding resistance levels using a digital three-terminal earth tester. |
| Structural Expansion Gaps | Structural joint sealant inspection. | Bi-Annually (Pre/Post-Monsoon) | Inspect structural sealants, metal cover plates, and roof waterproofing membranes for cracks or degradation. |

### 7.4 	Grievance Redressal

#### Definitions of Bad Execution / Service Failure

- Leaving common lighting panels, streetlights, or pathway lamps unserved or dark for more than 24 hours.

- Allowing technical staff to work without required safety equipment, insulated tools, or valid trade wireman licenses.

- Extended delays or failure to dispatch on-site technicians to handle minor household labour assistance tickets during standard working hours.

- Using unapproved wire jumpers or ignoring standard LOTO safety procedures during sub-panel engineering overhauls.

- Delayed or missed quarterly water storage tank cleaning and disinfection treatments.

- Staff payout irregularities, including paying wages below Bihar statutory minimum standards, missing ESIC/EPF deposits, or missing biometric attendance logs.

#### Helpdesk Ticket Severity Routing

The facility office shall operate a central management ticketing service, classifying technical faults and household assistance requests into three operational severity levels:

- Critical Severity Technical Faults: Total common area power blackouts, primary water riser pipeline ruptures, fire system pressure drops, or failed water lift pumps. Acknowledgment target: 15 minutes; full resolution window: 2 hours.

- Major Severity Technical Faults: Fused tower corridor branch circuits, blocked vertical drainage stacks, dragging main lobby entry doors, or loose exterior paver grids. Acknowledgment target: 30 minutes; full resolution window: 6 hours.

- Minor Severity Technical Faults / Private Home Support: Handling household minor labour assistance tickets (switches, taps, door latches) using resident-supplied materials. Acknowledgment target: 2 hours; full resolution window: 24 hours.

#### Itemized Payment Deduction Schedule

- Failure to complete technical repairs on a Critical Severity defect within 2 hours: Deduct ₹3,000 per hour of continued downtime.

- Failure to complete repairs on a Major Severity defect within 6 hours: Deduct ₹1,500 per day of delay.

- Failure to resolve a Minor Severity or private unit labour assistance ticket within 24 hours: Deduct ₹500 per day of delay.

- Skipping or delaying a scheduled quarterly water storage tank cleaning loop: Deduct ₹10,000 per tank structure branch.

- Disbursing employee monthly wages past the statutory 7th-day calendar deadline: Deduct ₹5,000 per day of payroll delay.

- Deploying uncertified staff or substituting qualified trade specialists with unskilled helpers: Deduct ₹3,000 per shift branch, and the contractor must deploy a qualified replacement immediately.

SECTION 8

Comprehensive Electrical Substation, Power Distribution & Housing Electrification Management

8.1 	Scope of Work

The contractor shall deliver end-to-end operational control, preventive maintenance scheduling, predictive diagnostic profiling, breakdown rectification, and on-site technical labour assistance for the complete high-tension (HT) and low-tension (LT) electrical infrastructure.

Asset

- Substation Transformation Plant: Continuous 24/7 operation and maintenance of electrical transformers, including off-circuit tap changers, protective Buchholz relays, marshalling boxes, and structural earth pits, full operational oversight of distribution transformers.

- Standby Generation Power: Operation and maintenance of Diesel Generator (DG) set equipped with automated mains failure (AMF) control panels, residential-grade acoustic enclosures, day-use fuel storage infrastructure, and heavy-duty starter batteries.

- Power Factor Optimization: Management of Automatic Power Factor Correction (APFC) panels fitted with microprocessor-controlled multi-step power factor relays and heavy-duty capacitor banks.

- Campus Illumination Layouts: Operation and repair of all common external compound lights, asphalt road streetlights, basement light fixtures, emergency escape staircase lights, and decorative pathway fixtures across Plot-B1 buildings.

- Wiring Systems & Transmission Lines: Maintenance of all high-voltage and low-voltage electrical cables (HT/LT cross-linked polyethylene armored cables), common area infrastructure internal/external wiring layouts, structural cable trays, and aggregate lighting panels, air circuit breakers (ACBs), moulded case circuit breakers (MCCBs), primary underground busbar trunk loops, and all interconnecting heavy-gauge technical power cables.

Physical Boundaries of Agency Material & Labor Liabilities

This contract establishes a strict technical demarcation separating the estate common infrastructure from private individual private housing units:

- Campus Grounds & Common Infrastructure (Labour & Materials Fully Covered): The agency is completely liable for providing all technical manpower, certified equipment, safety gear, and 100% of all material and replacement part costs required to service the common areas. This includes substations, transformers, high-powered streetlights, external cabling networks, main LT panels, feeder pillars, and corridor illumination layouts.

- Private Houses & Individual Flats (Labour Assistance Only during Working Hours): The agency is explicitly excluded from funding structural remodelling, systemic apartment electrical overhauls, or interior material procurement. However, the agency must provide qualified technical manpower stationed on-site during standard day working hours to execute labour assistance and maintenance handling only inside flats/residences.

- Private Material Logistics Policy: The agency shall cover zero material replacement expenses, component supply fees, or single-use consumption fees inside private residential spaces. All raw hardware components, spare parts, wires, lighting fixtures, plumbing taps, or commode accessories must be purchased and supplied directly by the respective resident or administrative allottee before the technical team executes the repair.

- Exhaustive Index of Allowable Minor Private Repairs: On-site technical assistance inside individual flats is strictly restricted to Minor Electrical Assistance: Diagnostic troubleshooting and replacement of standard small household electrical components, including single LED/incandescent light bulbs, tube light electronic chokes, modular single-phase switches, multi-pin wall plugs, fuses, fan regulators, and doorbells.

8.2 	Operational Execution Guidelines (Do's and Don'ts)

Do's

- Enforce Safety Clearance Checklists: Require electricians to verify single-phase and three-phase lines using industrial insulation multimeters and non-contact voltage detectors before executing common panel work.

- Maintain Peak Power Factor Standards: Continuously monitor step-capacitor tracking metrics inside the APFC panels to maintain a target power factor score of greater than 0.99 lagging. This eliminates low power factor surcharge penalties from the South Bihar Power Distribution Company Limited (SBPDCL).

- Perform Rigorous Fluid Diagnostics: Monitor transformer oil levels using sight glass indicators daily. Check winding and oil temperatures to ensure they stay safely within normal operating parameters (<600C above ambient temperature).

- Execute Precise Engine Maintenance: Perform weekly checkups on standby generator engines. Check engine lube oil levels, fuel filters, cooling jacket fluid levels, and charger battery terminal voltages (greater than 12.6V for 12V systems or greater than 25.2V for 24V configurations).

- Ensure Balanced Phase Distribution: Check the phase load distribution across all main LT panel bars and feeder pillars weekly using clamp meters. Re-balance the circuit distribution as needed to prevent neutral current lines from overheating.

- Enforce Uniform Parts Inspections: Instruct technicians to carefully inspect resident-provided parts to ensure they match equipment specifications before starting any minor labour repair work inside an individual flat.

Don'ts

- Prohibit Unauthorized Household Procurement: Never purchase, store, or clear any raw material items intended for individual private flat interiors using agency financial resources.

- Prohibit Unauthorized Cash Surcharges: Strictly prohibit on-site operators or helpers from charging direct fee tips or claiming separate cash payouts from residents for daytime household maintenance support.

- Prohibit Unregulated Circuit Bypasses: Do not allow electricians to bypass residual current circuit breakers (RCCBs), introduce loose temporary wire jumpers, or override core micro-controller relays inside floor distribution boxes.

- Do Not Neglect Dehydrating Breathers: Never allow transformer silica gel charges to remain unchanged once the granules shift colour from operational dark blue to a saturated light pink hue.

- Prohibit Hot-Circuit Terminations: Never attempt to tighten high-amperage terminal screws or adjust busbar links on live LT main panel frames without implementing a formal Lock-Out/Tag-Out (LOTO) safety protocol.

8.3 	Granular Task Frequency Matrix

| Component | Task | Frequency | Operating Methodology | Quality Standard |
| --- | --- | --- | --- | --- |
| Transformers | Comprehensive physical diagnostics logging. | Daily | Log oil levels via sight glass, record winding/oil temperatures, and inspect high-voltage bushing insulators for physical tracking or cracking. | Zero fluid leaks; structural temperature metrics maintained within normal manufacturing parameters (< 600C variance). |
| Standby DG Systems | System parameters tracking and test operations. | Every 2 Hours during run; Weekly no-load run | Check engine oil levels, log fuel metrics, check exhaust smoke clarity, and run standby engine for 10 minutes on no-load cycles. | Immediate battery crank execution (less than 10 seconds startup latency); zero liquid fuel leaks or blockages. |
| APFC Panels | Microprocessor relay verification & tuning. | Weekly | Read reactive power factor metrics on main step relays; inspect step contactors for signs of electrical arcing; swap out blown capacitor fuses. | Energy profile power factor sustained strictly greater than 0.99 lagging; zero utility system cost penalties from SBPDCL. |
| Feeder Pillars & Indoor Floor Panels | Line balancing and frame insulation audits. | Monthly | Check current load metrics on phase branches using digital clamp meters; torque all internal busbar termination connections. | Maximum line load variance across phases balanced <10%; zero hot spots detected on connection points. |
| Campus Lighting Grid | External pole light & common illumination audits. | Daily (At dusk transitions) | Walk compound paths, asphalt roadways, and building corridors; replace failed lamps immediately using agency inventory stock. | 100% operational lighting across common zones; zero dark zones along perimeter boundary paths. |
| Potable Storage Tanks | High-pressure structural cleaning loops. | Quarterly | Drain storage volumes completely; scrub internal structural surfaces with mechanical brushes; spray food-grade sodium hypochlorite. | Sanitized common storage infrastructure; water laboratory test profile certifying zero coliform presence. |
| Substation Earthing Networks | Soil pit moisture and resistance tests. | Bi-Annually | Isolate individual copper/GI ground electrodes; measure line-to-ground values using digital three-terminal earth testers. | Total ground electrical resistance profile sustained under a threshold metric of <2.0 ohms. |
| Private Units Helpdesk | Minor home labour assistance delivery. | Continuous (Standard working hours) | Dispatch plumbers, electricians, or carpenters to units to execute basic labour touch-ups using resident-supplied components. | 100% tracking data entries on incoming requests; professional technical support delivery. |

8.4 	Grievance Redressal, Failure Parameters & Payment Deduction Framework

Definitions of Bad Execution / Service Failure

- Low power factor tracking anomalies (<0.90) inside main APFC panels that result in operational surcharges or cost penalties from SBPDCL.

- Unserved or non-functional streetlight fixtures, common corridor LEDs, or basement lighting grids left dark for over 24 hours.

- Allowing standby generator batteries to drop below starting voltage thresholds, leading to backup power startup failures during blackouts.

- Failure or refusal to dispatch on-site technical manpower to handle allowable minor residential flat requests during working hours.

- Utilizing temporary un-insulated wire lines, open splices, or ungrounded extension circuits inside sub-distribution blocks.

Helpdesk Ticket Severity Routing

The facility management control centre shall handle common infrastructure maintenance and individual flat labour requests through a structured severity response tracking protocol:

- Critical Severity Electrical Faults (Substation blackouts, burning panel smells, primary cable faults): Acknowledgment within 15 minutes; immediate LOTO deployment; full resolution window within 2 hours.

- Major Severity Electrical Faults (Fused block corridor loops, failed essential common lighting panels, dead streetlights): Acknowledgment within 30 minutes; full replacement and repair resolution completed within 6 hours.

- Minor Severity Electrical Faults / Flat Support (Allowable minor household tasks using resident-supplied parts): Request logged on terminal app; technician dispatched within 1 hour; labour assistance finalized within 24 hours.

Itemized Payment Deduction Schedule for System Failures

- Failure to resolve a Critical Severity common area infrastructure breakdown within 2 hours: Deduct ₹3,000 per hour of continued downtime.

- Failure to complete repairs on a Major Severity common area system fault within 6 hours: Deduct ₹1,500 per day of delay.

- Failure to address an allowable private unit minor labour assistance ticket within 24 hours: Deduct ₹500 per day of delay from the monthly running invoice.

- Incurring a low power factor penalty from SBPDCL due to neglected APFC panel servicing: The contractor must cover 100% of the utility fine, plus a contract penalty deduction of ₹10,000 per bill instance.

- Leaving any main fire suppression pump or water lift pump selector set to "Manual" mode instead of "Auto": Deduct ₹5,000 per shift instance.

- Skipping or delaying a scheduled quarterly common water storage tank cleaning cycle: Deduct ₹10,000 per tank structure.

- Shortfall in minimum mandatory engineering team staffing counts against the contract roster: Deduct the individual's daily wage rate plus a penalty of ₹1,000 per missing shift.

- Deploying technicians who lack valid trade wireman certificates or appropriate insulated tools: Deduct ₹3,000 per shift, and the contractor must replace the individual immediately.