# KARNAT AKA POWER TRANSMISSION CORPORATION LIMITED

# OPGW cabling & associated hardware & fittings Index

Fibre Optic Cabling

Required Optical Fibre Characteristics

Physical Characteristics

      - Attenuation

      - Fibre Optic Cable Construction Transmission Line Details

      - Optical Fibre Cable Link Lengths

      - Optical Fibre Identification

      - Buffer Tube

      - Optical Fibre Strain & Sag-tension chart

      - Cable Materials

        - Filling Materials

        - Metallic Members

        - Marking, Packaging and Shipping

      - OPGW cable installation requirements

      - Optical Ground Wire (OPGW)

        - Central Fibre Optic Unit

        - Basic Construction

        - Breaking Strength

        - Electrical and Mechanical Requirements

        - Operating conditions

        - Installation

        - Installation Hardware (Holding/Supporting Equipments)

    - Fibre Optic Splice Enclosures (Joint Box) /Jointing Kit

      - Optical Fibre Splices

    - Fibre Optic Approach Cables (End Termination OFC)

      - Basic Construction

      - Jacket Construction & Material.

      - Optical, Electrical and Mechanical Requirements

    - Installation of Approach Cable (End Termination OFC)

    - Optical Fibre Termination and Splicing

      - Optical Fibre Connectors

    - Methodology for Installation and Termination

    - Cable Raceways.

OPGW cabling and associated hardware & fittings

This section describes the functional & technical specifications of OPGW cabling and associated hardware & fittings.

  - Fibre Optic Cabling

This section defines the requirements for G.652D Dual-window Single mode (DWSM) telecommunications grade fibre optic cable. Bidders shall furnish with their bids, detailed descriptions of the fibres & cable(s) proposed.

All optical fibre cabling including fibre itself and all associated installation hardware shall have a minimum guaranteed design life span of 25 years. Documentary evidence in support of guaranteed life span of cable & fibre shall be submitted by the Contractor during detailed engineering.

    - Required Optical Fibre Characteristics

This section describes the characteristics of optical fibre to be provided under this specification.

      - Physical Characteristics

Dual-Window Single mode (DWSM), G.652D optical fibres shall be provided in the fibre optic cables. DWSM optical fibres shall meet the requirements defined in Table 2-1(a).

      - Attenuation

The attenuation coefficient for wavelengths between 1525 nm and 1575 nm shall not exceed the attenuation coefficient at 1550 nm by more than 0.05 dB. The attenuation coefficient between 1285 nm and 1330 nm shall not exceed the attenuation coefficient at 1310 nm by more than 0.05 dB. The attenuation of the fibre shall be distributed uniformly throughout its length such that there are no point discontinuities in excess of 0.10 dB. The fibre attenuation characteristics specified in table 2-1 (a) shall be “guaranteed” fibre attenuation of any & every fibre reel.

The overall optical fibre path attenuation shall not be more than calculated below:

Maximum attenuation @ 1550nm: 0.21 dB/km x total km + 0.05 dB/splice x no. of splices + 0.5 dB/connector x no. of connectors

Maximum attenuation @ 1310nm: 0.35dB/km x total km + 0.05 dB/splice x no. of splices + 0.5    dB/connector x no. of connectors Power Grid Corporation of India Ltd. Volume II - Technical Page

Table 2-1(a)

DWSM Optical Fibre Characteristics

| Fibre Description: | Dual-Window Single-Mode |
| --- | --- |
| Mode Field Diameter: | 8.6 to 9.5 μm (± 0.6μm ) |
| Cladding Diameter: | 125.0 μm ± 1 μm |
| Mode field concentricity error | ≤ 0.6μm |
| Cladding non-circularity | ≤ 1% |
| Cable Cut-off Wavelength λ cc | ≤ 1260 nm |
| 1550 nm loss performance | As per G.652 D |
| Proof Test Level | ≥ 0.69 Gpa |
| Attenuation Coefficient: | @ 1310 nm ≤ 0.35 dB/km @ 1550 nm ≤ 0.21 dB/km |
| Chromatic Dispersion; Maximum: Zero Dispersion Wavelength: Zero Dispersion Slope: | 18 ps/(nm x km) @ 1550 nm 3.5 ps/(nm x km) 1288-1339nm 5.3 ps/(nm x km) 1271-1360nm 1300 to 1324nm 2 0.092 ps/(nm xkm) maximum |
| Polarization mode dispersion coefficient | ≤ 0.2 ps/km^½ |
| Temperature Dependence: | Induced attenuation ≤ 0.05 dB (-60°C - +85°C ) |
| Bend Performance: | @ 1310 nm (75±2 mm dia Mandrel), 100 turns; Attenuation Rise ≤ 0.05 dB @ 1550 nm (30±1 mm radius Mandrel), 100 turns; Attenuation Rise ≤ 0.05 dB @ 1550 nm (32±0.5 mm dia Mandrel, 1 turn; Attenuation Rise ≤ 0.50 dB |

## Fibre Optic Cable Construction

Overhead Fibre Optic Cables shall be OPGW (Optical Ground Wire). The OPGW cable is proposed to be installed on transmission lines. The design of cable shall account for the varying operating and environmental conditions that the cable shall experience while in service.

## Trans mission Line Details

Any details, as required for cable design etc. shall be collected by the Contractor during survey.

## Optical Fibre Cable Link Lengths

The Contractor shall supply & install the optical fibre cable as required based on detailed site survey to be carried out by the Contractor during the project execution. The Contract price shall be adjusted accordingly.

For the purpose of payment, the optical fibre link lengths are defined as transmission line route lengths from Gantry at one terminating station to the Gantry in the other terminating station. The actual cable lengths to be delivered shall take into account various factors such as sag, service loops, splicing, working lengths & wastage etc. and no additional payment shall be payable in this regard. The unit rate for FO cable quoted in the Bid price Schedules shall take into account all such factors.

## Op tical Fibre Identification

Individual optical fibres within a fibre unit and fibre units shall be identifiable in accordance with EIA/TIA 598 or IEC 60304 or Bellcore GR-20 colour-coding scheme.

Colouring utilized for colour coding optical fibres shall be integrated into the fibre coating and shall be homogenous. The colour shall not bleed from one fibre to another and shall not fade during fibre preparation for termination or splicing.

Each cable shall have traceability of each fibre back to the original fibre manufacturer's fibre number and parameters of the fibre. If more than the specified number of fibres are included in any cable, the spare fibres shall be tested by the cable manufacturer and any defective fibres shall be suitably bundled, tagged and identified at the factory by the vendor.

## Buffer Tube

Loose tube construction shall be implemented. The individually coated optical fibre(s) shall be surrounded by a buffer for protection from physical damage during fabrication, installation and operation of the cable. The fibre coating and buffer shall be strippable for splicing and termination. Each fibre unit shall be individually identifiable utilizing colour coding. Buffer tubes shall be filled with a water-blocking gel.

## Op tical Fibre Strain & Sag-tension chart

The fibre optic cable shall be designed and installed such that the optical fibres experience no strain under all loading conditions defined in IS 802. Zero fibre strain condition shall apply even after a 25 year cable creep.

For the purpose of this specification, the following definitions shall apply:

        - Maximum Working Tension (MWT) is defined as the maximum cable tension at which there is no fibre strain.

        - The no fibre strain condition is defined as fibre strain of less than or equal to 0.05%, as determined by direct measurements through IEC/ ETSI (FOTP) specified optical reflectometry techniques.

* The Cable strain margin is defined as the maximum cable strain at which there is no fibre strain.

          - The cable Maximum Allowable Tension (MAT) is defined as the maximum tension experienced by the Cable under the worst case loading condition.

          - The cable max strain is defined as the maximum strain experienced by the Cable under the worst case loading condition.

          - The cable Every Day Tension (EDT) is defined as the maximum cable tension on any span under normal conditions.

          - The Ultimate /Rated Tensile Strength (UTS/ RTS/ breaking strength) is defined as the maximum tensile load applied and held constant for one minute at which the specimen shall not break.

While preparing the Sag-tension charts for the OPGW cable the following conditions shall be met:

          - The Max Allowable Tension (MAT) / max strain shall be less than or equal to the MWT/ Strain margin of the cable.

          - The sag shall not exceed the earth wire sag in all conditions.

          - The Max Allowable Tension shall also be less than or equal to 0.4 times the UTS.

          - The 25 year creep at 25% of UTS (creep test as per IEEE 1138) shall be such that the 25 year creep plus the cable strain at Max Allowable Tension (MAT) is less than or equal to the cable strain margin.

          - The everyday tension (EDT) shall not exceed 20% of the UTS for the OPGW cable.

The Sag-tension chart of OPGW cable indicating the maximum tension, cable strain and sag shall be calculated and submitted along with the bid under various conditions mentioned below:

- 53° C , no wind and no ice

- 32° C, no wind and no ice

- 0°C, no wind and no ice

- 32° C, full wind and no ice

- 32° C, 75% full wind and no ice

rd

6. 0° C, 2/3 / 36% of full wind (IS 802:1977/1995)

The above cases shall be considered for the spans from 100 m to 600 m or higher span length in the range of 50 m spans. Max. vertical sag, max. tension and max sag at 0° C & no wind shall be considered for in line with the design parameter of transmission line. The typical details are indicated in the Appendices. The full wind load shall be considered as the design wind load for all the specified transmission lines as per relevant IS 802 version and the sag-tension chart shall be submitted considering the transmission lines. The Contractor shall submit the stringing chart for review of Employer.

The stringing chart shall be submitted by the Tower Package Contractor(s) for Raichur 765kV – Kurnool new Transmission line. However, same shall be reviewed by this Package Contractor and Employer.

## Cable Materials

The materials used for optical fibre cable construction, shall meet the following requirements:

## Filling Materials

The interstices of the fibre optic unit and cable shall be filled with a suitable compound to prohibit any moisture ingress or any water longitudinal migration within the fibre optic unit or along the fibre optic cable. The water tightness of the cable shall meet or exceed the test performance criteria as per IEC-794-1- F-5.

The filling compound used shall be a non-toxic homogenous waterproofing compound that is free of dirt and foreign matter, nonhygroscopic, electrically nonconductive and non-nutritive to fungus. The compound shall also be fully compatible with all cable components it may come in contact with and shall inhibit the generation of hydrogen within the cable.

The waterproofing filling materials shall not affect fibre coating, colour coding, or encapsulant commonly used in splice enclosures, shall be dermatologically safe, non-staining and easily removable with a non- toxic cleaning solvent.

## Metallic M embers

When the fibre optic cable design incorporates metallic elements in its construction, all metallic elements shall be electrically continuous.

## Mark ing, Packaging and Shipping

This section describes the requirements for marking, packaging and shipping the overhead fibre optic cable.

- Drum Markings: Each side of every reel of cable shall be permanently marked in white lettering with the vendors' address, the Purchaser’s destination address, cable part number and specification as to

the type of cable, length, number of fibres, a unique drum number including the name of the transmission line & segment no., factory inspection stamp and date.

- Cable Drums: All optical fibre cabling shall be supplied on strong drums provided with lagging of adequate strength, constructed to protect the cabling against all damage and displacement during transit, storage and subsequent handling during installation. Both ends of the cable shall be sealed as to prevent the escape of filling compounds and dust & moisture ingress during shipment and handling. Spare cable caps shall be provided with each drum as required.

The spare cable shall be supplied on sturdy, corrosion resistant, steel drums suitable for long periods of storage and re-transport & handling.

There shall be no factory splices allowed within a continuous length of cable. Only one continuous cable length shall be provided on each drum. The lengths of cable to be supplied on each drum shall be determined by a "schedule" prepared by the Contractor.

## OPGW cab le installation requirements

Most of the OPGW fibre optic cables to be installed under this project shall be installed under live line conditions, i.e. with all the circuits of the transmission line charged to their rated voltage. However, some of OPGW cables may be installed in off-line conditions.

Under live line installation, the OPGW cable shall be installed on transmission lines under live line conditions, i.e. with all the circuits of the transmission line charged to their rated voltage.

The splicing work shall be carried out by Communication system Package Contractor. All hardware & fittings needed to tie the OPGW to the towers/gantries shall be provided by Communication system Package Contractor to the transmission line tower contractor.

While handing over the OPGW drums, the testing (fibre loss and length measurement using OTDR) of OPGW in each drum shall be carried out by Communication system Package Contractor in presence of Tower package contractor(s) and Employer representative. After installation of OPGW cable, the testing of each section shall be carried out again by the Communication system Package Contractor in presence of Tower package contractor(s) and Employer representative. In case of any damage/high loss in the fibre, the total length of that particular section of OPGW cable shall be replaced by Tower package Contractor(s). Communication system Package Contractor shall supply new OPGW cable in place of damaged cable. The Contract price shall be adjusted accordingly.

Supervision of Installation -The Contractor shall supervise the stringing at site as per the approved stringing procedure. Site visit for supervision shall be carried out as per instruction of Employer. The Supervision/Inspection work in Contractor’s scope shall mainly include inspection as per stringing procedure, proper location of drum site, installation of stringing blocks/pulleys, proper sagging, proper installation of hardware, proper tension as per Sag-Tension chart, provision of service loops of OPGW in jointing locations etc.

## Op tical Ground Wire (OPGW)

OPGW cable construction shall comply with IEEE-1138, 1994. The cable provided shall meet both the construction and performance requirements such that the ground wire function, the optical fibre integrity and optical transmission characteristics are suitable for the intended purpose. The cable shall consist of

optical fibre units as defined in this specification. There shall be no factory splices within the cable structure of a continuous cable length.

The composite fibre optic overhead ground wire shall be made up of buffered optical fibre units(fibres in the buffer tube) embedded in a water tight aluminium / aluminium alloy/stainless steel protective central fibre optic unit surrounded by concentric-lay stranded metallic wires in single or multiple layers. The dual purpose of the composite cable is to provide the electrical and physical characteristics of conventional overhead ground wire while providing the optical transmission properties of optical fibre.

## Central Fibre Optic Unit

The central fibre optic unit shall be designed to house and protect multiple buffered optical fibre units from damage due to forces such as crushing, bending, twisting, tensile stress and moisture. The central fibre optic unit and the outer stranded metallic conductors shall serve together as an integral unit to protect the optical fibres from degradation due to vibration and galloping, wind and ice loadings, wide temperature variations, lightning and fault current, as well as environmental effects which may produce hydrogen.

The OPGW design of dissimilar materials such as stainless steel tube with aluminium or aluminium –clad- steel wire strands are not allowed. Central fibre optic unit may be of aluminium or stainless steel tube with aluminium protective coating. In case of aluminium protective coating, the coating must completely cover the tubes leaving no exposed areas of tubing that can make electrical contact either directly or indirectly through moisture, contamination, protrusions, etc with the surrounding stranded wires. The tube may be fabricated as a seamless tube, seam welded, or a tube without a welded seam.

## Basic Construction

The cable construction shall conform to the applicable requirements of this specification, applicable clauses of IEC 61089 related to stranded conductors and Table 2.2(a) OPGW Mechanical and Electrical Characteristics. In addition, the basic construction shall include bare concentric-lay-stranded metallic wires with the outer layer having left hand lay. The wires may be of multiple layers with a combination of various metallic wires within each layer. The direction of lay for each successive layer shall be reversed. The finished wires shall contain no joints or splices unless otherwise agreed to by the Employer and shall conform to all applicable clauses of IEC 61089 as they pertain to stranded conductors.

The wires shall be so stranded that when the complete OPGW is cut, the individual wires can be readily regrouped and then held in place by one hand.

## Breaking Strength

The rated breaking strength of the completed OPGW shall be taken as no more than 90 percent of the sum of the rated breaking strengths of the individual wires, calculated from their nominal diameter and the specified minimum tensile strength.

The rated breaking strength shall not include the strength of the optical unit. The fibre optic unit shall not be considered a load bearing tension member when determining the total rated breaking strength of the composite conductor.

## Electrical and Mechanical Requirements

Table 2-2(a) provides OPGW Electrical and Mechanical Requirements for the minimum performance characteristics. Additionally, the OPGW mechanical & electrical characteristics shall be similar to that of the earthwire being replaced such that there is no or minimal consequential increase in stresses on towers. For the purposes of determining the appropriate Max Working Tension limit for the OPGW cable IS 802:1995 and IS 875: 1987 shall be applied. However the OPGW installation sag & tension charts shall be based on IS 802 version to which the line is originally designed. For the OPGW cable design selection and preparation of sag tension charts, the limits specified in this section shall also be satisfied. The Bidder shall submit sag-tension charts with their bids.

## Table 2.2(a)

OPGW Electrical and Mechanical Requirements

| (1) | Everyday Tension | ≤ 20% of UTS of OPGW |
| --- | --- | --- |
| (2) | D.C. Resistance at 20ºC: | < 1.0 ohm/Km |
| (3) | Short Circuit Current: | ≥ 6.32 kA for 1.0 second |

        - Operating conditions

Since OPGW shall be located at the top of the EHV transmission line support structure, it will be subjected to Aeolian vibration, Galloping and Lightning strikes. It will also carry ground fault currents. Therefore, its electrical and mechanical properties shall be same or similar as those required of conventional ground conductors.

## Installation

OPGW installed under live line condition, i.e. with all circuits charged to the rated line voltage as specified in this section shall be generally in accordance with the IEEE Guide to the Installation of Overhead Transmission Line Conductors (IEEE STD. 524 with latest revisions), with additional instructions and precautions for live line working and fibre optic cable handling. The stringing procedure shall be submitted by the Contractor prior to stringing for Employer’s approval.

A tower structural analysis shall be carried out by the Contractor, based on the relevant data to be provided by Employer, to ensure that with the replacement of existing earthwire with the OPGW cable, the tower members remain within the statutory safety limits as per Indian Electricity rules and if required the Contractor shall carry out the tower strengthening as necessary. The OPGW cable sections shall normally be terminated & spliced only on tension towers. In exceptional circumstances, and on Employer specific approval, cable may be terminated on Suspension towers, but in this case tower strength shall be examined to ensure that tower loads are within safe limits and if required, necessary tower strengthening shall be carried out by the Contractor.

## Installation Hard ware (Holding/Supporting Equipments)

The scope of supply of the optical cable includes the assessment, supply and installation of all required fittings and hardware such as Tension assembly, Suspension assembly, Vibration dampers, Reinforcing rods, Earthing clamps, Downlead clamps, splice enclosure etc. The Bidder shall provide documentation justifying the adequacy and suitability of the hardware supplied. The Contractor shall determine the exact requirements of all accessories required to install and secure the OPGW.

The OPGW hardware fittings and accessories shall follow the general requirements regarding design, materials, dimensions & tolerances, protection against corrosion and markings as specified in clause 4.0 of EN 61284: 1997 (IEC 61284). The shear strength of all bolts shall be at least 1.5 times the maximum installation torque.

The OPGW hardware & accessories drawing & Data Requirement Sheets (DRS) document shall consist of three parts:

(1) A technical particulars sheet

(2) An assembly drawing i.e. level 1 drawing and

(3) Component level drawings i.e. level 2 & lower drawings. All component reference numbers, dimensions and tolerances, bolt tightening torques & shear strength and ratings such as UTS, slip strength etc shall be marked on the drawings.

The fittings and accessories described herein are indicative of installation hardware typically used for OPGW installations and shall not necessarily be limited to the following:

          - Suspension Assemblies: Preformed armour grip suspension clamps and aluminium alloy armour rods/ reinforcing rods shall be used. The suspension clamps shall be designed to carry a vertical load of not less than 25 KN. The suspension clamps slippage shall occur between 12kN and 17 kN.

The Contractor shall supply all the components of the suspension assembly including shackles, bolts, nuts, washers, split pins, etc. The total drop of the suspension assembly shall not exceed

150 mm (measured from the centre point of attachment to the centre point of the OPGW). The design of the assembly shall be such that the direction of run of the OPGW shall be the same as that of the conductor.

          - Dead End Clamp Assemblies: All dead end clamp assemblies shall preferably be of performed armoured grip type and shall include all necessary hardware for attaching the assembly to the tower strain plates. Dead end clamps shall allow the OPGW to pass through continuously without cable cutting. The slip strength shall be rated not less than 95% of the rated tensile strength of the OPGW.

          - Clamp Assembly Earthing Wire: Earthing wire consisting of a 1500 mm length of aluminium or aluminium alloy conductor equivalent in size to the OPGW shall be used to earth suspension and dead end clamp assemblies to the tower structure. The earthing wire shall be permanently fitted with lugs at each end. The lugs shall be attached to the clamp assembly at one end and the tower structure at the other.

          - Structure Attachment Clamp Assemblies: Clamp assemblies used to attach the OPGW to the structures, shall have two parallel grooves for the OPGW, one on either side of the connecting bolt. The clamps shall be such that clamping characteristics do not alter adversely when only one OPGW is installed. The tower attachment plates shall locate the OPGW on the inside of the tower and shall be attached directly to the tower legs/cross-members without drilling or any other structural modifications.

          - Vibration Dampers: Vibration dampers type 4R Stockbridge or equivalent, having four (4) different frequencies spread within the Aeolian frequency bandwidth, shall be used for suspension and tension points in each span. The Contractor shall determine the exact numbers and placement(s) of vibration dampers through a detailed vibration analysis as specified in technical specifications. Vibration damper clamps shall be made of aluminium or aluminium alloy, shall support the dampers during installation and shall maintain the dampers in position without damage to the OPGW and without causing fatigue. Armour or patch rods made of aluminium or aluminium alloy shall be provided as required to reduce clamping stress on the OPGW. The vibration damper body shall be hot-dip galvanised mild steel/cast iron or shall be permanent mould cast zinc alloy.

## Fibre Optic Splice Enclosures (Joint Box) / Jointing Kit

All splices shall be encased in Fibre Optic Splice Enclosures. Suitable splice enclosures shall be provided to encase the optical cable splices in protective, moisture and dust free environment. Splice enclosures shall comply to ingress protection class IP 66 or better. The splice enclosures shall be designed for the storage and protection of required number of optical fibre splices and equipped with sufficient number of splice trays for splicing all fibres in the cable. No more than 6 fibres shall be terminated in a single splice tray. They shall be filled with suitable encapsulate that is easily removable should re-entry be required into the enclosures.

Splice enclosures shall be suitable for outdoor use with each of the cable types provided under this contract. Splice enclosures shall be appropriate for mounting on transmission line towers above anti-climb guard levels at about 10 metres from top of the tower and shall accommodate pass-through splicing. The actual mounting height and location shall be finalised after Survey. Contractor shall be responsible for splicing of fibres and installation of splice enclosures.

## Op tical Fibre Splices

Splicing of the optical fibre cabling shall be minimized through careful Contractor planning. There shall be no mid-span splices allowed. All required splices shall be planned to occur on tower structures. All optical fibre splicing shall comply with the following:

- All fibre splices shall be accomplished through fusion splicing.

- Each fibre splice shall be fitted with a splice protection sheath fitted over the final splice.

- All splices and bare fibre shall be neatly installed in covered splice trays. No more than six (6) fibres shall be installed in each splice tray.

- For each link, bi-directional attenuation of single mode fusion splices, shall not average more than

0.05 dB and no single splice loss shall exceed 0.1 dB when measured at 1550 nm.

- For splicing, fibre optic cable service loops of adequate length shall be provided so that all splices occurring at tower structures can be performed at ground level.

## Fibre Optic Approach Cables (End Termination OFC)

For purposes of this specification, a fibre optic approach cable is defined as the Armoured underground fibre optic cable required to connect Overhead Fibre Optic Cable (OPGW) between the final in line splice enclosure on the gantry / tower forming the termination of the fibre cable on the power line and LIU installed within the building. The estimated fibre optic approach cabling length requirements are as per the site requirement. However, the Contractor shall supply & install the optical fibre approach cable as required based on detailed site survey to be carried out by the Contractor during the project execution and the Contract price shall be adjusted accordingly.

## Basic Construction

The cable shall be suitable for direct burial, laying in trenches & PVC/Hume ducts, laying under false flooring and on indoor or outdoor cable raceways.

## Jack et Construction & Material

The Approach Cable shall be a UV resistant, rodent proof, armoured cable with metallic type of armouring. The outer cable jacket for approach cable shall consist of carbon black polyethylene resin to prevent damage from exposure to ultra-violet light, weathering and high levels of pollution. The jacket shall conform to ASTM D1248 for density.

## Op tical, Electrical and Mechanical Requirements

Approach cable shall contain fibres with identical optical/ physical characteristics as those in the OPGW cables. The cable core shall comprise of tensile strength member(s), fibre support/bedding structure, core wrap/bedding, and an overall impervious jacket.

## Installation of Approach Cable

The existing cable trenches/ cable raceways proposed to be used shall be identified in the survey report. The Contractor shall make its best effort to route the cable through the existing available cable trenches. Where suitable existing cable trenches are not available, suitable alternatives shall be provided after Employer approval. However, the approach cable shall be laid in the HDPE pipe in all condition.

Suitable provisions shall be made by the Contractor to ensure adequate safety earthing and insulated protection for the approach cable.

All required fittings, supports, accessories, ducts, inner ducts, conduits, risers and any item not specially mentioned but required for laying and installation of approach cables shall be supplied and installed by the Contractor.

## Optical Fibre Termination and Sp licing

Optical fibre cables shall be terminated in LIU (Line Interface Unit) inside the building with 24 Fiber with suitable SC connector.

## Optical Fibre Connectors

Optical fibres shall be connectorised with SC-SC type connectors preferably. Alternatively connector with matching patch cord shall also be acceptable.

## Methodology for Installation and Termination

All optical fibre cable termination, installation, stringing and handling plans, guides and procedures, and engineering analysis (e.g. tension, sag, vibration etc.) shall be submitted to the Employer for review and approval in the engineering/design phase of the project, prior to establishing the final cable lengths for manufacture. Installation procedures including details of personnel and time required shall be documented in detail and submitted to Employer for approval. All installation practices shall be field proven and ISO accredited.

All cable segments shall include service loops as specified in this specifciation. The maximum allowable stringing tension, maximum allowable torsional shear stress, crush strength and other physical parameters of the cable shall not be exceeded. The preventative measures to be taken shall be documented in detail and submitted to Employer in advance of installation.

Optical fibre attenuation shall be measured after installation and before splicing. Any increase in attenuation or step discontinuity in attenuation shall not be acceptable and shall constitute a cable segment failure. In the event of cable damage or any fibre damage, the complete section (tension location to tension location) shall be replaced as mid-span joints are not acceptable.

Any or all additional steel work or modifications required to attach the fibre cabling to the overhead transmission/ distribution line towers shall also be carried out by the Contractor. It shall be the Contractors responsibility to provide adequate communications among all crew members and support staff to ensure safe and successful installations.

## Cable Raceways

To the extent possible, existing cable raceways shall be utilised. The Contractor is required to provide and install any additional indoor cable raceways which may be required for proper implementation of the Communication System. This requirement shall be finalised during survey. The cable raceways shall conform to the following:

- All cable raceways shall be sized to support full loading requirements plus at least a 200% safety loading factor.

- Indoor cable raceways shall be fabricated from construction grade aluminium, galvanized iron or anodized sheet metal or any other suitable material approved by the Employer. Suitable anti-corrosion measures shall be provided. Steel fabricated raceways shall be finished inside and out, treated to resist rust and to form a metal-to- paint bond.

- Mechanical construction drawings of the cable raceways shall be submitted for Employer’s information & review.

## -------------------------------- ---------------- End of this Section------------------- ----------------------------