## Abstract
HUBLI ELECTRICITY SUPPLY COMPANY LIMITED
Estimate for Providing additional 3rd 5 MVA, 33/11KV power transformer at 33/11KV sub-station Athani in Athani Taluk, Belagavi District in 33KV S&L Division, Belagavi on PTK basis (5 MVA Power Transformer will be supplied by departmentally)
ABSTRACT
Sl. No | Particulars | Material | Labour | Civil | Total
1 | Materials cost (Exclusive of GST) | 7974811.1367 |  |  | 7974811.1367
2 | Labour charges+ Decommissioning (Exclusive of GST) |  | 219635.7742 |  | 219635.7742
3 | Civil Engineering Charges (Exclusive of GST) |  |  | 775707.8333 | 775707.8333 |  |  |  | 2.8062
4 | Basic rate | 7974811.1367 | 219635.7742 | 775707.8333 | 8970154.7442
5 | Area Specific Loading @ 5% on labour charges | 0 | 0 | 0 | 0
| Overhead Charges @ 10% on Sl No. 4 & 5 | 797481.1137 | 21963.5774 | 77570.7833 | 897015.4744
| Contractors Profit @ 10% on Sl No. Sl No. 4 & 5 | 797481.1137 | 21963.5774 | 77570.7833 | 897015.4744
7 | Cost of the Estimate /APT (Without GST) | 9569773.364 | 263562.929 | 930849.4 | 10764185.693 | 50614881.6107 |  | 48828398.671
% age of tender compenents included
38064212.978
| Executive Engineer (EL), |  |  | Superintending Enginner (El),
| Projects - 1 , HESCOM, Hubli |  |  | PMC, HESCOM, Hubli
-10764185.693
-1
21528371.386

## mat
HUBLI ELECTRICITY SUPPLY COMPANY LIMITED
Estimate for Providing additional 3rd 5 MVA, 33/11KV power transformer at 33/11KV sub-station Athani in Athani Taluk, Belagavi District in 33KV S&L Division, Belagavi on PTK basis (5 MVA Power Transformer will be supplied by departmentally)
PART-A (Material portion)
Sl. No. |  | Particulars | Unit | Qty | Rate | Amout in Rs. | Reamarks
1 | 2 | 3 | 4 | 5 |  | 7
HESCOM PORTION
A.1 |  | Power Transformers:
| a) | 33/11KV, 5 MVA, DELTA/STAR, DY 11, 3Ph, 50Hz,Core type winding with OLTC, RTCC panel etc., complete filled with Transil Oil and 10 % spare Oil in Non Returnable Drums (Power Transformer shall be supplied by departmentaly) (As per ESCOM's CSR- 2025-26 33KV Material. page No- 69 of 81 SL.No-1, Item No-1.01 ,Material Code-1.01)( Supplied Departmentally) | Nos | 0 | 6597322 | 0
Deloaded 21% on Estimate cost
A.2 |  | 33KV SF-6/ VCB Breakers:
| a) | 66 kV, 40 kA class, SF-6 Circuit Breaker with terminal connector suitable for Al. tube/conductor with spring/semi-pneumatic/pneumatic type operating mechanism and mounting structure etc., as per technical specification. (As per KPTCL SR 2025-26, Page No- 14, SL.No-278 | Nos | 1 | 645000 | 645000
A.3 |  | Control and relay panels Simplex type as per technical specifications (Control Voltage 110V DC) |  |  |  | 0
| a) | 33KV Panel for Overhead Line (KPTCL SR-2023-24, Page No:41,Sl. No-16 Item No:16.2.8,HSN Code,8537 Rs:214170 (33KV Panel rate) | panel | 0 | 178475 | 0 | Not updated in new SR
| b) | 5MVA, 33/11KV Transformer Panel (KPTCL SR-2023-24, Page No:41, Sl. No-16 Item No:16.2.7,HSN Code,8537 Rs:631620 (66KV Panel rate rate is considered due to non availability for 33 KV Panel in the CSR 2023-24) | panel | 1 | 526350 | 526350 | Not updated in new SR
A.4 |  | 33KV Current Transformers |  |  |  | 0
| a) | 36KV, 20KA CT of ratio 400-200/1-1-1A with rigid terminal connector suitable for Coyote ACSR conductor with marshallling Box for Incomer. (As per ESCOM's CSR- 2025-26 33KV Material. page No- 81 SL.No-6, Item No-2.01) | Nos | 0 | 57030 | 0
| b) | 36KV, 20KA CT of ratio 200-100/1-1-1A with rigid terminal connector suitable for Coyote ACSR conductor with marshallling Box for power transformer. (As per ESCOM's CSR- 2025-26 33KV Material. page No- 81 SL.No-6, Item No-2.02) | Nos | 3 | 57030 | 171090
| c) | 11kV NCTs 600-300/1-1-1A (for PCVCBs upto 10 MVA Transformer) (As per ESCOM's CSR- 2025-26 33KV Material. page No- 81 SL.No-14, Item No-2.10) | No's | 1 | 66582 | 66582
A.5 |  | 33KV Voltage Transformers |  |  |  | 0
| a) | Voltage Transformers 33 kV/√3 / 110 V/√3 - 110 V/√3 (As per ESCOM's CSR- 2025-26 33KV Material. page No- 81 SL.No-16, Item No-2.12) | No's | 0 | 53234 | 0
A.6 |  | Surge Arrestors, Metal Oxide, as per Technical Specification. |  |  |  | 0
| a) | 30KV, 10KA normal duty Polymeric with terminal connectors suitable for Coyote Conductor (As per ESCOM's CSR- 2025-26 33KV Material. page No- 81 SL.No-18, Item No-3.01) | No's | 3 | 11583 | 34749 | Not updated in new SR
| b) | 10 kV, 5 kA Lightning Arrester Polymeric type with GROUND DISCONNECTOR) ( As per ESCOM's CSR- 2025-26 33KV Material. page No- 13 SL.No-184 Item No-19.02) | Set (3 Nos) | 3 | 1735 | 5205 | Not updated in new SR
A.7 |  | 33 KV Isolators : |  |  |  | 0
| 1) | 33KV, 800A, 25 KA Class Double Break manually operated isolators with Pad connectors suitable for Coyote ACSR Conductor, as per technical specification with Solid Core, cylindrical post insulators |  |  |  | 0
| a) | a) 33 kV, 800 A, 25 kA Upright without Earth Switch (As per KPTCL SR- 2023-24 Page No.34 SL.No-9, Item No-9.14.1 HSN Code-8535, RS-84700/-) | Nos | 1 | 70583.3333 | 70583.3333 | Not updated in new SR
| 2) | 11 KV Isolators 400A with manually operated isolators with Pad connectors suitable for Lynx ACSR Conductor, as per technical specification with cylindrical post insulators |  |  |  | 0
| a) | 11KV 400A Special Roaster switch with H frame for mounting Structure. ( As per ESCOM's CSR- 2025-26. page No- 17 SL.No-220 Item No-24.09) | Set | 0 | 13295 | 0 | Not updated in new SR
| b) | 11KV 400A Double break GOS with H frame for mounting Structure(Dwg No. BESCOM/GM/QS&S/22 Dtd 24.11.2018), ( As per ESCOM's CSR- 2025-26 33KV Material. page No- 16 SL.No-215 Item No-24.04) & ( As per ESCOM's CSR- 2025-26 page No- 16 SL.No-217 Item No-24.06) | Set | 3 | 23987 | 71961 | Not updated in new SR
A.8 |  | 11kV Switch Gear |  |  |  | 0
| a) | 11 kV MCVCB, 350 MVA, 25 kA, 1250 A incomer, 800 A feeder (SCADA compatible)Incommer (KPTCL 25-26, Page No:12 Sl.No:237) | No | 1 | 869184.1667 | 869184.1667
| b) | 11 kV MCVCB, 350 MVA, 25 kA, 1250 A incomer, 800 A feeder (SCADA compatible) Feeder (KPTCL 25-26, Page No:12 Sl.No:238) | No | 3 | 773342.5 | 2320027.5 | Not updated in new SR
| c) | 11 kV MCVCB, 350 MVA, 25 kA, 1250 A incomer, 800 A feeder (SCADA compatible) Bus Coupler (KPTCL 23-24, Page No:29, Sl.No:4, item No:4.8) | No | 1 | 752411.6667 | 752411.6667 | Not updated in new SR
| d) | Annunciator Panel for the following combinations (for both MCVCB & PCVCB), 1IC+4F+1CB (As per KPTCL SR-2025-26, No- 13, SL.No-251) | No | 1 | 151921.6667 | 151921.6667 | Not updated in new SR
A.9 |  | MOUNTING STRUCTURES: With including fabrication and galvanisation. |  |  |  | 0
| a) | Mounting Structure: 33KV, 800A, 25 KA Class Double Break manually operated ISOLATOR Live point height 3750 mm - 2Nos. (As per KPTCL SR- 2025-26, No- 02, SL.No-16) ii) (The weight of structure is 0.240t X2 Nos=480t) | t | 0.24 | 106666.6667 | 25600
| b) | Mounting Structures:33KV Potential Trasformers -0.142x 3Nos =0.426 t (As per KPTCL SR 2025-26, Page No-245 Sl.NO:I,Item.No:E (3)(d), As per KPTCL SR- 2025-26, No- 02, SL.No-16) | t | 0 | 106666.6667 | 0
| c) | Mounting Structures:33KV Current Trasformers- 0.142x 3Nos =0.426 t As per KPTCL SR- 2025-26, No- 02, SL.No-16) | t | 0.426 | 106666.6667 | 45440 |  |  | 0.246
| d) | Mounting Structures:33KV Lightning Arrestors - 0.082 x 3 Nos =0.0.246 tAs per KPTCL SR- 2025-26, No- 02, SL.No-16) | t | 0.246 | 106666.6667 | 26240
| e) | Mounting Structures: P.I. Support (33kv side): 0.082x 9 Nos =0.738 t As per KPTCL SR- 2025-26, No- 02, SL.No-16) | t | 0.492 | 106666.6667 | 52480 |  | 0.492
| f) | Mounting Structures:11KV NCT 1 No. 0.146x 1 No =0.146 t As per KPTCL SR- 2025-26, No- 02, SL.No-16) | t | 0.146 | 106666.6667 | 15573.3333
| g) | Mounting Structures:High P.I. Support (11kv side) 6 Nos As per KPTCL SR- 2025-26, No- 02, SL.No-16) | t | 0.66 | 106666.6667 | 70400
| h) | Mounting Structures:High P.I. Support (11kv side),2 Nos Harizontal cross arm for support of 11 KV 3CX400 Sq.mm XLPE U.G cable 0.22x 2 Nos =0.44 t As per KPTCL SR- 2025-26, No- 02, SL.No-16) | t | 0.22 | 106666.6667 | 23466.6667
| i) | Bolts & Nuts for all Station Mounting Structures, such as, A)3T1- (0.017t), 3B1 (0.010t), As per KPTCL SR 2023-24, Page No. 244, Sl. No. I; Item No. (D)(i.ii). B)33KV PT (0.010t X 3 =0.000t)Asper KPTCL SR 2023-24, Page No. 245,Sl. No. I; Item No.(E)3 (d). C) 33KV CT (0.010t X 3 =0.030t) Asper KPTCL SR 2023-24, Page No.245,Sl. No.I; Item No.(E)2 (d). D) 33KV LAs( 0.005X3=0.015) Asper KPTCL SR 2023-24, Page No.245,Sl. No.I; Item No. E) 4(d). E) 33KV PI (0.005x 6 =0.030 t) ( Asper KPTCL SR 2023-24,Page No-247 Sl.NO:II, Item.No:E (iv), F)11KV NCT(0.011x 1 No =0.011t) (Asper KPTCL SR 2023-24, Page No-247 Sl.NO:II, Item.No:D(viii), G)11KV High P.I(0.011x 3 No =0.033t). (Asper KPTCL SR 2023-24, Page No-247 Sl.NO:II, Item.No:E(viii), (Bolts & Nuts Rate, As per KPTCL SR 2023-24; Page No-43;Sl.No.18 Item No.18.3) Rs 142780.00t | t | 0.129 | 118983.3333 | 15348.85 | Not updated in new SR |  |  | 0.129
A.10 | b) | S.M. Rail angle for Transformer plinth ( 2 nos. of 3m long) SM rail. (As Per KPTCL SR-2023-24, Page No:116, Sl.No.10, Set Rs=1626.00) and .M.S angle 75 x 75 x 6 mm angle iron 8 mtr long 0.2 MT each.(As Per PWD Electrical SR-2023-24, Page No:19, Sl.No.5.40, Item No:5.41.3, Per Mtr Rs:555 X 8 = Rs.4440.00) ,(1626+4440=6066.00) | Set | 1 | 5055 | 5055 | Not updated in new SR
A.11 |  | Conductors |  |  |  | 0
| a) | Lynx ACSR (30/2.79 mm Al + 7/2.79 mm St), Std Wt: 842 Kg/KM As per KPTCL SR- 2023-24, No- 02, SL.No-23) | Kms. | 0.25 | 187500 | 46875
| b) | Coyote ACSR (26/2.54 mm Al + 7/1.90 mm St), Std Wt: 521 Kg/KM As per ESCOM's CSR- 2025-26 33KV page No- SL.No- Item No-22.8)(Extracted from KPTCL SR) | Kms. | 0.25 | 135537 | 33884.25
A.12 |  | 11KV ODS: |  |  |  | 0
| a) | 9 Mtr. Long, 145kg RCC pole for 11KV ODS ( As per ESCOM's CSR- 2025-26 33KV Material. page No- 3 SL.No-1 Item No-1.01) | Nos | 0 | 6276 | 0 | Not updated in new SR
| b) | RCC Pole - 8 Mtr Long, 115 Kg WL for LED Light ( As per ESCOM's CSR- 2025-26. page No- 3 SL.No-3 Item No-1.03) | Nos | 0 | 4706 | 0 | Not updated in new SR
A.13 |  | 33 kV side Station Structure |  |  |  | 0
| a) | 11 Mtrs long I Beams of size (300*150mm)-vertical (4 nos.) (As per KPTCL SR- 2025-26, No- 02, SL.No-16) | MT | 1.608 | 106666.6667 | 171520 | Not updated in new SR | #REF! | 1.316 | 1608
| b) | 9 Mtrs long I Beams of size (300*150mm)- (6 nos.) for harizontal structure (As per As per KPTCL SR-2025-26, No- 02, SL.No-16) weight 0.329*4=1.316MT | MT | 1.316 | 106666.6667 | 140373.3333 | Not updated in new SR |  |  | 36.53 | 328.77
| c) | supply of Galvanised Bolts & Nuts (KPTCL 23-24, Page No:43, Sl.No:18, item No:18.3) | MT | 0.18 | 118983.3333 | 21417 | Not updated in new SR
A.14 |  | 11 KV D.P.Structures: |  |  |  | 0
| a) | D.P. Structures with hardware consisting of double power X-arms, horizonontal cross brace, cross braces, back cleat, strain plate, bolt & nuts, painted with two coats of metal primer and aluminium paint, etc as per drawing. ( As per ESCOM's CSR- 2025-26. page No- 17, SL.No-225 Item No-26.02) | Set | 3 | 7374 | 22122
A.15 |  | Control Cable with Accessories: (With glands/lugs/ferruels) |  |  |  | 0
| a) | 19 Core 2.5 Sq.mm (As per KPTCL SR- 2025-26, No- 10, SL.No-181) . | Kms. | 0.555 | 590833.3333 | 327912.5
| b) | 4 Core 6 Sq.mm (As per KPTCL SR-2023-24, Page No:40 Sl No-13, Item No:13.8, HSN Code:8544, Rs:247*1000=.247000 Total Rs =247000) | Kms. | 0.345 | 205833.3333 | 71012.5 | Not updated in new SR
| c) | 4 core 2.5 Sq.mm As per KPTCL SR-2025-26 No- 10, SL.No-176) | Kms. | 0.2 | 149166.6667 | 29833.3333
| d) | 2 core 2.5 Sq.mm As per KPTCL SR- 2025-26, No- 10, SL.No-175) | Kms. | 0.64 | 92500 | 59200
| e) | 10 Core 2.5 Sq.mm As per KPTCL SR- 2025-26, No- 10, SL.No-179) | Kms. | 0.07 | 340833.3333 | 23858.3333
A.16 |  | Insulators & Hardware materials: |  |  |  | 0
| a) | Pad clamp for Coyote ACSR As per As per ESCOM's CSR- 2025-26. page No- 7 SL.No-77 Item No-10.09 | Nos | 12 | 734 | 8808
| b) | Pad clamp for Lynx ACSR As per KPTCL SR- 2025-26, No- 3, SL.No-45) | Nos | 42 | 725 | 30450
| c) | T clamp for Coyote ACSR ( As per ESCOM's CSR- 2025-26. page No- 7 SL.No-75 Item No-10.07) | Nos | 12 | 426 | 5112
| d) | T clamp for Lynx ACSR As per KPTCL SR- 2025-26, No- 5, SL.No-87) | Nos | 45 | 526.6667 | 23700
| e) | 33KV CT bimetalic clamps for Lynx ACSR (As per present market rate) | Nos | 6 | 1000 | 6000
| f) | NCT Pad Clamp As per KPTCL SR- 2025-26, No- 16, SL.No-327) | Nos | 1 | 849.1667 | 849.1667
| g) | Post Insulator Clamps As per KPTCL SR- 2025-26, No- 5, SL.No-74) | Nos | 3 | 845.8333 | 2537.5
| h) | Terminal Connector Clamps Suitable for 36 kV class bushing to suit Coyote / Lynx conductor for HV Bushings of Power Transformers (Asper KPTCL SR-2023-24, Page No 135, Sl.No-E Item No-viii HSN Code:8536 Total Rs =512) | Nos | 3 | 426.6667 | 1280 | Not updated in new SR
| h) | Terminal Connector Clamps Suitable for 12.1 kV class bushing to suit Drake conductor for Bushings of Power Transformers (As per KPTCL SR-2023-24, Page No 135, Sl.No.2E Item No-ix HSN Code:8536 Total Rs.1113/-) | Nos | 4 | 927.5 | 3710 | Not updated in new SR
| i) | Strain Clamp for Lynx ACSR,( As per ESCOM's CSR- 2025-26. page No- 5 SL.No-46 Item No-5.16) | Nos | 55 | 588 | 32340 | Not updated in new SR
| j) | Solid Core Bus Post Insulator 33 kV As per KPTCL SR- 23-24, No- 11, SL.No-186) | Nos | 6 | 3060 | 18360
| k) | 70 KN Disc Insulators Ball and socket type ( As per ESCOM's CSR- 2025-26. page No- 82 SL.No-25 Item No-6.03) | Nos | 55 | 390 | 21450
| i) | I bolts (As per present market rate) | Nos | 30 | 55 | 1650
A.17 |  | Ground Mat & Earthing : |  |  |  | 0
| a) | Grounding of equipment by providing Cast iron pipe of 100 mm ID 13 mm thickness, 2.75 metre long with 2 part clamp out of G.I. Flat 50 X 6 mm continuously welded alround the pipe using cast iron welding electrodes as per drawing including the cost of excavation (All materials to be supplied by the contractor) (As per KPTCL SR-2023-24, Page No:115, Sl.No-6 Item No:c Material Rs-12792+3491 Labour | Set | 15 | 13569.1667 | 203537.5 | Not updated in new SR
| b) | Supplying & providing 450 mm dia 450 mm height 1.5" to 2" thick hume pipe collar (non pressure type) for earth pits including all lead and lifts etc.,.(As per KPTCL SR-2023-24, Page No:124, Sl.No-26 Item No:i Material Rs-1499.00 | Each | 15 | 1249.1667 | 18737.5 | Not updated in new SR
| c) | Grounding of equipment with 50X6 mm GI flat & connecting equipment to the earth mat / ground pit. Each point of Earthing with all formation works like bending, twisting, drilling of holes & conncting by welding (inclusive of all T & P consumables) to the earth mat/ ground pit/point of earth connection, all the materails supplied by the contractor (As per KPTCL SR-2023-24, Page No:123, Sl.No-26 Item No:i Material Rs-335.00 | Rmt | 300 | 279.1667 | 83750 | Not updated in new SR
| d) | Supplying and laying of MS Flats of various sizes, welding and applying ACB paint to welded portion and covering with sodium bentonite clay as per the drawing/standard specification and consolidation (MS Flat of size 50x6 ) (As per KPTCL SR-2023-24, Page No:123, Sl.No-26 Item No:f Material Rs-404.00 | m | 350 | 336.6667 | 117833.3333 | Not updated in new SR
A.18 |  | 11kV, 3X400 Sqmm Core, XLPE HTUG Cable (ROUND Armoured Cable) |  |  |  | 0
| a) | 11 kV, 3x400Sqmm Core, XPLE HTUG Cable with pressure extruded inner sheeth, ROUND WIRE ARMOURED as per IS-7098 (Part-2) Armouring wires dia and Resistivity as per IS-3975 ( As per ESCOM's CSR- 2025-26 33KV Material. page No- 128 SL.No-1) | Kms. | 0.11 | 2857768 | 314354.48 | Not updated in new SR
| b) | Cable Covering Tiles 250x125x40 mm or 125x125x40mm. ( As per ESCOM's CSR- 2025-26 33KV Material. page No- 128 SL.No-5) | Nos | 100 | 8.98 | 898 | Not updated in new SR
|  |  | Nos | 100 | 4.49 | 449
| c) | Artificial/Manufacture Sand (Extracted from Vol-1, PWD SR Sl No. 62),( As per ESCOM's CSR- 2025-26 33KV Material. page No- 128 SL.No-6) | Cmt | 20 | 1620 | 32400 | Not updated in new SR
| d) | GI Pipe, 150 mm Dia for drain crossing, cable raising etc., (( As per ESCOM's CSR- 2025-26 33KV Material. page No- 128 SL.No-9) | Mtr | 16 | 1532 | 24512 | Not updated in new SR
| e) | Route and Joint indicating stones ( As per ESCOM's CSR- 2025-26 33KV Material. page No- 128 SL.No-10) | Nos | 10 | 117 | 1170 | Not updated in new SR
|  | 11kV Jointing and Cable Termination Kits |  |  |  | 0 | Not updated in new SR
| f) | Heat Shrinkable Outdoor Type Cable Termination Kit for XLPE Cable 3X400 Sqmm As per ESCOMs SR- 2025-26, No- 20 of 50, SL.No-419) | Per Kit | 4 | 4694 | 18776 | Not updated in new SR
| g) | 11KV, 3 Core, 240 Sqmm XLPE HT UG cable (Round Armord). as per IS-3975 As per ESCOMs SR- 2023-24, No- 15 of 50, SL.No-321) | Kms | 0.105 | 4218 | 442.89 | Not updated in new SR
| h) | Heat Shrinkable Outdoor Type Cable Termination Kit for XLPE Cable 3X240 Sqmm (As per ESCOMs SR- 2025-26, No- 32, SL.No-425) | Per kit | 3 | 4659 | 13977 | Not updated in new SR
| i) | Heat Shrinkable Indoor Type Cable Termination Kit for XLPE Cable 3X240 Sqmm (As per ESCOMs SR- 2025-26, No- 33, SL.No-428) | Per kit | 3 | 4110 | 12330 | Not updated in new SR
A.19 |  | Miscellaneous items |  |  |  | 0
| a) | Caution/Danger Board As per ESCOMs SR- 2025-26, No- 52, SL.No-710) | Nos | 6 | 131 | 786
| b) | Phase plates (As per KPTCL SR 2023-24, Page No.43, Sl. No.19, Item No,19.1, Rs.528/- | Set (3 Nos) | 3 | 440 | 1320
| c) | Name Plates for equipment/Earth Pit (As per present market rate due to non availability of rates in the current SR) | Nos | 20 | 250 | 5000 | Not updated in new SR
| d) | Name plate for feeders and banks (As per present market rate due to non availability of rates in the current SR) | Nos | 4 | 250 | 1000 | Not updated in new SR
A.20 |  | FIRE FIGHTING EQUIPMENT (with necessary mounting stand) |  |  |  | 0
| a) | Foam type extinguisher (Mech) 9.00 Ltr. Capacity. (As per KPTCL SR 2023-24, Page No.74 Sl.No.51, Item No,51.1.2, Rs.4118/- | Nos | 4 | 3431.6667 | 13726.6667 | Not updated in new SR
| b) | Carbon dioxide type 4.5Kg. Capacity (As per KPTCL SR 2023-24, Page No.74 Sl.No.51, Item No,51.5.2, Rs8691/-) | Nos | 4 | 7242.5 | 28970 | Not updated in new SR
A.21 |  | Station Service Equipments: |  |  |  | 0
| a) | Single line diagram Photo sheet paper (Size 20x20 inch) (As per present market rate) | Nos | 2 | 2000 | 4000 | Not updated in new SR
| b) | Supplying and installation of Rubber mat 1mtr x 1mtr -1Omm thick.complete including cost of materials, labour, usage charges of machinery complete as per specifications. (As per PWD SR 2023-24, Page No.93 of 105 Sl.No.15, Item No,15.117, Rs 1900/-) | Nos | 5 | 1583.3333 | 7916.6667 | Not updated in new SR
Total material cost | [5 empty] | 7974811.1367 |  |  |  | 8706840.62

## Erre
HUBLI ELECTRICITY SUPPLY COMPANY LIMITED
Estimate for Providing additional 3rd 5 MVA, 33/11KV power transformer at 33/11KV sub-station Athani in Athani Taluk, Belagavi District in 33KV S&L Division, Belagavi on PTK basis (5 MVA Power Transformer will be supplied by departmentally)
PART-B (Electricals Erection Works)
Sl. No. |  | Particulars | Unit | Qty | Rate | Amout in Rs.
1 | 1 |  | 3 | 4 |  | 6
B.1 | a) | Power Transformers: Moving the Transformer to the plinth. (15 MT for 10 mtrs) on ramp. (As per KPTCL SR-2023-24 Page No-116, Sl.No-9, Item No-(a)) Rs-80/- | per MT/ mtr | 300 | 66.6667 | 20000 | 300
| b) | Assembly of Transformer parts like bushings, radiators, filling oil into Transformer etc., for the total weight of the Transformer. (As per KPTCL SR-2023-24 Page No-116, Sl.No-9, Item No-(b)) 1134.00 | MT | 15 | 945 | 14175 |  |  |  | 150
| c) | Filtration of oil using filter set of the contractor, to bring the insulation value to I.E. Specifications.(As per KPTCL SR-2023-24 Page No-116, Sl.No-9, Item No-(d)) Rs-7.00 | ltrs | 3500 | 5.8333 | 20416.6667
| d) | 5 MVA to 6.3/8 MVA Tr Wiring: Identification of wires,Wiring of Transformer marshalling box, bucholtz relay, OLTC upto control panel Ferruling crimping and termination of wires. Wiring of Protective Devices, OLTC, RTCC , fixing Thermometer, etc.,including assisting in Testing & Commissioning: (As per KPTCL SR-2023-24 Labour,Page No-116, Sl.No-9, Item No-(f&i)) 6708 | per transfor mer | 1 | 5590 | 5590
| e) | Fabrication of Transformer railing & embedding in Transformer plinth. (As per KPTCL SR-2023-24 Labour, Page No-116, Sl.No-10,Rs-1626 | Set | 1 | 1355 | 1355
B.2 | a) | 33KV SF-6/ VCB Breakers: Breaker Erection, assembly, alignment & wiring of breakers with its connected equipments including movement from the point of unloading to the point of erection. (As per KPTCL SR-2023-24 Labour,Page No-117, Sl.No-13, Item No-(a) Rs-5934 | Per Set | 1 | 4945 | 4945
| b) | Assisting in Testing & Commissioning: (As per KPTCL SR-2023-24 Labour, Page No-117, Sl.No-13, Item No-(b) Rs-1938.00 | Set | 1 | 1615 | 1615
| c) | Wiring : Identification, Ferruling crimping and termination of wires in Breaker & Wiring up to control panel/Relay panels. (As per KPTCL SR-2023-24 Labour,Page No-117, Sl.No-13, Item No-(c) Rs-8487 | Set | 1 | 7072.5 | 7072.5
B.3 | a) | Control Panels : Erection of control panel, auxilary panel, carrier cabinet etc., alignment and fixing properly to foundation base including movement from the point of unloading to the point of erection.(As per KPTCL SR-2023-24 Labour,Page No-120, Sl.No-23, Item No-(a) Rs-4191) | Nos. | 1 | 3492.5 | 3492.5
| b) | Wiring & Assisting in Testing & Commissioning: (As per KPTCL SR-2023-24 Labour,Page No-120, Sl.No-23, Item No-(b) Rs-7612.00 | Nos. | 1 | 6343.3333 | 6343.3333
B.4 | a) | Erection of CTs and wiring including movement from the point of unloading to the point of erection. (As per KPTCL CSR 23-24, Labour, Page No: 118, Sl No.: 14 a) Rs-2199 | Set (3 Nos) | 1 | 1832.5 | 1832.5
| b) | Assisting in Testing & Commissioning: (As per KPTCL CSR 23-24, Labour, Page No: 118, Sl No.: 14 (b) Rs-768.00 | Set (3 Nos) | 1 | 640 | 640
| c) | Welding work for alteration of existing PI mounting structure to errect the incomer Current Transformers (As per present market rates) | No's | 3 | 416.6667 | 1250
B.5 | a) | Erection of NCTs including movement from the point of unloading to the point of erection with grounding connections (As perKPTCL CSR 23-24, Labour, Page No: 118, Sl No.:15(a) Rs-733.00 | Set | 1 | 610.8333 | 610.8333
| b) | Assisting in Testing & Commissioning:(As per KPTCL CSR 2023-24, Labour, Page No: 118, Sl No.:15(c) Rs-99.00 | Set | 1 | 82.5 | 82.5
B.6 | a) | Releasing of Existing PTs and wiring including movement from the point of unloading to the point of erection. (As per KPTCL CSR 2023-24, Labour, Page No: 118, Sl No.: 14 (a) Rs-2199.00 | Set (3 Nos) | 0 | 1832.5 | 0
| b) | Re-Erection of Existing PTs and wiring including movement from the point of unloading to the point of erection. (As per KPTCL CSR 2023-24, Labour, Page No: 118, Sl No.: 14 (a) Rs-2199.00X90%=1979.10 | Set (3 Nos) | 0 | 1649.25 | 0 | 1979.1
| c) | Assisting in Testing & Commissioning: (As per KPTCL CSR 23-24, Labour, Page No: 118, Sl No.: 14 (b) Rs-768.00 | Set (3 Nos) | 0 | 640 | 0
B.7 | a) | Erection of Lightning arrestors and wiring including movement from the point of unloading to the point of erection (33 KV) (As per KPTCL CSR 23-24, Labour, page No119, Sl.No:18 )Rs.333/- | Set | 1 | 277.5 | 277.5
| b) | 9 KV, 5 KA class (Station type) (11kv) (As per ESCOMS SR 23-24, Labour, page No: 48 of 81, Sl.No:101, item no: 13.06) Rs-119.00 | Set (3 Nos) | 3 | 99.1667 | 297.5
B.8 | 1) | 33 KV Isolators : |  |  | 0 | 0
| a) | Erection of Isolators (33 KV) Assembly, Errection alignment and wiring including movement from the point of unloading to the point of erection.(Upright type),( As per KPTCL CSR 23-24, Labour, Pg No: 119, Sl No.: 17 A(i) ,) Rs-1319.00 ) | Set | 1 | 1099.1667 | 1099.1667
| b) | Assisting in Testing and Commissioning ( KPTCL CSR 23-24, Labour, Pg No:119 , Sl No.: 17 E(i) ,) Rs-191/- | Nos | 1 | 159.1667 | 159.1667
| 2) | 11KV Isolators: |  |  | 0 | 0
| a) | Erection of 400A, special roster switch with H-frame & clamps to be mounted on DP (As per ESCOM SR- 2025-26, Labour, Pg No:58 Sl No.: 37 ,itme no: 2.09) (Rs - 288) (Total - 1082+288=1370) | Nos | 0 | 1370 | 0
| b) | Erection of 11 kV, 400 Amps Double Break GOS (As per ESCOM SR- 2025-26, Labour, Pg No:58 Sl No.: 37 ,itme no: 2.09) (Rs - 288) (Total - 1082+288=1370) | Nos | 3 | 1370 | 4110
B.9 | a) | 11 KV Switchgear : Erection, alignment and fixing to the foundation, indoor/outdoor 11KV switchgear Panel/unit including movement from the point of unloading to the point of erection. (1Bank+3 feeders+busu coupler) (As per KPTCL SR 23-24, Labour, page No: 121, Sl.No:24 a (i) ) Rs-2081/-) | Per Panel | 5 | 1734.1667 | 8670.8333
| b) | Wiring and assisting in Testing & Commissioning: (As per KPTCL SR 23-24, Labour, page No: 122, Sl.No:24 b (i) ) Rs-941.00 | Per Panel. | 5 | 784.1667 | 3920.8333
B.10 | a) | 33KV Station structures: |  |  |  | 0
|  | Erection, alignment & assembly of fabricated steel lattice structure, pedestal structures & Mounting structures, for 3T1 Tower ,3B1 Beam,G.O.S., CTs, PTs LAs, 11KVNCT, High P.I, etc. (As per KPTCL SR 23-24, Labour, Page No: 116, Sl No.: 8, (b) , Rs-5723.00 | t | 2.43 | 3257.405 | 7915.4942
B.11 | a) | Bus Formation |  |  |  | 0
|  | Formation of cross bus in each individual bay using Lynx/Coyote -Single/Double conductor with fixing of insulators, spacers, levelling the strung conductors to the required height above the equipment including providing jumps to inter-connect different segments of the main bus. ( As per KPTCL SR 23-24, Labour, Page No: 122, Sl No.: 25) Rs-7364.00 (Incuding 33KV Bus Formation) | Per bay | 4 | 6136.6667 | 24546.6667
B.12 | a) | 11KV ODS: |  |  |  | 0
|  | 1) Digging of Pit 1.8 Mtr depth (Ordinary Soil) for errection of 9Mtr 11KV ODS pole- ESCOMs Labour (As per ESCOMs Labour SR-2025-26 Page No- 57 Sl.No-1 Item No-1.1.1 RS- 561) 2) Errection of 9 Mtr. Long, 145kg RCC pole for 11KV ODS. (As per ESCOMs Labour SR-2025-26 Page No- 58 Sl.No-30 Item No-2.02) RS-991 (Total Rs 561+9991=1552) | Nos | 0 | 1552 | 0
| b) | 1) Digging of Pit 1.6 Mtr depth (Ordinary Soil) for erection of 7.5/8 Mtr Long Steel/RCC pole for LED Light (As per ESCOMs Labour SR-25-26 Page No- 57 Sl.No-5 Item No-1.2.1 RS-449) 2)Errection of RCC Pole - 8 Mtr Long, 115 Kg WL. (As per ESCOMs Labour SR-2025-26 Page No- 58 Sl.No-29 Item No-2.01) RS-821 Total Rs-1270 (Total Rs 449+821=1552) | Nos | 0 | 1270 | 0
| c) | Supplying and fixing angle iron frame work fabricated out of M.S. angle iron.. and M.S. Flat......with bolts, washers etc., and painted with 2 coats of red oxide and then two coats of approved paint for 11 KV ODS mounting structure using 50 x 100 x 50 x 6 mm C channel MS, each 4.0 mtr long , As per PWD Electrical Page 19 Sl.No-5.41.4 Rs-Per Mtr-756.00 28NosX4Mtr=112 Mtr | Mtr | 0 | 630 | 0 |  | 112
B.13 |  | Erection of 2 Pole DP Structure using RCC/PSCC Pole 9 to 10 Mtr long (As per ESCOMs Labour SR-2025-26 Page No- 58 Sl.No-34 Item No-2.06) | Per Structure | 3 | 3682 | 11046 | 1403 only dp |  | 1341
B.14 |  | Laying of control cables from equipments to control panels. |  |  |  | 0
| a) | 19 Core 2.5 Sq.mm (As per KPTCL SR 23-24, Labour, page No: 120, Sl.No:22, (b) Rs- Per Mtr-15.00 | Rmtr | 555 | 12.5 | 6937.5
| b) | 4 Core 6 Sq.mm (As per KPTCL SR 23-24, Labour, page No: 120, Sl.No:22, (b) Rs- Per Mtr-15.00 | Rmtr | 345 | 12.5 | 4312.5
| c) | 4 core 2.5 Sq.mm (As per KPTCL SR 23-24, Labour, page No: 120, Sl.No:22, (b) Rs- Per Mtr-15.00 | Rmtr | 200 | 12.5 | 2500
| d) | 2 core 2.5 Sq.mm (As per KPTCL SR 23-24, Labour, page No: 120, Sl.No:22, (b) Rs- Per Mtr-15.00 | Rmtr | 640 | 12.5 | 8000
| e) | 10 core 2.5 Sq.mm (As per KPTCL SR 23-24, Labour, page No: 120, Sl.No:22, (b) Rs- Per Mtr-15.00 | Rmtr | 70 | 12.5 | 875
A.15 |  | 11kV, 3 Core, XLPE HTUG Cable (ROUND Armoured Cable) |  |  |  | 0
| a) | a) Cable trench excavation, 22x0.6x1=13.2, Ordinary soil (HESCOM SR-2025-26,Labour, Cost data sheet-23, Sl No- 11 (a) . | Cmt | 0 | 228 | 0
| b) | Laying of cable in trench. (HESCOM SR-2025-26,Labour, Cost data sheet-23, Sl No- 11 (b) . | KM | 0.11 | 58866 | 6475.26
| c) | Refilling and consolidation (HESCOM SR-2025-26,Labour, Cost data sheet-23, Sl No- 11 (g) . | Cmt | 20 | 143 | 2860 |  |  | 40000
| d) | Heat Shrinkable Outdoor Type Cable Termination Kit for XLPE Cable 3X400 Sqmm (HESCOM SR-2025-26,Labour, Cost data sheet-23, Sl No- 11 (g) . | Per Kit | 4 | 2368 | 9472
| e) | Covering the cable with tile (As per KPTCL SR- 2023-24, Page No- 45 of 50, SL.No-257) | KM | 0.02 | 4491 | 89.82
| f) | Spreading Sand and forming with Sand round the Cable (BESCOM SR-2023-24,Labour,Cost data sheet-284 | KM | 0.15 | 13220 | 1983
| g) | Laying of GI Pipe (HESCOM SR-2025-26,Labour ,Cost data sheet-23, Sl No- 11 (i) Rs:93 | Mtr | 16 | 83 | 1328
| h) | Laying of Route and Joint indicating stone (As per KPTCL SR- 2025-26, Page No- 34 of 50, SL.No-2, 55 of 50, SL.No-258) | Nos | 10 | 103 | 1030
| i) | 11KV, 3 Core, 240 Sqmm XLPE HT UG cable (Round Armord). As per ESCOM SR- 2023-24, Page No- 41 of 50, SL.No-172) . | Mtr | 105 | 57.14 | 5999.7
| j) | Cable Termination Kit Outdoor HS Type Suitable for 240 Sqmm Cable HESCOM SR 23-24 Labour charge page No: 42 of 50 Sl.No: 183, | Nos | 3 | 2368 | 7104
| k) | Cable Termination Kit Indoor HS Type Suitable for 240 Sqmm Cable HESCOM SR 23-24 Labour charge page No: 42 of 50 Sl.No: 183, | Nos | 3 | 2368 | 7104
A.16 |  | Miscellaneous items |  |  |  | 0
| a) | Fixing Caution/Danger Boards (As per ESCOM SR- 2025-26, Labour, Pg No:60 Sl No.: 63 ,itme no:5.15) | Nos | 6 | 71 | 426
| b) | Fixing Phase Plates As per KPTCL Labour SR 23-24,Pg No.113 ,Sl No.3(c) Rs-238 | Set (3Nos) | 3 | 198.3333 | 595 | 71.5986
| c) | Fixing Name Plates for equipment/Earth Pit ,KPTCL SR 21-22, page No-09 of 27 Sl No-7 Item No:- (d), Labour Charge Rs.54 | Nos | 20 | 45 | 900
| d) | Name plate for feeders and banks KPTCL SR 21-22 , Labour Charge No-09 of 27 Sl No-7, Item No:- (d),Rate Rs.54 | Nos | 4 | 45 | 180
A-17 |  | Fixing halogen/metal halide /SVL/IL/LED floodlight fitting over existing pole / wall ceiling including clamps, bolts, nuts and wiring using suitable capacity wires. As per PWD Ele SR 2-2023-24 Page No-56 Of 105,Item No:13.5 | Each | 0 | 135 | 0
A-18 | a) | Existing 63KVA Auxillary Transformers |  |  |  | 0
|  | Releasing of Existing 63KVA station Auxillary TC Asper BESCOMs SR-2023-24 Labour Charge Cast Data sheet No-25 Sl No-5, Rate Rs.1828X90%= | No | 0 | 1370.7 | 0 | 1073.7
| b) | Re-Erection of Existing 63KVA Station Auxillary TC (As per KPTCL SR- 2023-24, Page No-35 of 50, SL.No-46) | No | 0 | 1523 | 0
Total Labour cost | [5 empty] | 219635.7742 | 196888.88

## Civil (2)
HUBLI ELECTRICITY SUPPLY COMPANY LIMITED
Estimate for Providing additional 3rd 5 MVA, 33/11KV power transformer at 33/11KV sub-station Athani in Athani Taluk, Belagavi District in 33KV S&L Division, Belagavi on PTK basis (5 MVA Power Transformer will be supplied by departmentally)
PART-C-(CIVIL WORKS)
Sl No. | Item Description |  | Unit | Qty | Unit Price (Rs) | Total Price (Rs)
1 | 2 |  | 3 | 4 |  | 6
C |  | SCHEDULE OF ITEMS FOR ASSOCIATED CIVIL WORKS AND STRUCTURES:
C.1 |  | Cable Trenches including road crossing :
| a) | RCC Cable duct for laying of control cables with cable tray.(Duct size:1 mtr WidthX 1 mtr DepthX 37 Mtr Length including 33 KV and 11 KV side) | Mtrs | 0 | 6387.5 | 0
| b) | b) Providing and Laying RCC Hume pipe sub ducts using NP 2 class 300mm dia Hume pipe including cost of Excavation, laying charges and back filling wherever required as per technical specification and enclosed drawings including cost of all materials, labour, etc., complete. | Rmtrs | 0 | 710.8333 | 0
| c) | Cable duct covers RCC made with suitable size to cover the duct length of 35 Mtrs ( of Size 1m x 1m x 0.15m) | Nos | 0 | 1411.6667 | 0
C.2 |  | SITE SURFACING: Jelly Spreading (20-25 mm) : Supplying and providing jelly in the station yard of uniform thickness of 100 mm including the cost of materials, labour charges, required tools and plants etc., complete. Work shall be carried out as per the instructions of Engineer- in-charge of works as per the standard procedure(As per KPTCL SR 2023-24,Page No.158,Sl.No.1) | Cmt | 73.8 | 1477.5 | 109039.5
C.3 |  | Foundations: Engineering, supply of all labour,material and construction of RCC footing including the cost of excavation, cement concreting, reinforcement, backfilling, waterproof cement painting, for all works, grouting underpinning etc ,for the following works |  |  | 0 | 0
| a) | 9 mtrs long RCC poles for ODS (As per ESCOM's SR 2023-24,Base concreting Rs.312+Pole concreting Rs.3434,Coping Rs.312) | No's | 0 | 3381.6667 | 0
| b) | 8 mtrs long RCC poles for station Yard lights (As per ESCOM's SR 2023-24,Base concreting Rs.312+Pole concreting Rs.1498+Coping Rs.312) | No's | 0 | 1760 | 0
| c) | 33KV CT support structure (0.95 mtrX0.55 mtr X 1mtr Depth),with M-20 Concreting,PCC of M-10 and FE-550 TMT steel | Nos | 3 | 4708.3333 | 14125
| d) | 33KV Surge arrestor support structure (0.95 mtrX0.55 mtr X 1mtr Depth),with M-20 Concreting,PCC of M-10 and FE-550 TMT steel | Nos | 3 | 4708.3333 | 14125
| e) | PI support structure (0.95 mtrX0.55 mtr X 1mtr Depth),with M-20 Concreting,PCC of M-10 and FE-550 TMT steel | Nos | 3 | 4708.3333 | 14125
| f) | 11 KV NCT mounting structure (0.95 mtrX0.55 mtr X 1mtr Depth),with M-20 Concreting,PCC of M-10 and FE-550 TMT steel | Nos | 1 | 4950.8333 | 4950.8333
| g) | 33KV Isolators support structure(0.95 mtr X 0.45 mtr X 1mtrDepth),with M-20 Concreting,PCC of M-10 and FE-550 TMT steel | Set | 1 | 4728.3333 | 4728.3333
| h) | PI support structure for raising the U.G cable (0.95 mtrX0.55 mtr X 1mtr Depth),with M-20 Concreting,PCC of M-10 and FE-550 TMT steel | No. | 6 | 4708.3333 | 28250
| i) | 11 Mtrs long I Beams of size (300*150mm)-vertical (4 nos.) (0.95 mtrX0.55 mtr X 1mtr Depth),with M-20 Concreting,PCC of M-10 and FE-550 TMT steel | No. | 4 | 4708.3333 | 18833.3333
| j) | 9 Mtrs long I Beams of size (300*150mm)- (6 nos.) for harizontal structure (0.95 mtrX0.55 mtr X 1mtr Depth),with M-20 Concreting,PCC of M-10 and FE-550 TMT steel | No. | 6 | 4708.3333 | 28250
C.4 |  | Transformer foundation and associated rail track: |  |  | 0 | 0
|  | Design, Engineering,supply of material / equuipment, labour and construction of Tr. Foundation by providing all associated works, rail tracks jacking pads, anchor block RCC, PCC misscellanellaneous structural steel including MS, grouting gravel filling pylon support system and other items not mentioned herein, but required for the completion of the work as per the technical spcfication and drawings |  |  | 0 | 0
| a) | 5 MVA, 33/11 KV Transformer (3.3 mtr Width X 3.3 mtr Length X 3 mtr Depth) | Nos | 1 | 256005.8333 | 256005.8333
C.5 | a) | SF-6 Breaker foundation, 33KV SF-6 Breaker foundation as per approved design and drawing including supply of material and labour | Nos | 1 | 21872.5 | 21872.5
C.6 |  | Providing PVC ringtite pipes conforming to IS 4985:2000 with latest amendments and conveying to worksite, rolling and lowering into trenches, laying true to line and level and perfect linking at joints, testing and commissioning, including loading unloading at both destinations and cuts of pipes wherever necessary including jointing of PVC pipes and specials (excluding cost of specials) with jointing of approved type, with all labour with all lead & lift including encasing the pipe alround to a depth of not less than 15 cms. with soft gravel or selected earth available from the excavation etc. complete and giving necessary hydraulic test to the required pressure as per ISS (Contractor will make his own arrangements for procuring water for testing) etc. complete For: |  |  | 0 | 0
| a) | PVC pipes 63mm dia., 6 kg/sqcm & class 3 | Mtrs | 25 | 134.1667 | 3354.1667
| b) | PVC pipes 75mm dia., 6 kg/sqcm & class 3 | Mtrs | 25 | 183.3333 | 4583.3333
C.7 | a) | Earth mat formation : |  |  | 0 | 0
|  | Excavation, formation, refilling. | CMT | 304 | 168.3333 | 51173.3333
C.8 | a) | Design, Engineering,supply of material / equuipment, labour and construction of 11 KV out door PCVCB foundation by providing all associated works as per standard and approved specification. | No's | 5 | 36021.6667 | 180108.3333 | 23573(As per estimate)
| b) | Design, Engineering,supply of material / equuipment, labour and construction of 11 KV out door Capacitor Bank cells foundation by providing all associated works as per standard and approved specification. | Set | 1 | 22183.3333 | 22183.3333
C.9 |  | Station security fencing with foundation | Rmtrs | 0 | 4461.6667 | 0
|  | Total Civil cost |  |  |  | 775707.8333