## Abstract (2)
HUBLI ELECTRICITY SUPPLY COMPANY LIMITED
Construction of S/C 33 KV new line from proposed 110/33/11 KV MUSS Hanamapur to the existing 33/11 KV MUSS Muragundi for a distance of 8.2 Kms using coyote ACSR for providing second source in 33KV S&L Division,Belagavi on total turnkey basis.
ABSTRACT
Sl. No | Particulars | Material | Labour | Civil | Total
1 | Materials cost (Exclusive of GST) | 9136568.9469 |  |  | 9136568.9469
2 | Labour charges+ Decommissioning (Exclusive of GST) |  | 2409474.9825 |  | 2409474.9825
3 | Civil Engineering Charges (Exclusive of GST) |  |  | 26290 | 26290 |  |  |  | 2.8062
4 | Basic rate | 9136568.9469 | 2409474.9825 | 26290 | 11572333.9294
5 | Area Specific Loading @ 5% on labour charges | 0 | 0 | 0 | 0
| Overhead Charges @ 10% on Sl No. 4 & 5 | 913656.8947 | 240947.4983 | 2629 | 1157233.3929
| Contractors Profit @ 10% on Sl No. Sl No. 4 & 5 | 913656.8947 | 240947.4983 | 2629 | 1157233.3929
7 | Cost of the Estimate /APT (Without GST) | 10963882.7363 | 2891369.979 | 31548 | 13886800.7153 | 50614881.6107 |  | 48828398.671
| % age of tender compenents included | [8 empty] | 236
34941597.9556
| Executive Engineer (EL), |  |  | Superintending Enginner (El),
| Projects - 1 , HESCOM, Hubli |  |  | PMC, HESCOM, Hubli
-13886800.7153
-1
27773601.4307

## Mat&Lab
HUBLI ELECTRICITY SUPPLY COMPANY LIMITED
Construction of S/C 33 KV new line from proposed 110/33/11 KV MUSS Hanamapur to the existing 33/11 KV MUSS Muragundi for a distance of 8.2 Kms using coyote ACSR for providing second source in 33KV S&L Division,Belagavi on total turnkey basis.
PART A 33KV line
Sl. No | Particulars | Unit | Qty | Material Cost |  | Labour rate |  | 39
|  |  |  | Unit rate as per SR 25-26 | Amount | Unit rate as per SR 25-26 | Amount | 15 |  |  |  | Remarks
1 | Supply and errection of 9.5 Mtr long, 350 kg WL RCC Three pole structure of including transportation to the work site, with all lead and lift from the factory and head load from the nearest road, digging pit to a depth or 2.0M. giving a coating of coal for aligning if required, refilling the soil, ramming etc; complete including providing pole base concreting with CC 1:4:8 for pole base and concreting the pole and copping with CC 1:2:4 using all materials such as cement, sand jelly, etc; complete including consolidating, curing etc; complete for each pole . | Set | 2 | 42323 | 84646 | 16448 | 32896 | [5 empty] | #REF! | #REF!
| Supply of 9.5 Mtr long, 350 kg WL RCC for 3 pole structure (As per KPTCL SR- 2025-26, Page No- 3 of 50, SL.No-08) (Rs.10015 X 3 = 30045) | [11 empty] | #REF! | #REF!
| Three pole structure for 33kV. (As per KPTCL SR- 2025-26, Page No- 82 of 84, SL.No-13) (Rs. 6139*2=12278) | [7 empty] | 30045 | 6833.0579 |  |  | #REF! | #REF! |  | 42323
| Concreting materials for 9.5 Mtr long, 350 kg WL RCC (HESCOM CSR 23-24, 11 KV Labour Page No:8, Sl.No:26 A(a), B(a), C(a), (Rs. 312+3746+312 =4370x3 Nos= 13110.00) | [7 empty] | 12070 |  |  |  | #REF! | #REF! |  | 50787.6
| Erection of three pole structure using 9.5 Mtr long, 350 kg WL RCC pole (HESCOM CSR 25-26 Page No 35 of 50, Sl No: 34 , Rs:3682*2=7364 in this amount less the errection chargers of 1No's 9.5mtr RCC pole Rs:1590, Total amount: 7364-5523) | [7 empty] | 42115 |  |  |  | #REF! | #REF! |  | 12278 |  |  | 4987.6033
2 | Supply and errection of 9.5 Mtr long, 350 kg WL RCC Double Pole Structure of including transportation to the work site, with all lead and lift from the factory and head load from the nearest road, digging pit to a depth or 2.0M. giving a coating of coal for aligning if required, refilling the soil, ramming etc; complete including providing pole base concreting with CC 1:4:8 for pole base and concreting the pole and copping with CC 1:2:4 using all materials such as cement, sand jelly, etc; complete including consolidating, curing etc; complete for each pole . | Set | 22 | 26169 | 575718 | 13544 | 297968 |  |  |  | 2806 |  | #REF! | #REF!
| Supply of 9.5 Mtr long, 350 kg WL RCC for two pole structure as per HESCOM CSR 25-26 11 KV system, Page No: 3, Sl No.: 08, Item.No.: 1.08 (Rs.10015 X 2 = 20030) | [7 empty] | 20030 |  |  |  | #REF! | #REF!
| Double pole structure for 33kV (HESCOM CSR 25-26, 33 KV system, Page No: 69, Sl No.: 13, Item No.: 6.07 (Rs. 6139*1=6139) | [8 empty] | 2065 |  |  | #REF! | #REF!
| Concreting materials for 9.5 Mtr long, 350 kg WL RCC (HESCOM CSR 23-24, 11 KV Labour Page No:8, Sl.No:26 A(a), B(a), C(a), (Rs. 312+3746+312 =4370*2=8740) | [6 empty] | 8502 |  |  |  |  | #REF! | #REF!
| Erection of double pole structure using 9.5 Mtr long, 350 kg WL RCC pole (HESCOM CSR 25-26 Page No 35 of 50, Sl No: 34 Rs:4804) | [7 empty] | 3472 |  |  |  | #REF! | #REF!
3 | Supply and errection of 9.5 Mtr long, 350 kg WL RCC Single pole of including transportation to the work site, with all lead and lift from the factory and head load from the nearest road, digging pit to a depth or 2.0M. giving a coating of coal for aligning if required, refilling the soil, ramming etc; complete including providing pole base concreting with CC 1:4:8 for pole base and concreting the pole and copping with CC 1:2:4 using all materials such as cement, sand jelly, etc; complete including consolidating, curing etc; complete for each pole . | Nos. | 192 | 10015 | 1922880 | 6403 | 1229376 | [5 empty] | #REF! | #REF!
| Supply of 9.5 Mtr long, 350 kg WL RCC for single pole (As per KPTCL SR- 2025-26, Page No- 2 of 50, SL.No-08) | [7 empty] | 3472 |  |  |  | #REF! | #REF!
| Concreting materials for 9.5 Mtr long, 350 kg WL RCC (HESCOM CSR 23-24, 11 KV Labour Page No:8, Sl.No:26 A(a), B(a), C(a), (Rs. 312+3746+312 =4370) | [7 empty] | 4875 |  |  |  | #REF! | #REF!
| Erection of 9.5 Mtr long, 350 kg WL RCC pole (HESCOM CSR 25-26 Page No 34 of 50, Sl No: 13, 35 of 50 Sl No.31, Rs:617+1416=2033) | [7 empty] | 571.9008 | 2033 |  |  | #REF! | #REF!
4 | Erection of 9.5 Mtr long, 350 kg WL RCC pole for stud (HESCOM CSR 25-26 Page No 34 of 50, Sl No: 13, 35 of 50 Sl No.31, Rs.7509 and (HESCOM CSR 25-26 Page No 34 of 50, Sl No: 13, 35 of 50 Sl No.31 Rs:617+1416=2033) | Nos. | 120 | 10015 | 1201800 | 1976.6667 | 237200 | [5 empty] | #REF! | #REF!
5 | LT 2 Pin Cross Arm - MS(Dwg No. BESCOM/GM/QS&S/32 Dtd 24.11.2018) (As per KPTCL SR- 2025-26, Page No- 91 | Nos. | 240 | 290 | 69600 | 143 | 34320 | [5 empty] | #REF! | #REF!
6 | "Coyote" ACSR Conductor (As perESCOMs SR- 2025-26, Page No- 2 of 50, SL.No-24) | Km | 24.969 | 135537 | 3384223.353 | 6666.6667 | 166460 | 162644.4 |  |  |  |  | #REF! | #REF! | #REF!
7 | Supply and fixing of Horizantal cross arms for 33 KV using pole clamps, bolts and nuts etc., for 9.5 Mtr long, 350 kg WL RCC (As per KPTCL SR- 2025-26, Page No- 82 of 84, SL.No-15 & 16 And 36 of 50 Sl No: 50) 2045+99= | Set | 192 | 2144 | 411648 | 228 | 43776 | 2144 |  |  |  |  | #REF! | #REF! | #REF!
8 | Supply and fixing of top supports for 33 KV line with clamps, bolts and nuts etc; for I beams (As per KPTCL SR- 2025-26, Page No- 82 of 84, SL.No-16) | Set | 192 | 376 | 72192 | 0 | 0 | [5 empty] | #REF! | #REF!
9 | 33 kV Polymer Pin Insulator (As per KPTCL SR- 2025-26, Page No- 82 of 84, SL.No-11) | Nos. | 648 | 756 | 489888 | 0 | 0 | [5 empty] | #REF! | #REF!
10 | 33 kV 70 KN Polymer Insulator (Ball & socket type) (As per KPTCL SR- 2025-26, Page No- 82 of 84, SL.No-12) | Nos. | 150 | 390 | 58500 | 0 | 0 | [5 empty] | #REF! | #REF!
11 | Strain Clamp for Coyote to Coyote, (As per KPTCL SR- 2025-26, Page No- 3 of 50 SL.No-46) | Nos. | 150 | 578 | 86700 | 0 | 0 | [5 empty] | #REF! | #REF!
12 | 33 KV Guy Set with (includes Anchor Rod, Turn buckle(GI), Guy wire, 2 nos. of No.15 Strain Insulator, Guy clamp with Bolts, Nuts and Washers) (As per KPTCL SR- 2025-26, Page No- 3 of 50 SL.No-41, 3 of 50 SL N. 42,39, 4 of 50 Sl No. 54 , 60 ) 205+197+71+49+505.3 Labour charges 292+237=529 Page No 34 of 50 & 36 fo 50 Sl No. 25& 58 resply) | Set | 50 | 1208 | 60400 | 530 | 26500 | 978.3 |  |  |  |  | #REF! | #REF!
13 | Guy concreting with Boulders, Mud & Sand (300x300x450 mm) As per Drawing No. BESCOM/GM/CP/7 Dt: 24.10.07 | Nos. | 50 |  | 0 | 250 | 12500 | [5 empty] | #REF! | #REF!
14 | Spiral Earth electrode (As per KPTCL SR- 2023-24, Page No- 3 of 50 SL.No-26) Labour 35 of 50 Sl No. 36 | Set | 240 | 199 | 47760 | 83 | 19920 | [5 empty] | #REF! | #REF!
15 | a) Guarding for road crossing (As per KPTCL SR- 2023-24, Page No- 3 of 50 SL.No-30) (76*40Mtr) Labour 36 of 50 Sl No.61 | Span | 10 | 3120 | 31200 | 921 | 9210 | [5 empty] | #REF! | #REF!
| a) 3 pin cross arm for Guarding (As per KPTCL SR- 2023-24, Page No- 2 of 50 SL.No-13) (705 | Span | 20 | 705 | 14100 | 0 | 0 | [5 empty] | #REF! | #REF!
16 | Supplying and Providing of Pipe type Earthing consisting of Class "C" GI Pipe of 3mtr long, 40mm dia, 2.5mm thick, with Clamp, Bolt & Nuts, GI Wire / 50 x 6mm GI flat of 3mtrs long, Charcoal,salt, including earth excavation, re-filling as per KPTCL 23-24, page no: 115, Sl.No.: 6a, Rs. 5224+2111/- | Set | 48 | 4317.3554 | 207233.0579 | 1759.1667 | 84440 |  |  |  |  | Not updated | #REF! | #REF!
17 | G I Bolt & Nuts of required various size HESCOM CSR 23-24, KPTCL, Page No.: 43, Sl.No.:18.3, Rs. 142780/MT | MT | 0.1 | 118000 | 11800 | 0 | 0 |  |  |  |  | Not updated | #REF! | #REF!
18 | Anticlimbing Device GI Barbed wire (12 Mtr/Kg) (As per KPTCL SR- 2025-26, Page No- 3 of 50 SL.No-29) labour No: 36 of 50 Sl N.57 | Nos. | 240 | 152 | 36480 | 143 | 34320 | [5 empty] | #REF! | #REF!
19 | Caution/Danger Board (As per KPTCL SR- 2023-24, No- 31 of 50, SL.No-687) labour No: 36 of 50 Sl N.57 | Nos. | 24 | 131 | 3144 | 71 | 1704 | [5 empty] | #REF! | #REF!
20 | Number plates with pole clamps Bolt & nuts KPTCL SR 23-24, page No-43, Sl.No: 19.2, Rs.318/- and labour Page. No/: 113, Sl. No.: 3, Item No.: b, Rs. 80/- | Nos. | 216 | 262.8099 | 56766.9421 | 71 | 15336 |  |  |  |  | Not updated | #REF! | #REF!
21 | Phase plates (set of 6 per tower) KPTCL SR 23-24, page No-43, Sl.No: 19.1 Rs:528 labour Page. No/: 113, Sl. No.: 3, Item No.:d, Rs. 238/- | Set (3 Nos) | 24 | 436.3636 | 10472.7273 | 198.3333 | 4760 |  |  |  |  | Not updated | #REF! | #REF!
22 | PG Clamp for Coyote to Coyote, (As per KPTCL SR- 2025-26, No-3, SL.No-39) | Nos. | 150 | 333 | 49950 | 0 | 0 | [5 empty] | #REF! | #REF!
23 | Preliminary survey: Preliminary survey for identification of 3 alternative routes using Google Images and Survey of India maps and finalization of most economical, optimum route showing the topographical and other features on either side and indicating final selected route alignment and digital modeling in undulated hilly terrain along the proposed route using contour data from topographical map and submission of preliminary survey reports for approval as detailed in technical specification, inall types of terrain. (KPTCL SR 23-24, Page No.: 153, Sl. No.: 1,) | Km | 8.2 |  | 0 | 3025 | 24805 | [5 empty] | #REF! | #REF!
24 | Detailed Survey: Detailed survey along the approved route alignment by using Modern Survey equipment like DGPS/Total Stations/Digital Theodolites/GPS including profiling, tower spotting and optimization of locations by using computer aided techniques as detailed in the scope of work using PLS-CADD software in all types of terrains and includes the following: (KPTCL SR 23-24, Page No.: 153, Sl. No.: 2,) | Km | 8.2 |  | 0 | 12200.8333 | 100046.8333 | [5 empty] | #REF! | #REF!
25 | Check survey to be conducted during construction stage: Conducting detailed check survey along the approved route duly following the route alignment, GPS Co-ordinates, submission of detailed line schedule, tower schedule, land schedule and comparing the same with respect to detailed survey report, bringing out the differences if any. Submission of contour maps for undulated/hilly tower. The work also includes marking corridor width in the field and computing the quantum of benching and revetment, preparation of detailed land schedule along the corridor on the digitized Revenue village maps indicating the Sy. Nos. falling within the corridor for the purpose of estimation of the land compensation, submission of detailed consolidated hard copy of reports of check survey in 6 sets along with soft copy for approval in all types of terrain per km (KPTCL SR 23-24, Page No.: 155, Sl. No.: 3,) | Kms | 8.2 |  | 0 | 2218.3333 | 18190.3333 | [5 empty] | #REF! | #REF!
| Total in Rs. |  |  |  | 8887102.0803 |  | 2393728.1667 | [5 empty] | #REF! | #REF! |  |  | 11280830.2469 | 1410103.7809
Part-B 33KV Line breaker material estimate | [6 empty] | 0 | [5 empty] | #REF! | #REF!
| 33 KV Isolators : | [5 empty] | 0 | [5 empty] | #REF! | #REF!
| 33KV, 800A, 25 KA Class Double Break manually operated isolators with Pad connectors suitable for Coyote ACSR Conductor, as per technical specification with Solid Core, cylindrical post insulators | [5 empty] | 0 | [5 empty] | #REF! | #REF!
a | 33 kV, 800 A, 25 kA Upright with Earth Switch complete metallic portion with insulator (KPTCL SR-2023-24, Page No:37, Item No:9.14.1) RS:84700 | Nos | 1 | 70583.3333 | 70583.3333 |  | 0 | [5 empty] | #REF! | #REF!
| Erection of Lightning arrestors and wiring including movement from the point of unloading to the point of erection (33 KV) (KPTCL CSR 23-24, Labour, Page No: 119, Sl No.: 18) | Set | 1 | 0 | 0 | 278 | 278 | [5 empty] | #REF! | #REF!
| Erection of Isolators (33 KV) Assembly, Errection alignment and wiring including movement from the point of unloading to the point of erection.(Upright type) ( KPTCL CSR 23-24, Labour, Pg No: 119, Sl No.: 17 a(i)) | Nos | 1 | 0 | 0 | 1099 | 1099 | [5 empty] | #REF! | #REF!
| Assisting in Testing and Commissioning ( KPTCL CSR 23-24, Labour, Pg No: 119, Sl No.: 17 E(i) , ) | Nos | 1 | 0 | 0 | 159 | 159 | [5 empty] | #REF! | #REF!
| Surge Arrestors, Metal Oxide, as per Technical Specification. |  |  |  | 0 |  | 0 | [5 empty] | #REF! | #REF!
a) | 30 kV Metal Oxide with surge counter Arrestor class : Discharge Class 2 (Station Low Duty (SL)- for Overhead Line (KPTCL SR-2025-26, Page No:34, Item No:8.8, Rs:4840) . | Nos | 3 | 11583 | 34749 |  | 0 | [5 empty] | #REF! | #REF!
| Conductors |  |  |  | 0 |  | 0 | [5 empty] | #REF! | #REF!
a) | "Coyote" ACSR Conductor (KPTCL 2025-26, Page No.:44, SL No.:20.6. Rs:139) | Meter | 200 | 135.53 | 27106 |  | 0 | [5 empty] | #REF! | #REF!
| Mounting Structures: |  |  |  | 0 |  | 0 | [5 empty] | #REF! | #REF!
| Mounting Structures for equipments made out of fabricated galvanised angle of High tensile steel for GOS / CT's / PT's / LA's / NCT / HI PI etc as per approved drawing |  |  |  | 0 |  | 0 | [5 empty] | #REF! | #REF!
a) | 33KV Isolators - 0.248 MT (KPTCL SR-2023-24, Page No:43, Sl.No:18, Item No:18.3, Rs:148830 for MT) . (0.248MT=36909.84) (As per KPTCL SR- 2025-26, No- 02, SL.No-16) | Nos | 1 | 25626.6667 | 25626.6667 |  | 0 | [5 empty] | #REF! | #REF!
c) | 33KV Lightning Arrestors - 0.075 MT (KPTCL SR-2023-24, Page No:43, Sl.No:18, Item No:18.3, Rs:148830 for MT) . (0.075MT=11162.25) (As per KPTCL SR- 2025-26, No- 02, SL.No-16) | Nos | 3 | 7750 | 23250 |  | 0 | [5 empty] | #REF! | #REF!
| 33KV ODS Structures |  |  |  | 0 |  | 0 | [5 empty] | #REF! | #REF!
a) | RCC Pole - 9 Mtr Long, 145 Kg WL (As per KPTCL SR- 2025-26, Page No- 2 of 50, SL.No-08) | Nos | 2 | 6276 | 12552 |  | 0 | [5 empty] | #REF! | #REF!
b) | 11KV ODS mounting structure using 50 x 100 x 50 x 6 mm C channel MS, each 4.0 mtr long , As per PWD Electrical Page 19 Sl.No-5.41.4 Rs-Per Mtr-756.00 3NosX4Mtr=12 Mtr | Mtr | 12 | 630 | 7560 |  | 0 | [5 empty] | #REF! | #REF!
c) | Erection, alignment & assembly of fabricated steel lattice structure, pedestal structures & Mounting structures, for G.O.S. LAs etc. ( KPTCL CSR 23-24, Labour, Page No: 116, Sl No.: 8 b) | MT | 0.473 |  | 0 | 4769.1667 | 2255.8158 | [5 empty] | #REF! | #REF!
d | Formation of cross bus in each individual bay using Lynx/Coyote - Single/Double conductor with fixing of insulators, spacers, levelling the string conductors to the required height above the equipment including providing jumps to inter-connect different segments of the main bus. ( KPTCL CSR 23-24, Labour, Page No: 122, Sl No.: 25) | Per bay | 1 |  | 0 | 6136.6667 | 6136.6667 | [5 empty] | #REF! | #REF!
| Insulators & Hardware materials: |  |  |  | 0 |  | 0 | [5 empty] | #REF! | #REF!
a) | Pad clamp for Coyote ACSR (KPTCL SR-2025-26, Sl.No:77, Item No:10.09, Rs:725) | Nos | 6 | 734 | 4404 |  | 0 | [5 empty] | #REF! | #REF!
b) | T clamp for Coyotte ACSR (KPTCL SR-2025-26, Page No:69, Item No:47.7.11, Rs:509.00) | Nos | 6 | 426 | 2556 |  | 0 | [5 empty] | #REF! | #REF!
e) | I bolts | Nos | 6 | 55 | 330 |  | 0 | [5 empty] | #REF! | #REF!
| Ground Mat & Earthing : |  |  |  | 0 |  | 0 | [5 empty] | #REF! | #REF!
a) | Grounding of equipment by providing cast iron pipe of 100mm ID 13mm thick, 2.75Mtr long wih 2part clamps out of GI flat 50/6 mm continously welded alround the pipe using cast iron welding electrodes as per drawing (al materials to be supplied by contractors) ( KPTCL CSR 23-24, Labour, Page No: 115, Sl No.: 6c, Rs:12792) , | Set | 2 | 10635 | 21270 | 2909.1667 | 5818.3333 | [5 empty] | #REF! | #REF!
b) | Supplying & providing 450mm dia 450mm hieght 1.5" - 2" thick hume pipe coller ( non PR type) fop earth quits including all lead & lift. ( KPTCL CSR 23-24, Labour, Page No: 124, Sl No.: 26i, Rs:1499) , | each | 2 | 1249.1667 | 2498.3333 | 0 | 0 | [5 empty] | #REF! | #REF!
c) | Grounding of equipment with 50/6 mm GI flat & connecting equipment to the earth mat / ground pit. Each point of earthinh with all formation works like bending, twisting, drilling of holes & conncting by welding (inclusive of all T & P consumables) to the earth mat/ ground pit/point of earth connection, all the materails supplied by the contractor ( KPTCL CSR 23-24, Labour, Page No: 123, Sl No.: 26f, Rs:335) , | Rmt | 45 | 279.1667 | 12562.5 | 0 | 0 | [5 empty] | #REF! | #REF!
a) | Bolt & Nut as per IS-1367 GI (HESCOM SR-2023-24, Sl.No:494 to 504, item no:61.12 to 61.22, RS:132571 for MT) | MT | 0.04 | 110475.8333 | 4419.0333 |  | 0 | [5 empty] | #REF! | #REF!
Total cost |  |  |  |  | 249466.8667 |  | 15746.8158 | [5 empty] | #REF! |  |  |  | 265213.6825
Grand Total Cost |  |  |  |  | 9136568.9469 |  | 2409474.9825 | [5 empty] | #REF!

## covering (hidden)
ÌÐÔ½ñÏü Á·ÐÔô³ý ÊÐ¤Ð½¤Ñ¡Ô ‘Ðo»Ðº ºo¦ÐÔÁÔ³Ð |  |  | Hubli Electricity Supply Company Ltd
ÊÐÌÑo¦ÐÔ‘Ð ‘Ño¦ÐÔþºÀÑþÌÐ‘Ð ƒ¿°o¦ÐÔo³Ð¤Ð¤ÐÔ(Á) |  |  | Office of the
ŠÊý ÀÐÔ³ÐÔê ŠÄý ‡»Ð Á¾°Ñ–Ð, |  |  | Asst.Executive Engineer (Ele)
ÌÐÔ.Á.ÊÐ.‘Ð.º. ƒµÐ±Ò. |  |  | 33KV S&L Sub-Divn. Athani
No.ATN/AEE/33KV/S&L/25-26/ |  |  |  | Date:
To,
The Executive Engineer Ele,
33KV S&L Division,
HESCOM,Belagavi.
Sir,
Sub: Submission of Estimates for Sanction.
With reference to the above subject, I am herewith submitting the following estimates for your kind sanction.
Sl.No | Name of the work |  |  |  |  | Cost of the estimate
1 | Estimate for construction of S/C 33 KV new link line from proposed 110/33/11 KV MUSS Hanamapur to existing 33/11 KV MUSS Muragundi for a distance of 8.2 Kms using coyote ACSR for providing second source and along with incommer isolator at existing 33/11 KV MUSS Muragundi in O&M Division, HESOM, Athani Taluk: Athani Dist: Belagavi, on Total Turn Key basis. |  |  |  |  | 13026355
2 | Estimate for construction of S/C 33 KV new link line from proposed 110/33/11 KV MUSS Sankratti to existing 33/11 KV MUSS Saptsagar for a distance of 4 Kms using coyote ACSR for providing second source with incommer 33KV 800Amps isolator at existing 33/11 KV MUSS Saptsagar in O&M Division, HESOM, Athani Taluk: Athani Dist: Belagavi, on Total Turn Key basis. |  |  |  |  | 8093040
3 | Estimate for construction of S/C 33 KV new link line from proposed 110/33/11 KV MUSS Sankratti to existing 33/11 KV MUSS Koligudd for a distance of 3 Kms using coyote ACSR for providing second source along with incomming 33KV line breaker at existing 33/11 KV MUSS Koligudd in O&M Division, HESOM, Raibag, Taluk: Raibag, Dist: Belagavi, on Total Turn Key basis. |  |  |  |  | 8527991
4 | Estimate for construction of S/C 33 KV new link line from proposed 110/33-11 KV MUSS Hanamapur to the existing 33/11 KV MUSS Jambagi for a distance of 8.0 Kms using Coyote ACSR for providing second source at existing 33/11 KV MUSS Jambagi in O&M Division, HESOM, Athani Taluk: Athani Dist: Belagavi, on Total Turn Key basis Under RDSS Scheme |  |  |  |  | 13089426
5 | Estimate for construction of S/C 33 KV new link line from proposed 1X20MVA, 110/33KV at exisiting 2X10MVA, 110/11 KV MUSS Ghatanatti to existing 2X5MVA, 33/11 KV MUSS Sankonatti for a distance of 1.2 Kms using coyote ACSR for providing second source at existing 33/11 KV MUSS Sankonatti in O&M Division, HESOM, Athani, Taluk: Athani, Dist: Belagavi, on Total Turn Key basis. (Under RDSS Scheme) |  |  |  |  | 3199438
6 | Estimate for construction of S/C 33 KV new link line from proposed 1X20MVA, 110/33KV at exisiting 2X10MVA, 110/11 KV MUSS Ghatanatti to existing 2X5MVA, 33/11 KV MUSS Nandagaon for a distance of 7.5 Kms using coyote ACSR for providing second source at existing 33/11 KV MUSS Nandagaon in O&M Division, HESOM, Athani, Taluk: Athani, Dist: Belagavi, on Total Turn Key basis. (Under RDSS Scheme) |  |  |  |  | 12577718
7 | Estimate for providing additional 2nd 5MVA, 33/11 KV Power Transformer at existing 1X5 MVA,33/11 KV Substation Athani Town in O&M Division, HESCOM, Athani Under Total Turnkey basis. Under RDSS Scheme. |  |  |  |  | 18900137
| Total |  |  |  |  | 77414105
Yours faithfully
Asstistant Executive Engineer Ele,
33KV S&L Sub-Division HESCOM
Athani
ÌÐÔ½ñÏü Á·ÐÔô³ý ÊÐ¤Ð½¤Ñ¡Ô ‘Ðo»Ðº ºo¦ÐÔÁÔ³Ð |  |  | Hubli Electricity Supply Company Ltd
ÊÐÌÑo¦ÐÔ‘Ð ‘Ño¦ÐÔþºÀÑþÌÐ‘Ð ƒ¿°o¦ÐÔo³Ð¤Ð¤ÐÔ(Á) |  |  | Office of the
ŠÊý ÀÐÔ³ÐÔê ŠÄý ‡»Ð Á¾°Ñ–Ð, |  |  | Asst.Executive Engineer (Ele)
ÌÐÔ.Á.ÊÐ.‘Ð.º. ƒµÐ±Ò. |  |  | 33KV S&L Sub-Divn. Athani
No.ATN/AEE/33KV/S&L/25-26/ |  |  |  | Date:
To,
The Executive Engineer Ele,
33KV S&L Division,
HESCOM,Belagavi.
Sir,
Sub: Submission of Estimates for Sanction.
With reference to the above subject, I am herewith submitting the following estimates for your kind sanction.
Sl.No | Name of the work |  |  |  |  | Cost of the estimate
1 | Estimate for construction of S/C 33 KV new link line from proposed 110/33/11 KV MUSS Hanamapur to existing 33/11 KV MUSS Muragundi for a distance of 8.2 Kms using coyote ACSR for providing second source and along with incommer isolator at existing 33/11 KV MUSS Muragundi in O&M Division, HESOM, Athani Taluk: Athani Dist: Belagavi, on Total Turn Key basis. |  |  |  |  | 13026355
2 | Estimate for construction of S/C 33 KV new link line from proposed 110/33/11 KV MUSS Sankratti to existing 33/11 KV MUSS Saptsagar for a distance of 4 Kms using coyote ACSR for providing second source with incommer 33KV 800Amps isolator at existing 33/11 KV MUSS Saptsagar in O&M Division, HESOM, Athani Taluk: Athani Dist: Belagavi, on Total Turn Key basis. |  |  |  |  | 9149851
3 | Estimate for construction of S/C 33 KV new link line from proposed 110/33/11 KV MUSS Sankratti to existing 33/11 KV MUSS Koligudd for a distance of 3 Kms using coyote ACSR for providing second source along with incomming 33KV line breaker at existing 33/11 KV MUSS Koligudd in O&M Division, HESOM, Raibag, Taluk: Raibag, Dist: Belagavi, on Total Turn Key basis. |  |  |  |  | 8527991
| Total |  |  |  |  | 30704197
|  | Yours faithfully |  | Yours faithfully
Asstistant Executive Engineer Ele,
33KV S&L Sub-Division HESCOM
|  | Athani |  |  | Athani

## Sketch (2) (hidden)
Construction of S/C 33 KV new line from proposed 110/33/11 KV MUSS Hanamapur to the existing 33/11 KV MUSS Muragundi for a distance of 8.2 Kms using coyote ACSR for providing second source in 33KV S&L Division,Belagavi on total turnkey basis.
[5 empty] | TP | 2
[5 empty] | DP | 22
[5 empty] | Pole | 162
30
192
87
INDEX
|  |  | Prop 9.5Mtr RCC DP sets |  |  |  | INDEX
Prop 9.5Mtr RCC DP sets
Prop 9.5Mtr RCC TP sets
Prop 9.5Mtr RCC TP sets
Prop Coyote ACSR
Prop Coyote ACSR
Prop 9.5Mtr RCC Pole for line=192 No's
|  | Prop 9.5Mtr RCC DP sets =22No's |  |  |  |  | Prop 9.5Mtr RCC Pole for line=192 No's
|  | Prop 9.5Mtr RCC TP sets =2No's |  |  |  |  | Prop 9.5Mtr RCC DP sets =22No's
Prop 9.5Mtr RCC TP sets =2No's
| Asst, Executive Engineer(Ele) |  |  | Junior Engineer(Ele),
| 33KV S&L Sub-Division, HESCOM,Athani |  |  | 33KV line Maintenance Athani
Sankratti
Village
Masaraguppi To Muragundi road
Athani To Miraj road
10 Poles
Athani To Madabhavi road
E
W
S
N
9Poles
9Poles
9Poles
9Poles
9Poles
9Poles
9Poles
9Poles
9Poles
9Poles
9Poles
9Poles
9Poles
9Poles
9Poles
9Poles
9Poles
9Poles
5Poles
2Poles
7Poles
7Poles
5Poles
4Poles
33/11KV MUUS Muragundi
110/33/11KV MUUS Hanmapur
Existing 33KV Muragundi+Athani Town Tota distance:14Km
Existing 33KV Muragundi+Athani Town Tota distance:3.2Km
33/11KV MUSS Athani Town
110/33/11KV MUSS Athani

## Muragundi saving (hidden)
HUBLI ELECTRICITY SUPPLY COMPANY LIMITED.
HTVR & Annual energy loss calculation of existing S/C 33 KV Muragundi feeder eminating from 110\33\11 KV MUSS Athani.
Node No | KVA at node | CUM KVA | Distance KM | KVA-KM | Conductor constant ohm/kms | KVA-KM Conductor constant
1 | 15000 | 15000 | 14 | 210000 | 0.248 | 52080
2 | 5000 | 5000 | 3.2 | 16000 | 0.248 | 3968
| 20000 |  | 17.2 | 226000 |  | 56048
8760
1. Total connected load P= | [5 empty] | 20000
2. Total length in Km. L= | [5 empty] | 17.2
3. Sum of moments= KVA*KM= | [5 empty] | 226000
4. LDF= P*L/ KVA*KM | [5 empty] | 1.5221 |  |  | Total
5. Annual energy sent out of the feeder | [5 empty] | 38329890 | 1 | 2022-08-01 | 180 | 1308400 |  |  | 2170090 | 1250700 | 3420790
6. Peak load = | [5 empty] | 200 | 2 | 2022-09-01 | 130 | 1064400 |  |  | 1595940 | 1317000 | 2912940
7. Diversity factor= Total connected load in KVA/1.73*33*Peak load | [5 empty] | 1.7516 | 3 | 2022-10-01 | 80 | 850400 |  |  | 1452930 | 1338600 | 2791530
8. Load factor = Annual energy sent out on the feeder/ Energy computed on the basis of the peak load= Annual energy sent out/ 1.73*33*0.8*8760*peak load | [5 empty] | 0.47902 | 4 | 2022-11-01 | 105 | 1974800 |  |  | 1723840 | 1140900 | 2864740
[5 empty] | 38329890 |  | 5 | 2022-12-01 | 130 | 2242000 |  |  | 2529600 |  | 2529600
[5 empty] | 200 |  | 6 | 2023-01-01 | 140 | 2180400 |  |  | 1682890 | 1116000 | 2798890
9. Loss load factor(LLF) =0.30*LF+.70*LF*LF) | [5 empty] | 0.30433 | 7 | 2023-02-01 | 180 | 2727200 |  |  | 2434800 |  | 2434800
10.Load density factor= | [5 empty] | 1.5221 | 8 | 2023-03-01 | 192 | 3199600 |  |  | 3145200 |  | 3145200
11. Annual energy losses= 0.105*P*P*L*R*LLF/2*LDF*DF*DF | [5 empty] | 5837289.9141 | 9 | 2023-04-01 | 200 | 3199600 | Aprox |  | 3145200 |  | 3145200
Resistance of the conductor in Ohms per KM= | [5 empty] | 0.248 | 10 | 2023-05-01 |  | 3199600 | Aprox | 48228800 | 4104000 |  | 4104000
[7 empty] | 11 | 2023-06-01 | 220 | 3199600 | Aprox | 22952400 | 4311600 |  | 4311600
12. Add 10% spur line loss= Annual energy loss*0.1= | [5 empty] | 0 | 12 | 2023-07-01 | 224 | 2588800 |  |  | 3870600 |  | 3870600
13. Total loss = | [5 empty] | 5837289.9141 | Total |  |  | 27734800 |  |  |  |  | 38329890
14. HTVR calculation
I) % HTVR= KVA*KM *0.00341/100 | [5 empty] | 7.7066
Asst. Executive Engineer(El), Junior Engineer(El)
33 KV S & L Sub-Division, HESCOM, Athani 33KV line maintenance Athani
HUBLI ELECTRICITY SUPPLY COMPANY LIMITED.
HTVR & Annual energy loss calculation of proposed 33 KV S/C Muragundi link line from 110/33/11 KV MUSS Hanamapur after providing 33 KV S/C link line from 110/33/11 KV MUSS Hanamapur
Node No | KVA at node | CUM KVA | Distance KM | KVA-KM | Conductor constant ohm/kms | KVA-KM Conductor constant
1 | 15000 | 15000 | 8.2 | 123000 | 0.248 | 30504
| 15000 |  | 8.2 | 123000 |  | 30504
1. Total connected load P= | [5 empty] | 15000
2. Total length in Km. L= | [5 empty] | 8.2
3. Sum of moments= KVA*KM= | [5 empty] | 123000
4. LDF= P*L/ KVA*KM | [5 empty] | 1
5. Annual energy sent out of the feeder | [5 empty] | 38329890
6. Peak load = | [5 empty] | 200
7. Diversity factor= Total connected load in KVA/1.73*33*Peak load | [5 empty] | 1.3137
8. Load factor = Annual energy sent out on the feeder/ Energy computed on the basis of the peak load= Annual energy sent out/ 1.73*33*0.8*8760*peak load | [5 empty] | 0.47902
38329890
200
9. Loss load factor(LLF) =0.30*LF+.70*LF*LF) | [5 empty] | 0.30433
10.Load density factor= | [5 empty] | 1
11. Annual energy losses= 0.105*P*P*L*R*LLF/2*LDF*DF*DF | [5 empty] | 4235909.4952
Resistance of the conductor in Ohms per KM= | [5 empty] | 0.248
12. Add 10% spur line loss= Annual energy loss*0.1= | [5 empty] | 0
13. Total loss = | [5 empty] | 4235909.4952
14. HTVR calculation
I) % HTVR= KVA*KM *0.00341/100 | [5 empty] | 4.1943
Calculation of Energy Savings
1 | HTVR & Annual energy loss calculation of existing S/C 33 KV Muragundi feeder eminating from 110\33\11 KV MUSS Athani. |  |  |  |  | 5837289.9141
2 | HTVR & Annual energy loss calculation of proposed 33 KV S/C Muragundi link line from 110/33/11 KV MUSS Hanamapur after providing 33 KV S/C link line from 110/33/11 KV MUSS Hanamapur |  |  |  |  | 4235909.4952
Therefore Annual Energy Savings in Units = 1-2 | [5 empty] | 1601380.4189 |  | 1.6014
Cost Banefit ratio=Energy Saving x 8.35
Cost of Estimate
1.0265
| = | 1601380.4189 | x 8.35
#REF!
| = | #REF!
Asst. Executive Engineer(Ele) Junior Engineer(Ele)
33 KV S & L Sub-Division, HESCOM, Athani 33KV line maintenance Athani

## Muragundi .mat (hidden)
HUBLI ELECTRICITY SUPPLY COMPANY LIMITED
#REF!
Part-B 33KV Line breaker material estimate
Sl. No. |  | Particulars | Unit | Qty to be erected | Unit Material Cost Rs. | Deloaded 21% | New SR 2025-26(20% Loaded) | Total Material Cost Rs.
1 |  | 33 KV Isolators :
33KV, 800A, 25 KA Class Double Break manually operated isolators with Pad connectors suitable for Coyote ACSR Conductor, as per technical specification with Solid Core, cylindrical post insulators
| b) | 33 kV, 800 A, 25 kA Upright with Earth Switch complete metallic portion with insulator (KPTCL SR-2023-24, Page No:37, Item No:9.14.1) RS:84700 | Nos | 1 | 84700 | 70000 | 84000 | 84000
2 |  | Surge Arrestors, Metal Oxide, as per Technical Specification. | [5 empty] | 0
| a) | 30 kV Metal Oxide with surge counter Arrestor class : Discharge Class 2 (Station Low Duty (SL)- for Overhead Line (KPTCL SR-2023-24, Page No:34, Item No:8.8, Rs:4840) . | Nos | 3 | 4840 | 4000 | 4800 | 14400
3 |  | Conductors | [5 empty] | 0
| a) | "Coyote" ACSR Conductor (KPTCL 23-24, Page No.:44, SL No.:20.6. Rs:139) | Meter | 200 | 139 |  | 155 | 31000
4 |  | Mounting Structures: | [5 empty] | 0
|  | Mounting Structures for equipments made out of fabricated galvanised angle of High tensile steel for GOS / CT's / PT's / LA's / NCT / HI PI etc as per approved drawing | [5 empty] | 0
| a) | 33KV Isolators - 0.248 MT (KPTCL SR-2023-24, Page No:43, Sl.No:18, Item No:18.3, Rs:148830 for MT) . (0.248MT=36909.84) (As per KPTCL SR- 2025-26, No- 02, SL.No-16) | Nos | 1 | 36909.84 |  | 30752 | 30752
| c) | 33KV Lightning Arrestors - 0.075 MT (KPTCL SR-2023-24, Page No:43, Sl.No:18, Item No:18.3, Rs:148830 for MT) . (0.075MT=11162.25) (As per KPTCL SR- 2025-26, No- 02, SL.No-16) | Nos | 3 | 11162.25 |  | 9300 | 27900
5 |  | 33KV ODS Structures | [5 empty] | 0
| a) | RCC Pole - 9 Mtr Long, 145 Kg WL (As per KPTCL SR- 2025-26, Page No- 2 of 50, SL.No-08) | Nos | 2 | 7076 |  | 12018 | 24036
| b) | 11KV ODS mounting structure using 50 x 100 x 50 x 6 mm C channel MS, each 4.0 mtr long , As per PWD Electrical Page 19 Sl.No-5.41.4 Rs-Per Mtr-756.00 3NosX4Mtr=12 Mtr | Mtr | 12 | 756 |  | 756 | 9072
6 |  | Insulators & Hardware materials: | [5 empty] | 0
| a) | Pad clamp for Coyote ACSR (KPTCL SR-2023-24, Sl.No:77, Item No:10.09, Rs:725) | Nos | 6 | 725 |  | 725 | 4350
| b) | T clamp for Coyotte ACSR (KPTCL SR-2023-24, Page No:69, Item No:47.7.11, Rs:509.00) | Nos | 6 | 509 |  | 509 | 3054
| e) | I bolts | Nos | 6 | 55 |  | 55 | 330
7 |  | Ground Mat & Earthing : | [5 empty] | 0
| a) | Grounding of equipment by providing cast iron pipe of 100mm ID 13mm thick, 2.75Mtr long wih 2part clamps out of GI flat 50/6 mm continously welded alround the pipe using cast iron welding electrodes as per drawing (al materials to be supplied by contractors) ( KPTCL CSR 23-24, Labour, Page No: 115, Sl No.: 6c, Rs:12792) , | Set | 2 | 12762 | 10547.1074 | 12656.5289 | 25313.0579
| b) | Supplying & providing 450mm dia 450mm hieght 1.5" - 2" thick hume pipe coller ( non PR type) fop earth quits including all lead & lift. ( KPTCL CSR 23-24, Labour, Page No: 124, Sl No.: 26i, Rs:1499) , | each | 2 | 1499 | 1238.843 | 1486.6116 | 2973.2231
| c) | Grounding of equipment with 50/6 mm GI flat & connecting equipment to the earth mat / ground pit. Each point of earthinh with all formation works like bending, twisting, drilling of holes & conncting by welding (inclusive of all T & P consumables) to the earth mat/ ground pit/point of earth connection, all the materails supplied by the contractor ( KPTCL CSR 23-24, Labour, Page No: 123, Sl No.: 26f, Rs:335) , | Rmt | 45 | 335 | 276.8595 | 332.2314 | 14950.4132
8 | a) | Bolt & Nut as per IS-1367 GI (HESCOM SR-2023-24, Sl.No:494 to 504, item no:61.12 to 61.22, RS:132571 for MT) | MT | 0.04 | 132571 |  |  | 0
Total cost | [7 empty] | 272130.6942

## Muragundi Erre (hidden)
HUBLI ELECTRICITY SUPPLY COMPANY LIMITED
#REF!
PART-C (33KV Line breaker Electricals Erection Works)
Sl. No. |  | Particulars | Unit | Qty to be erected | Unit Labour Charge Rs. | Total Labour Charge Rs.
1 | a) | Erection of Lightning arrestors and wiring including movement from the point of unloading to the point of erection (33 KV) (KPTCL CSR 23-24, Labour, Page No: 119, Sl No.: 18) | Set | 1 | 333 | 333
2 | a) | Erection of Isolators (33 KV) Assembly, Errection alignment and wiring including movement from the point of unloading to the point of erection.(Upright type) ( KPTCL CSR 23-24, Labour, Pg No: 119, Sl No.: 17 a(i)) | Nos | 1 | 1319 | 1319
| b) | Assisting in Testing and Commissioning ( KPTCL CSR 23-24, Labour, Pg No: 119, Sl No.: 17 E(i) , ) | Nos | 1 | 191 | 191
3 |  | 33KV Station structures:
| a) | Erection, alignment & assembly of fabricated steel lattice structure, pedestal structures & Mounting structures, for G.O.S. LAs etc. ( KPTCL CSR 23-24, Labour, Page No: 116, Sl No.: 8 b) | MT | 0.473 | 5723 | 2706.979 |  | 0.48 | 0.426 | 0.21
4 | a) | Formation of cross bus in each individual bay using Lynx/Coyote - Single/Double conductor with fixing of insulators, spacers, levelling the string conductors to the required height above the equipment including providing jumps to inter-connect different segments of the main bus. ( KPTCL CSR 23-24, Labour, Page No: 122, Sl No.: 25) | Per bay | 1 | 7364 | 7364
5 | a) | Errection of RCC pole-9Mtr long (HESCOM SR 23-24, Labour page pageNo: 43 & 44, Sl.No: 1&30, Item No:1.1.1 &2.02, Rs:629&1113) | No's | 2 | 1742 | 3484 | 1403 only dp | 1341
6 |  | Ground Mat & Earthing : | [5 empty] | 1341
| a) | Grounding of equipment by providing cast iron pipe of 100mm ID 13mm thick, 2.75Mtr long wih 2part clamps out of GI flat 50/6 mm continously welded alround the pipe using cast iron welding electrodes as per drawing (al materials to be supplied by contractors) ( KPTCL CSR 23-24, Labour, Page No: 115, Sl No.: 6c, Rs:3491) , | Set | 2 | 3491 | 6982 |  | 1403
Total cost | [5 empty] | 22379.979 | 59780.84
| Asst. Executive Engineer(Ele) |  | Junior Engineer(Ele)
| 33 KV S & L Sub-Division,HESCOM, Athani |  | 33KV line Maintenance Athani
711119.469

## Muragundi Civil
HUBLI ELECTRICITY SUPPLY COMPANY LIMITED
Construction of S/C 33 KV new line from proposed 110/33/11 KV MUSS Hanamapur to the existing 33/11 KV MUSS Muragundi for a distance of 8.2 Kms using coyote ACSR for providing second source in 33KV S&L Division,Belagavi on total turnkey basis.
PART-D-(CIVIL WORKS)
Sl No. | Item Description |  | Unit | Qty | Unit Price (Rs) | Total Price (Rs)
SCHEDULE OF ITEMS FOR ASSOCIATED CIVIL WORKS AND STRUCTURES:
1 |  | Foundations: Engineering, supply of all labour,material and construction of RCC footing including the cost of excavation, cement concreting, reinforcement, backfilling, waterproof cement painting, for all works, grouting underpinning etc ,for the following works
| a) | 9 mtrs long RCC poles for ODS (As per ESCOM's SR 2023-24,Base concreting Rs.312+Pole concreting Rs.3434,Coping Rs.312) | Nos | 2 | 3381.6667 | 6763.3333
| b) | 33KV Surge arrestor support structure (0.95 mtrX0.55 mtr X 1mtr Depth),with M-20 Concreting,PCC of M-10 and FE-550 TMT steel | Nos | 3 | 4708.3333 | 14125
| c) | 33KV Isolators support structure(0.95 mtr X 0.45 mtr X 1mtrDepth),with M-20 Concreting,PCC of M-10 and FE-550 TMT steel | Set | 1 | 4728.3333 | 4728.3333
2 |  | Earth mat formation : |  |  | 0 | 0
| a) | Excavation, formation, refilling. | CMT | 4 | 168.3333 | 673.3333
|  | Total cost |  |  |  | 26290