SCOPE OF WORK

Name of Work: Supply, Erection, Testing and commissioning of 7.5 HP submersible sludge pump for dewatering at BP Dam.

The detailed scope of work (SOW) covers the end-to-end execution of the project—from procuring the equipment and physical installation to electrical integration and performance testing. It must ensure the 7.5 HP submersible sludge pump operates safely and efficiently in dewatering system

1. Scope of Supply

- Pump Unit: Supply of 7.5 HP Horizontal open well submersible pump with motor and bottom base frame suitable for Duty Head: 27 Mtr and Head range-- 20 to 35 Mtr. Make: Unnati/ Kirloskar/CRI.

Must be non-clog, equipped with a heavy-duty semi-open or vortex impeller capable of handling suspended solids and sludge.

- Accessories:

80NB MS "C" class pipe Make: Apollo/Jindal/Tata

80NB MS "C" class long bend (2.5 D)

80NB MS Flanges BS 10 Table E, 10-11 mm Thick

Delivery Distance piece (01 No) and support Riser Clamp (02 Pair) (Set: 2 nos.)

80NB ISI mark PN 1 sluice valve Make: Kirloskar/ Gavane Patil/ Agro

80NB ISI mark PN 1 Non Return Valve Make: Kirloskar/ Gavane Patil/ Agro

and all required suitable nut-bolts (4.6 grade), gasket packing, red oxide, Bus green Final paint, 12 mm nylon rope- 4 mtr required for delivery pipe line.

- Control Panel: Supply of starter panel suitable for controlling above pump, with automatic level controller, probe, cable etc complete set.

- Cables: Supply of submersible-grade, heavy-duty power and control cables of adequate length (4 Sq mm x 3 Core flat submersible cable. Make: Polycab/ Finolex/ Havels/ Rajat) matching the 7.5 HP rating.

2. Erection & Installation Works

- Site Preparation: Cleaning and clearing the dewatering sump of loose debris and sediments prior to equipment placement.

- Mechanical Installation:

  - Positioning and anchoring the pump at the lowest point of the dewatering sump.

  - Erection of pump frame, pump and motor, Welding of new 80 NB deliver pipeline with required reducers, bend, flanges etc.

- Electrical Work:

  - Erection of control panel and automatic control system.

  - Laying, glanding, and terminating the power and control cables between the pump and the control panel.

  - Installing dedicated safety earthing pits/stations for both motor body and neutral.

3. Testing Procedure

- Pre-commissioning Checks:

  - Testing insulation resistance and verifying the high-voltage (HV) capability of the motor windings using a megger.

  - Verifying electrical continuity and verifying the correct direction of pump rotation.

- No-Load & Load Testing:

  - Running the pump momentarily in a no-load scenario to verify smooth, vibration-free operation.

  - Submerging the pump in water to perform actual head/discharge (flow rate) capacity tests against the manufacturer’s pump curve.

- Safety Tests: Checking the calibration of thermal overload relays, low-level float switches (dry-run protection), and emergency shut-offs.

4. Commissioning & Handover

- Operation Sequence: Connecting the pump to the main power source and testing its auto-operation via float switches or sensors.

- Documentation: Handing over a detailed Operations and Maintenance (O&M) manual, functional checklists, and technical data sheets to engineering team.

General Conditions

- All Consumables required for the work viz., welding rods, grinding & cutting wheels, Acetylene gas, Oxygen gas, Welding Electrodes, consumables etc., shall be arranged by the contractor itself.

- Machineries, tools, tackles shall be arranged by the contractor itself.

- All the necessary safety gadgets have to be arranged by the contractor itself and safety procedures must be followed strictly while carrying out the work.

- The contractor must arrange to visit the site compulsorily before quoting so as to have overall idea of the work and to assess the exact quantum of work to avoid unnecessary post tender correspondence.

- The equipment and materials supplied shall confirm in all respects to high standard of engineering, design and workmanship and capable of performing continuous operation in the manner acceptable to the purchaser. The agency shall obtain the approval from EE(O,PS&C)Nagjhari for the make of the materials to be supplied.

- Any work which is not mentioned in the scope of work but very much essential for the completion of the work are treated as part of the scope of work and is to be carried out as per the direction of engineer in charge.

- Necessary safety equipment’s shall be arranged by the contractor and shall be compulsorily used while carrying out this work. The contractor has to arrange necessary tools, tackle & machineries, consumables, testing equipment, everything which are necessary for execution of works.

Executive Engineer (O, PS&C) Nagjhari

Karnataka Power Corporation Limited

Ambikanagar – 581363