## Quantity (hidden)
P. H. DIVISION, HAJIPUR
WORK DETAIL Of Quantity For Distribution System
DETAILS OF Pipeline Distribution System Of Different Schemes
Sl. No. | Ward No | Scheme Name | Different Size Of HDPE pipe (In Mtrs.) | [6 empty] | PVC Tank in Liter | Brass gate valve with C.I. wheel |  |  | Nos. of connections
|  |  | 110 mm | 90 mm | 75 mm | 63 mm | 50 mm | 40 mm | Total |  | 80 mm | 65 mm | 50 mm
1 | 6B | 6B (MUSLIM TOLA) | 0 | 100 | 250 | 350 | 350 | 400 | 1450 | 10000 | 1 | 2 | 2 | 150 |  |  | ( | )
| Total |  | 0 | 100 | 250 | 350 | 350 | 400 | 1450 | 10000 | 1 | 2 | 2 | 150
item No 7 | Providing and fixing G.I.Pipes complete with G.I. Fittings including trenching and refilling etc | [8 empty] | No Of Scheme | Quantity |  | Unit | Total
7.1 | 50mm dia G.I.Pipe from T/well to PVC Tank | [8 empty] | #REF! | 14 | m | P/M | #REF!
7.2 | 80mm dia G.I.Pipe from PVC Tank to Distribution main | [8 empty] | #REF! | 14 | m | P/M | #REF! | Districk | VAISHALI
7.3 | 65mm dia G.I.Pipe for wash out | [8 empty] | #REF! | 12 | m | P/M | #REF! | Block | HAJIPUR
[15 empty] | Panchayat | DAULATPUR CHANDI
Item No 12 | G.I pipe for using as filling station | [8 empty] | No Of Scheme | Quantity |  | Unit | Total | Habitation | MUSLIM TOLA
| 50mm dia. Pipe from distribution main | [8 empty] | #REF! | 3.5 | m | p/m | #REF!
| Providing and fixing G.I fittings | [8 empty] | #REF! | 1 | each | Each | #REF!
| 80mmx80mmx50mm dia Tee | [8 empty] | #REF! | 3 | each | Each | #REF!
| 50mm dia bend | [8 empty] | #REF! | 1 | each | Each | #REF!
Item No 13 | Providing and fixing PTMT extension nipple for water tank pipe, fittings of approved quality and colour. | [8 empty] | No Of Scheme | Quantity |  | Unit | Total
13.1 | 50mm dia | [8 empty] | #REF! | 2 | No's | Each | #REF!
13.2 | 63mm dia | [8 empty] | #REF! | 1 | No's | Each | #REF!
13.3 | 80 mm dia | [8 empty] | #REF! | 1 | No's | Each | #REF!
#REF!
#REF!

## Quantityof IRP MOTOR (hidden)
P. H. DIVISION, HAJIPUR
WORK DETAIL Of Quantity For Population Forcast Motor Pump Design
DETAILS OF Motor pump Of Different Schemes
Sl. No. | Ward No | Scheme Name | Different Size of Iron Treatment Unit Required in Schemes |  |  | Motor Pump Required
|  |  | 16KLPH | 12KLPH | 8KLPH | 2HP | 3HP
1 | 6B | 6B (MUSLIM TOLA) | 0 | 0 | 0 | 0 | 1
| Total |  | 0 | 0 | 0 | 0 | 1
Executive Engineer
#REF!

## Motor Design (hidden)
DESIGN OF MOTOR PUMP
1 | #REF! | #REF! | #REF! | #REF! | Scheme | 6B (MUSLIM TOLA)
Water demand in Intermediate year | [6 empty] | 80.5774 | KLD
Duration of Pumping | [6 empty] | 8 | Hrs.
Hence the rate of pumping | [6 empty] | 10.0722 | Kl/Hr
[7 empty] | 0.0027978 | Kl/Sec
[7 empty] | 2.7978 | LPS
Now calculation of Head
| (a) | Sub Soil Water Level |  |  |  |  | 11 | M
| (b) | Draw down created during pumping |  |  |  |  | 2 | M
| (c) | Frictional Loss in pipe and Treatment Unit |  |  |  |  | 5 | M
| (d) | Residual Head required to the pump |  |  |  |  | 12 | M
[7 empty] | 30 | M
Taking efficiency of Motor Pump --- 80%
|  | B.H.P. of Motor Pump |  | = | WQH
75 n
|  |  |  | = | 2.7978 | x | 30
[5 empty] | 75 | x | 0.7
[5 empty] | 1.5988 | HP
|  |  |  | Say | 2 | HP
| Considering life of Motor Pump :- |  |  |  | 15 Years
| Hence one no. of Subemersible Pump of |  |  |  | 2 | H.P.
| For Discharging |  | 2.7978 | LPS
| Capacity acting against a total head of |  |  | 30 | M Head
will be provide in both the present and intermediate stage.
| Hence we shall provide one nos |  |  | 2 | H.P. Submersible Pump
Executive Engineer P.H. Division, Hajipur

## IRP DESIGN (hidden)
CALCULATION OF CAPACITY OF IRON TREATMENT PLANT
1 | #REF! | #REF! | #REF! | #REF! |  | Scheme | 6B (MUSLIM TOLA)
As per CPHEEO monual on Water Supply and Treatment published by the Ministry of Urban Development Department, Government of India in May 1999, the design period of Water Treatment Unit is 15 years only.
Hence, Capacity of proposed Iron Treatment Plant (IRP) has been calculated for Intermediate Year requirement.
| In Intermediate year Water Demand |  |  | = | 0.080577 | MLD
| Pumping Hour |  |  | = | 8 | Hours
|  |  |  | = | 0.080577 | x 103 | KL
|  |  |  | = | 80.5774 | /8
|  |  |  | = | 10.0722 | KLPH
|  |  |  | Say: | 8 | KLPH
|  |  | Hence, | 8 | KLPH | Capacity of IRP may be provided
Executive Engineer P.H. Division, Hajipur

## Energy Charge (hidden)
Sub Estimate No.-10B
COST OF ENERGY CHARGES
1 | Cost of Energy charges
| HP of pump =3HP |  | 3
| 3 | HP | = | 2.238 | KW
| Oprating Hour Average running |  |  | 6 | Hours/Day
| Unit Expenditure per year |  |  | 5440.3542 | Unit
| Energy Charges @ |  |  | 8.31 | per Unit | 45209.3434
| Fixed charges (3HPx100x365/30) |  | 1 | 100 | Per HP per month | 3650 | 3650
| Duty charges @ 6% of energy charges |  |  |  |  | 2712.5606
| Total |  |  |  |  | 0
2 | Cost of Energy charges
| HP of pump =2HP |  | 2
| 2 | HP | = | 1.492 | KW
| Oprating Hour Average running |  |  | 6 | Hours/Day
| Unit Expenditure per year |  |  | 3626.9028 | Unit
| Energy Charges @ |  |  | 8.31 | per Unit | 30139.5623
| Fixed charges (2HPx100x365/30) |  | 1 | 100 | Per HP per month | 2433.3333
| Duty charges @ 6% of energy charges |  |  |  |  | 1808.3737
| Total |  |  |  |  | 0
Executive Engineer
P.H. Division, Hajipur

## Boring (hidden)
Sub Estimate no.- 1
CONSTRUCTION OF 150MM X 100MM DIA & 125M DEEP TUBE WELL
S.No. | Description | Qty. |  | Unit | Rate | Amount
1 | Boring/drilling bore well of required dia for casing/strainer pipe, by suitable method prescribed in IS: 2800 (part I), including collecting samples from different strata, preparing and submitting strata chart/ bore log, including hire & running charges of all equipments, tools, plants & machineries required for the job, all complete as per direction of Engineer -in-charge, upto 90 metre depth below ground level. (All types of soil)
24.1.1.2 | (a) 350mm dia bore from G.L. to 30.0M | 30 | M | P/M | 532.4 | 15972
24.1.1.1 | (b) 300mm dia bore from 30.0 m to 60.0M | 30 | M | P/M | 486.8 | 14604
| (c) 300mm dia bore from 60M to 90.0M | 30 | M | P/M | 486.8 | 14604
24.2.1 | (d) 300mm dia bore from 90.0M to 150.0M | 35 | M | P/M | 567.9 | 19876.5
2A | Supplying, assembling, lowering and fixing in vertical position in bore well, unplasticized PVC (UPVC) medium well casing (CM) pipe of required dia, conforming to IS: 12818, including required hire and labour charges, fittings & accessories etc. all complete, for all depths, as per direction of Engineer -in-charge.
24.3.2 | (a) 150 mm nominal size dia | 30 | M | P/M | 660.1 | 19803 | 246165 | 1969.32 | 177238.8
24.3.1 | (b) 100 mm nominal size dia | 60 | M | P/M | 546.1 | 32766
2B | Supplying, assembling, lowering and fixing in vertical position in bore well unplasticized PVC (UPVC) medium well screen (RMS) pipes with ribs, conforming to IS: 12818, including hire & labour charges, fittings & accessories etc. all complete, for all depths, as per direction of Engineer-in-charge.
24.4.1 | 100 mm nominal size dia | 30 | M | P/M | 573.1 | 17193
3 | Supplying the following fittings & fixing the same in position as per approved lowering assembly and strata chart including providing all equipments and welding the same on process of lowering the assay etc. all complete as per S/D of E/I.
24.13.2 | (a) 150 mm dia well cap | 1 | No. | Each | 210.7 | 210.7
24.14.2 | (b) 150 mm dia M.S. Clamp 1.6 M long (one Pair) | 1 | No. | Each | 1531.4 | 1531.4
| (c) 150 mm dia center guide | 4 | Nos. | Each | 150 | 600
| (d) 100 mm dia center guide | 6 | Nos. | Each | 100 | 600
| (e) 150 mm x 100 mm dia 6mm wall thickness MS reducer | 1 | No. | Each | 500 | 500
24.15.1 | (f) 100mm dia & 6mm thick M.S. well shoe plug | 1 | No. | Each | 228.3 | 228.3
4a 24.6 | Providing all materials, labours, & equipments for fixing tube well with pea gravel of Dalbhumigarh to size 4mm to 8mm approx. as suitable for strata including carriage washing, placing and packing the same in position around the tube well etc. all complete as per direction of E/I. | 9 | M3 | P/M3 | 1343.2 | 12088.8
4b | Carriage of Pea Gravel from Dhalbhumigarh (taken av distance 400km.) | 9 | M3 | P/M3 | 0 | 0
5 24.12 | Development of tube well in accordance with IS : 2800 (part I) and IS: 11189, to establish maximum rate of usable water yield without sand content (beyond permissible limit), with required capacity air compressor, running the compressor for required time till well is fully develo ped, measuring yield of well by "V" notch method or any other approved method, measuring static level & draw down etc. by step draw down method, collecting water sampl &getting tested in approved laboratory, disinfection of tubewell, all complete,including hire & labour charges of air compressor, tools & accessories etc., all as per requirement and direction of Engineer-in-charge. | 24 | Hrs. | P/H | 916.8 | 22003.2
6 | Transportation of drilling plants, developing equipments & all other required tools and M/c by and suitable mechanical means including all cost of loading, unloading, placing at work site and back after completion of work as per S/D of E/I | 1 | No. | Each | 9200 | 9200
7 | Supplying all materials and labours for arrangement for additional water required during the drilling period for 70 Hrs & site clearance & leveling etc. And providing the soap duster etc. to staff engaged in drilling etc. all complete work as per specification & direction of E.I. | 1 | No. | Each | 7000 | 7000
| TOTAL |  |  |  |  | 0
| Say |  |  |  |  | 0 |  |  | #REF!
188780.9
#REF!
#REF!

## Work sheet detail (2) (hidden)
ABSTRACT OF MAJOR PRD WARDS & THEIR DAMAGED COMPONENTS
Name Of Work- |  |  | REPAIRING OF NON-FUNCTIONAL PRD SCHEMES / (WARDS) TO MAKE IT FUNCTIONAL THAT HAVE BEEN TAKEN OVER BY PHED IN VAISHALI DISTRICT.
Block- |  |  | Bidupur
Sl.No | Panchyat | Ward No. | New Boring | Boring chamber | 3 H.P motor | New Starter | New Stablizer | NEW HDPE PIPE (Length in Mtr.) |  |  |  |  | Riser & Dilivery | Water Tank | Chlorinator | New Steel Staging | Painting Of Staging | Room Of Staging | Floor Of Staging | Ladder | New H.C | Repairing H.C | New Bib cock | Repair Motar | Repair Stater | Repair Stablizer | Service Cabel | Tank Cleaning | Leakage of HDPD Pipe (in Nos.) with PCC Road Cuting |  |  |  |  | Leakage of HDPD Pipe (in Nos.) without PCC Road cutting |  |  |  |  | Miscellaneous work | Total Amount In (Lakh)
[8 empty] | 90 MM | 75 MM | 63 MM | 50 mm | 40 MM | [16 empty] | 90 MM | 75 MM | 63 MM | 50 mm | 40 MM | 90 MM | 75 MM | 63 MM | 50 mm | 40 MM
|  |  | 1 | 2 | 3 | 4 | 5 | 6 |  |  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 |  |  |  |  | 23 |  |  |  |  | 24
1 | Saidpur Ganesh | 12 | 0 | 1 | 0 | 1 | 1 | 0 | 0 | 25 | 50 | 75 | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 6 | 85 | 45 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 1 | 2 | 3 | 3 | 3 | 1 | #REF!

## Report (hidden)
GOVERNMENT OF BIHAR PUBLIC HEALTH ENGINEERING DEPARTMENT PUBLIC HEALTH DIVISION, HAJIPUR.
NAME OF WORK:- CONSTRUCTION OF RURAL PIPED WATER SUPPLY SCHEME FOR THE LEFT OUT
HABITATIONS IN, PANCHAYAT- |  |  | DAULATPUR CHANDI |  | UNDER THE WARDS |  |  | 6B (MUSLIM TOLA)
TOTAL 01 NO'S SCHEMES, BLOCK - |  |  |  | HAJIPUR |  | OF VAISHALI DISTRICT HAVING |  |  | 150
HOUSE HOLDS WITH & 8 MTR. STEEL STAGING
REPORT
This estimate has been framed by Executive Engineer, P.H. Division, Hajpur for construction of rural piped water
Supply Scheme in Leftout Habitations of Panchayat- |  |  |  |  | DAULATPUR CHANDI |  | A Total of 1 No of Schems are
included in this Estimate under the panchayat, Block- |  |  |  |  | HAJIPUR |  | This estimate has been framed as per
guideline of “Har Ghar Nal Ka Jal”and as per direction of Engineer in Chief-cum-Special Secretary, P.H.E.D., Bihar,
Patna vide his Letter No.- 6B@fo0&106@2023& 314 Dated 19-04-2023.for the habitations of Vaishali district under
P.H Division, Hajipur
Below said habitations are situated either far away from the source of nearest existing water supply schemes or
obstructed through rivers/depressions/railway lines/NH etc. Hence there is a need of one Piped Water Supply Scheme
for saturation of each of the habitations. We have made provision of T/well, Motor pump, Steel Structure, Distrubtion
of pipe line, house connection etc. in the estimate.
Details provision made for this habitation with proposed house connection is as tabulated below : -
Sl. No. | Block | Panchayat | Proposed T/well | Ward no. Covered | House Hold Covered | Proposed length of diff. dia. Pipe line |  |  | Estimated Cost (in lacs)
1 | #REF! | #REF! | #REF! | #REF! | 150 | Dia mm | Length (m) | Rate
[6 empty] | 110 | #REF! | 646.25
[6 empty] | 90 | #REF! | 437.96 | #REF!
[6 empty] | 75 | #REF! | 306.31
[6 empty] | 63 | #REF! | 218.62
[6 empty] | 50 | #REF! | 116.25
[6 empty] | 40 | #REF! | 76.53
[6 empty] | Total | #REF!
Specification :- The standard specification of P.H.E.D. and PWD will be followed during the Execution of work
Time of completion: - This work will be completed in six (6)month after the fund is made available.
Estimated | cost :The estimated cost |  |  |  | #REF! | Lacs
Executive Engineer,
P. H. Division,………………....

## Cover Page
GOVERNMENT OF BIHAR
PUBLIC HEALTH ENGINEERING DEPARTMENT
PUBLIC HEALTH DIVISION - BEGUSARAI
Bill of Quantity
Comprehensive operation and maintenance, routine repairs and Special repairs of Rural Piped Water Supply Scheme 17 (PWS&SVS), Ward level Piped Water Supply Schemes 555 in quality affected wards (WLS_Quality) and Ward level Piped Water Supply Schemes 82 in non quality affected wards (WLS_Non Quality) based on item rates; constructed by the Public Health Engineering Department including payment to the pump operators, electricity bills for five years. Under P.H. Division, Begusarai for the Period 2026-2031 in the district of Begusarai.
No. of Schemes | 654 | Nos.
ESTIMATED COST - |  |  | 751861700
UNDER MUKHYA MANTRI PEYJAL NISCHAY YOJNA-2
Financial Year - 2026-27

## Financial Gr.1
FINANCIAL BID
NIT No.-03/BGS/O&M-PHED/2026-27
GROUP No.:-1
NAME OF WORK- |  | Part I: Fixed Operation of ward level piped water supply schemes (Quality affected/NQ affected) by deploying pump operators and payment of electricity charges and Part II: Variable Comprehensive maintenance of Ward level water supply schemes (PWS/SVS,Quality affected/NQ affected), i/c the cost of chemicals, overhauling of filter media and related apputenances, cleaning of ESR and campus, maintenance viz. cleaning painting of pump house, boundary wall, repair of leakages in districbuition line, repair and provision of new FHTCs, repair amd maintenance of pumps and other electromechanical components etc. all complete as per the directions of Engineer-in-charge. in Blocks:-Begusarai, Ballia, S.Kamal, Dandari, Samho, Nawkothi, Bakhri, Gardhpura & Matihani. No. of schemes: WLS(Non Quality): 82 WLS(Quality): 555 PWS &SVS : 17
Date of Tender :- |  | 04.06.2026
Estimated Cost :- |  | 7518.617 Lakh
Earnest Money :- |  | 85.187 Lakh
Duration of Maintenance Period |  | 60 Months
Cost of BOQ :- |  | As per online
SCHEDULE- 'A'
SI NO. | PARTICULARS |  |  | No. of Scheme | AMOUNT
1 | 2 |  |  | 3 | 4
1 | I. Operation of ward level piped water supply schemes (Quality affected/NQ affected) by deploying pump operators and payment of electricity charges and II. Comprehensive maintenance of Ward level water supply schemes (Quality affected/NQ affected) i/c the cost of chemicals, overhauling of filter media and related apputenances, cleaning of ESR and campus, maintenance viz. claning painting of pump house, boundary wall, repair of leakages in districbuition line, repair and provision of new FHTCs, repair amd maintenance of pumps and other electromechanical components etc. all complete as per the directions of Engineer-in-charge. |  |  | i.) Rural Piped Water Supply Scheme 17 (PWS & SVS), ii.) Ward level Piped Water Supply Schemes 555 in quality affected wards (WLS_Quality) and iii.) Ward level Piped Water Supply Schemes 82 in non quality affected wards (WLS_Non Quality) | 7518.617
Total Amount |  |  |  |  | 7518.617
Rupees:- Seventy five crore eighteen lakh sixty one thousand seven hundred Only
SCHEDULE- B---------------------------- NIL
SCHEDULE- C---------------------------- NIL
1 | Estimated cost |  | Rs. | 7518.617 | (A)
2 | Cost of Govt. Material |  | :- | NIL | NIL (B)
3 | Name of the Contractor |  | :-
4 | Address of the Contractor |  | :-
5 | I/we offer in Figures……. in words………………… % (Percentage) High on the rate for the fixed cost (Part I) for operation of the schemes. |  | IN FIG.
|  |  | IN WORDS |  |  |  | 60
6 | I/we offer in Figures……. in words………………… % (Percentage) High / Less on the rate for the variable cost (Part-II) for maintenance of the schemes. |  | IN FIG. |  |  |  | 100
IN WORDS
7 | Average rate quoted by the bidder |  |  | 0
| Note :- 1.) Bidders has to quote rate in Percentage High/Less only. |  |  |  |  | 0.6
Note :- 2.) Items/ Quantity of Work will be decided by the department on day to day / priority basis during period of maintenance.
Note :- 3.) The quoted rate for the operation part I (fixed cost) i.e. the payment to the operators and the electricity bills, the quote shall not be negative.
Note :- 4.) The electricity bills shall be paid as per actual.
Note :- 5.) The entry in row 7 shall be considered for decision of financially lowest bid.
Executive Engineer, P.H.Division, Begusarai

## BoQ_FC
BoQ (Fixed Cost)
I. | Fixed Costs (WLS (Q/NQ))
(a) | Cost of pump operator
| 1 nos for 365 days | per month | 48000 | 12 | 4000 | 48000
Sub Total a= | [5 empty] | 48000
(b) | Cost of energy charges
| Capacity of motor pump say 17.50 HP=(.746x17.5=13.055 kW) | kW |  | 2.24
| Avg. running hrs,/day |  |  | 8
| Energy charges per year= avg. running hrs/dayx.746x17.5x365 | per unit |  | 6534.96 | 2.6 | 16990.896
| fixed charges per month |  |  | 12 | 100 | 3600
| duty charges @6% of energy charge |  |  |  |  | 1019.45
SubTotal b= | [5 empty] | 21610.346
Total Fixed Cost (I) = | [5 empty] | 69610.346
| Contractor's profit @ 10% on (II)= |  |  |  |  | 11761.0346
| Add GST @ 18% on ( II)= |  |  |  |  | 2116.9862
| Total Cost (I) |  |  |  |  | 83488.3668

## BoQ_1
GOVERNMENT OF BIHAR
Public Health Engineering Department
Bill of Quantity 1 (Variable Cost)
S.N. | Description | [12 empty] | Quantity | Unit | Rate | Total Amount
1A | Construction of 150mm X100mmx 125m deep T/W etc. all complete and as per direction of E/I.(As per sub Estimate no.- 1) | [12 empty] | 1 | Nos. | 294314.7312 | 294314.7312
1B | Construction of 150 mmX90m deep drilled T/W etc. all complete and as per direction of E/I. | [12 empty] | 1 | Nos. | 180147.6888 | 180147.6888
2 | Constructing masonry Chamber 100x100x75 cm inside, in brick work in cement mortar 1:4 (1 cement : 4 coarse sand) for Tube Well, and RCC top slab 1:1.5:3 mix (1 cement : 1.5 coarse sand : 3 graded stone aggregate 20mm nominal size ) , necessary excavation, foundation concrete 1:2:4(1 cement : 2 fine sand : 4 graded stone aggregate 20 mm nominal size) and inside plastering with cement mortar 1:3 (1 cement : 3coarse sand) 12 mm thick with 5% cico fnished with a floating coat of neat cement, out side plastering with cement mortar 1:4 (1 cement : 4coarse sand) 12 mm thick complete as per standard specifications & direction of E/I. (As per sub Estimate no.- 2) | [12 empty] | 1 | Nos. | 15314.076 | 15314.076
3A | Supply Installation, commissioning and testing of single phase 3 H.P submersible pump set having discharging capacity 3.35 lps at a total head of 35 meter(approx) of different capacity of KSB/ Kirloskar or equivalent make with all accessories & fittings such as 7.5KVA Stabalizer, cable, panel board etc including loading unloading and transportation of the pump set to the work site with all required labour, materials, tools and tackles installation, testing & commissioning as per standards specifications and direction of E/I. (As per sub Estimate no.- 3a) | [12 empty] | 1 | Nos. | 110628 | 110628
3AA | Supply Installation, commissioning and testing of single phase 3 H.P submersible pump set only having discharging capacity 3.35 lps at a total head of 35 meter(approx) of different capacity of KSB/ Kirloskar or equivalent make with all accessories & fittings etc including loading unloading and transportation of the pump set to the work site with all required labour, materials, tools and tackles installation, testing & commissioning excluding the cost of GI pipes for lowering and cables etc. as per standards specifications and direction of E/I. (As per sub Estimate no.- 3a items) | [12 empty] | 1 | Nos. | 25000 | 25000
3B | Supply Installation, commissioning and testing of single phase 2 H.P submersible pump set having discharging capacity 2.25 lps at a total head of 35 meter(approx) of different capacity of KSB/ Kirloskar or equivalent make with all accessories & fittings such as 7.5KVA Stabalizer, cable, panel board etc including loading unloading and transportation of the pump set to the work site with all required labour, materials, tools and tackles installation, testing & commissioning as per standards specifications and direction of E/I. (As per sub Estimate no.- 3b) | [12 empty] | 1 | Nos. | 68220.6 | 68220.6
3BB | Supply Installation, commissioning and testing of single phase 2 H.P submersible pump set having discharging capacity 2.25 lps at a total head of 35 meter(approx) of different capacity of KSB/ Kirloskar or equivalent make with all accessories & fittings etc including loading unloading and transportation of the pump set to the work site with all required labour, materials, tools and tackles installation, testing & commissioning excluding the cost of GI pipes for lowering and cables etc. as per standards specifications and direction of E/I.(As per sub Estimate no.- 3B items) | [12 empty] | 1 | Nos. | 20000 | 20000
3C | Supply Installation, commissioning and testing of three phase 5 H.P submersible pump set including light wiring, power wiring and extension of over head L.T line from nearest point of electric line up to pump room having 50 C/sec. 2900 rpm at a total head of 35 meter(approx) of different capacity of KSB/ Kirloskar or equivalent make with all accessories & fittings etc including loading unloading and transportation of the pump set to the work site with all required labour, materials, tools and tackles installation, testing & commissioning complete set as per standards specifications and direction of E/I. (As per sub Estimate no.- 3c) | [12 empty] | 1 | Nos. | 140107.728 | 140107.728
3CC | Supply Installation, commissioning and testing of three phase 5 H.P submersible pump set only having 50 C/sec. 2900 rpm at a total head of 35 meter(approx) of different capacity of KSB/ Kirloskar or equivalent make with all accessories & fittings etc including loading unloading and transportation of the pump set to the work site with all required labour, materials, tools and tackles installation, testing & commissioning excluding the cost of GI pipes for lowering and cables etc. as per standards specifications and direction of E/I. | [12 empty] | 1 | Nos. | 40000 | 40000
4a | Providing & Fixing BIS approved 3 HP submersible motar starter all complete as per direction of engineer in charge. (As per sub Estimate no.- 4a) | [12 empty] | 1 | Nos. | 5478.72 | 5478.72
4b | Providing & Fixing BIS approved 2 HP submersible motar starter all complete as per direction of engineer in charge. (As per sub Estimate no.- 4b) | [12 empty] | 1 | Nos. | 4741.2 | 4741.2
4c | Providing & Fixing BIS approved 5 HP submersible motar starter all complete as per direction of engineer in charge. (As per sub Estimate no.- 4c) | [12 empty] | 1 | Nos. | 6321.6 | 6321.6
5a | Supply & Installation of 90-220 V range single phase7. 5 KVA automatic voltage stabilizer make- Sen & Pandit/ Vertex/ISI marked Stabilizer of reputed make. (As per sub Estimate no.- 05) | [12 empty] | 1 | Nos. | 26340 | 26340
5b | Supply & Installation of 90-220 V range single phase 5.0 KVA automatic voltage stabilizer make- Sen & Pandit/ Vertex/ISI marked Stabilizer of reputed make. (As per sub Estimate no.- 05) | [12 empty] | 1 | Nos. | 21072 | 21072
6A | Providing and Laying Distrbution network of 90 MM High Density Polyethylene pipe (HDPE pipe) all complete as per direction of E/I. (As per sub Estimate no.- 6A ) * | [12 empty] | 1 | per m | 794.9397 | 794.9397
6B | Providing and Laying Distrbution network of 75 MM High Density Polyethylene pipe (HDPE pipe) all complete as per direction of E/I. (As per sub Estimate no.- 6B ) * | [12 empty] | 1 | per m | 649.3021 | 649.3021
6C | Providing and Laying Distrbution network of 63 MM High Density Polyethylene pipe (HDPE pipe) all complete as per direction of E/I. (As per sub Estimate no.- 6C ) * | [12 empty] | 1 | per m | 552.2971 | 552.2971
6D | Providing and Laying Distrbution network of 50 MM High Density Polyethylene pipe (HDPE pipe) all complete as per direction of E/I. (As per sub Estimate no.- 6D ) * | [12 empty] | 1 | per m | 439.0457 | 439.0457
6E | Providing and Laying Distrbution network of 40 MM High Density Polyethylene pipe (HDPE pipe) all complete as per direction of E/I. (As per sub Estimate no.- 6E ) * | [12 empty] | 1 | per m | 395.1 | 395.1
7a | Cost of replacement of riser / delivery pipe by 50 mm dia G.I.Pipe from T/well to PVC Tank | [12 empty] | 1 | per m | 603.2914 | 603.2914
7b | Cost of replacement of riser / delivery pipe by 65 mm dia G.I.Pipe from PVC Tank to Distribution main | [12 empty] | 1 | per m | 703.4887 | 703.4887
7c | Cost of replacement of riser / delivery pipe by 80 mm dia G.I.Pipe for wash out | [12 empty] | 1 | per m | 862.0555 | 862.0555
7d | Providing and fixing brass gate valve with C.I. wheel of approved quality (screwed end). 80mm dia Pipe | [12 empty] | 1 | Job | 2346.9994 | 2346.9994
7e | Providing and fixing brass gate valve with C.I. wheel of approved quality (screwed end). 50mm dia Pipe | [12 empty] | 1 | Job | 925.2715 | 925.2715
7f | Supplying all materials labours & fixing 50mm dia. G.I pipe for using as filling station etc. All as per direction of E/I. | [12 empty] | 1 | Job | 3756.6108 | 3756.6108
8 | Estimate for supply & installation of water storage tank (5000 Ltr. =5000 X 1) as per direction of engineer in charge. (As per sub Estimate no.- 08) | [12 empty] | 1 | Job | 55840.8 | 55840.8
9 | Installation of Electronically Regulated Doser type chlorinator using Sodium Hypo Chlorite (Hypo NaOCl) (As per sub Estimate no.-09) | [12 empty] | 1 | Nos. | 24775.404 | 24775.404
10 | Providing and erecting 8M high staging with ladder of ISA65x65x6 and 16mm dia MS bar as trade @ 400mm c/c and GI enclosure to house electric switch panel & treatment unit (where required) of suitably designed MS section of angle, channel, etc. as per drawing attached. (As per sub Estimate no.-10) * | [12 empty] | 1 | Job | 734253.84 | 734253.84
11 | Estimate for Painting of 8M Steel Staging all complete as per direction of engineer in charge. (As per sub Estimate no.- 11) | [12 empty] | 1 | Job | 21282.72 | 21282.72
12a | Estimate for Providing GI enclosure to house electric switch panel for steel structure staging all complete. (As per sub Estimate no.- 12) * | [12 empty] | 1 | per m2 | 1581.77 | 1581.77
12 b | Repair/ Replacement of M.S angle / channel / Roof Sheet including riveted/ welded/bolted in built up sections, trusess and framed work, including cutting,hoisting,fixing in position and applying a priming coat of approved primer all complete | [12 empty] | 1 | per Kg | 109.5744 | 109.5744
13a | Estimate for Construction of floor of staging etc. all complete as per direction of engineer in charge. (As per sub Estimate no.- 13) * | [12 empty] | 1 | per m2 | 1625.5075 | 1625.5075
14 | Providing ladder in staging including all accessories etc. all complete. (As per sub Estimate no.- 14) | [12 empty] | 1 | Job | 13148.928 | 13148.928
15 | Providing New house connection for each house hold including supplying all materials, labours, tools and making ferrule connection with 20 mm dia MDPE and 15mm G.I Pipes with all fittings etc all complete. (As per sub Estimate no.- 15) | [12 empty] | 1 | Each | 2623.464 | 2623 | 5000
15a | Providing New house connection without retrofitting for each house hold including supplying all materials, labours, tools and making ferrule connection with 20 mm dia MDPE and 15mm G.I Pipes with all fittings etc all complete. (As per sub Estimate no.- 15a) | [12 empty] | 1 | Each | 2197 | 2197
16 | Repairing of House Connection (As per sub Estimate no.- 16) | [12 empty] | 1 | Nos. | 801.7896 | 801.7896
16A | Repairing of House Connection with leakage at ferrule (As per sub Estimate no.- 16A) | [12 empty] | 1 | Nos. | 1495.0584 | 1495.0584
16B | Minor repairs to House Connection (As per sub Estimate no.- 16B) | [12 empty] | 1 | Nos. | 191.7552 | 191.7552
17 | Replacing of damage Bib cock with New Bib cock (As per sub Estimate no.- 17) | [12 empty] | 1 | Nos. | 115.896 | 115.896
18 | Repairing of 3 HP/2 HP Pump Motor (As per sub Estimate no.- 18) | [12 empty] | 1 | Nos. | 9355.968 | 9355.968
18b | Repairing of 5 HP Pump Motor (As per sub Estimate no.- 18b) | [12 empty] | 1 | Nos. | 16583.664 | 16583.664
19 | Repairing of Starter (As per sub Estimate no.- 19) | [12 empty] | 1 | Nos. | 1580.4 | 1580.4
20 | Repairing of Stabilizer (As per sub Estimate no.- 20) | [12 empty] | 1 | Nos. | 3160.8 | 3160.8
21 | Supplying & fitting 2.5 mm2 copper service cable from power point from nearest source up-to pumping station. (As per sub Estimate no.- 21) | [12 empty] | 1 | per m | 136.968 | 136.968
22 | Cleaning of one 5000 Ltr capacity overhead pvc tank and getting water quality tested from departmental lab. (As per sub Estimate no.- 22) | [12 empty] | 1 | Nos. | 526.8 | 526.8
23A | Repairing of Leakages in HDPE Pipe line with PCC cutting & Restoration. (For HDPE Laid at depth 0.5 to 1.0 m)(As per sub Estimate no.- 23) | [16 empty] | 250 | 5 | 10 | 12500
| 90 mm Dia | [12 empty] | 1 | Nos. | 1671.0096 | 1671.0096
| 75 mm Dia | [12 empty] | 1 | Nos. | 1652.0448 | 1652.0448
| 63 mm Dia | [12 empty] | 1 | Nos. | 1596.204 | 1596.204
| 50 mm Dia | [12 empty] | 1 | Nos. | 1563.5424 | 1563.5424
| 40 mm Dia | [12 empty] | 1 | Nos. | 1536.1488 | 1536.1488
23B | Repairing of Leakages in HDPE Pipe line without PCC cutting & Restoration.(For HDPE Laid at depth 0.5 to 1.0 m)(As per sub Estimate no.- 23)
| 90 mm Dia | [12 empty] | 1 | Nos. | 1262.2128 | 1262.2128
| 75 mm Dia | [12 empty] | 1 | Nos. | 1243.248 | 1243.248
| 63 mm Dia | [12 empty] | 1 | Nos. | 1187.4072 | 1187.4072
| 50 mm Dia | [12 empty] | 1 | Nos. | 1154.7456 | 1154.7456
| 40 mm Dia | [12 empty] | 1 | Nos. | 1127.352 | 1127.352
24A | Repairing of Leakages in HDPE Pipe line with PCC cutting & Restoration. (For HDPE Laid at depth 0.0 to 0.5 m)(As per sub Estimate no.- 24)
| 90 mm Dia | [12 empty] | 1 | Nos. | 1590.936 | 1590.936
| 75 mm Dia | [12 empty] | 1 | Nos. | 1571.9712 | 1571.9712
| 63 mm Dia | [12 empty] | 1 | Nos. | 1516.1304 | 1516.1304
| 50 mm Dia | [12 empty] | 1 | Nos. | 1483.4688 | 1483.4688
| 40 mm Dia | [12 empty] | 1 | Nos. | 1456.0752 | 1456.0752
24B | Repairing of Leakages in HDPE Pipe line without PCC cutting & Restoration.(For HDPE Laid at depth 0.0 to 0.5 m)(As per sub Estimate no.- 24)
| 90 mm Dia | [12 empty] | 1 | Nos. | 1182.1392 | 1182.1392
| 75 mm Dia | [12 empty] | 1 | Nos. | 1163.1744 | 1163.1744
| 63 mm Dia | [12 empty] | 1 | Nos. | 1107.3336 | 1107.3336
| 50 mm Dia | [12 empty] | 1 | Nos. | 1074.672 | 1074.672
| 40 mm Dia | [12 empty] | 1 | Nos. | 1047.2784 | 1047.2784 | 2500
25 | Supplying and laying of submersible flat cable ISI marked 3 core copper wire of suitable size with proper clamping of approved make. (Rate Chattisgarh SOR 34.20.107) | Supplying and laying of submersible flat cable ISI marked 3 core copper wire of suitable size with proper clamping of approved make. (Rate Chattisgarh SOR 34.20.107 Rs.121.00+18% GST) | Supplying and laying of submersible flat cable ISI marked 3 core copper wire of suitable size with proper clamping of approved make. (Rate Chattisgarh SOR 34.20.107 Rs.121.00+18% GST) | Supplying and laying of submersible flat cable ISI marked 3 core copper wire of suitable size with proper clamping of approved make. (Rate Chattisgarh SOR 34.20.107 Rs.121.00+18% GST) | Supplying and laying of submersible flat cable ISI marked 3 core copper wire of suitable size with proper clamping of approved make. (Rate Chattisgarh SOR 34.20.107 Rs.121.00+18% GST) | Supplying and laying of submersible flat cable ISI marked 3 core copper wire of suitable size with proper clamping of approved make. (Rate Chattisgarh SOR 34.20.107 Rs.121.00+18% GST) | Supplying and laying of submersible flat cable ISI marked 3 core copper wire of suitable size with proper clamping of approved make. (Rate Chattisgarh SOR 34.20.107 Rs.121.00+18% GST) | Supplying and laying of submersible flat cable ISI marked 3 core copper wire of suitable size with proper clamping of approved make. (Rate Chattisgarh SOR 34.20.107 Rs.121.00+18% GST) | Supplying and laying of submersible flat cable ISI marked 3 core copper wire of suitable size with proper clamping of approved make. (Rate Chattisgarh SOR 34.20.107 Rs.121.00+18% GST) | Supplying and laying of submersible flat cable ISI marked 3 core copper wire of suitable size with proper clamping of approved make. (Rate Chattisgarh SOR 34.20.107 Rs.121.00+18% GST) | Supplying and laying of submersible flat cable ISI marked 3 core copper wire of suitable size with proper clamping of approved make. (Rate Chattisgarh SOR 34.20.107 Rs.121.00+18% GST) | Supplying and laying of submersible flat cable ISI marked 3 core copper wire of suitable size with proper clamping of approved make. (Rate Chattisgarh SOR 34.20.107 Rs.121.00+18% GST) | Supplying and laying of submersible flat cable ISI marked 3 core copper wire of suitable size with proper clamping of approved make. (Rate Chattisgarh SOR 34.20.107 Rs.121.00+18% GST) | 1 | m | 127.4856 | 127.4856 | 7500
26 | Replacing damaged portion of riser and delivery pipe 8 meter staging with CPVC / UPVC pipe and providing gun metal Gate valve. (Sub Estimate No.26)
| Replacing damaged portion 50 mm dia. CPVC / UPVC Riser pipe | Replacing damaged portion 50 mm dia. Riser pipe | Replacing damaged portion 50 mm dia. Riser pipe | Replacing damaged portion 50 mm dia. Riser pipe | Replacing damaged portion 50 mm dia. Riser pipe | Replacing damaged portion 50 mm dia. Riser pipe | Replacing damaged portion 50 mm dia. Riser pipe | Replacing damaged portion 50 mm dia. Riser pipe | Replacing damaged portion 50 mm dia. Riser pipe | Replacing damaged portion 50 mm dia. Riser pipe | Replacing damaged portion 50 mm dia. Riser pipe | Replacing damaged portion 50 mm dia. Riser pipe | Replacing damaged portion 50 mm dia. Riser pipe | 1 | m | 833.4 | 833.4 | 1000
| Replacing damaged portion 80 mm dia. CPVC / UPVC Riser pipe | Replacing damaged portion 80 mm dia. Riser pipe | Replacing damaged portion 80 mm dia. Riser pipe | Replacing damaged portion 80 mm dia. Riser pipe | Replacing damaged portion 80 mm dia. Riser pipe | Replacing damaged portion 80 mm dia. Riser pipe | Replacing damaged portion 80 mm dia. Riser pipe | Replacing damaged portion 80 mm dia. Riser pipe | Replacing damaged portion 80 mm dia. Riser pipe | Replacing damaged portion 80 mm dia. Riser pipe | Replacing damaged portion 80 mm dia. Riser pipe | Replacing damaged portion 80 mm dia. Riser pipe | Replacing damaged portion 80 mm dia. Riser pipe | 1 | m | 1990.78 | 1990.78
| Replacing CPVC / UPVC Gate Valve 50 mm dia. | Replacing Gate Valve 50 mm dia. | Replacing Gate Valve 50 mm dia. | Replacing Gate Valve 50 mm dia. | Replacing Gate Valve 50 mm dia. | Replacing Gate Valve 50 mm dia. | Replacing Gate Valve 50 mm dia. | Replacing Gate Valve 50 mm dia. | Replacing Gate Valve 50 mm dia. | Replacing Gate Valve 50 mm dia. | Replacing Gate Valve 50 mm dia. | Replacing Gate Valve 50 mm dia. | Replacing Gate Valve 50 mm dia. | 1 | Nos. | 915 | 915 | 915
| Replacing CPVC / UPVC Gate Valve 80 mm dia. | Replacing Gate Valve 80 mm dia. | Replacing Gate Valve 80 mm dia. | Replacing Gate Valve 80 mm dia. | Replacing Gate Valve 80 mm dia. | Replacing Gate Valve 80 mm dia. | Replacing Gate Valve 80 mm dia. | Replacing Gate Valve 80 mm dia. | Replacing Gate Valve 80 mm dia. | Replacing Gate Valve 80 mm dia. | Replacing Gate Valve 80 mm dia. | Replacing Gate Valve 80 mm dia. | Replacing Gate Valve 80 mm dia. | 1 | Nos. | 2240 | 2240 | 2240
27 | Development of Twell. (Sub Estimate No.27) | Development of Twell. (Sub Estimate No.11) | Development of Twell. (Sub Estimate No.11) | Development of Twell. (Sub Estimate No.11) | Development of Twell. (Sub Estimate No.11) | Development of Twell. (Sub Estimate No.11) | Development of Twell. (Sub Estimate No.11) | Development of Twell. (Sub Estimate No.11) | Development of Twell. (Sub Estimate No.11) | Development of Twell. (Sub Estimate No.11) | Development of Twell. (Sub Estimate No.11) | Development of Twell. (Sub Estimate No.11) | Development of Twell. (Sub Estimate No.11) | 1 | Job | 16973.496 | 16973.496
28 | Repairing and painting of RCC staging (Sub Estimate No.28) | Development of Twell. (Sub Estimate No.11) | Development of Twell. (Sub Estimate No.11) | Development of Twell. (Sub Estimate No.11) | Development of Twell. (Sub Estimate No.11) | Development of Twell. (Sub Estimate No.11) | Development of Twell. (Sub Estimate No.11) | Development of Twell. (Sub Estimate No.11) | Development of Twell. (Sub Estimate No.11) | Development of Twell. (Sub Estimate No.11) | Development of Twell. (Sub Estimate No.11) | Development of Twell. (Sub Estimate No.11) | Development of Twell. (Sub Estimate No.11) | 1 | Job | 75437.76 | 75437.76
29 | Restoration of road for pipeline work having trench size 300 mm. | Development of Twell. (Sub Estimate No.11) | Development of Twell. (Sub Estimate No.11) | Development of Twell. (Sub Estimate No.11) | Development of Twell. (Sub Estimate No.11) | Development of Twell. (Sub Estimate No.11) | Development of Twell. (Sub Estimate No.11) | Development of Twell. (Sub Estimate No.11) | Development of Twell. (Sub Estimate No.11) | Development of Twell. (Sub Estimate No.11) | Development of Twell. (Sub Estimate No.11) | Development of Twell. (Sub Estimate No.11) | Development of Twell. (Sub Estimate No.11) | 1 | per meter | 362.2593 | 362.2593
30 | Providing and fixing 19mm PVC/Block board with KitKat to affix/hang starter, fuses, IoT devices etc all complete as per the directions of the E/I. | [12 empty] | 1 | Job | 3000 | 3000
31 | Providing 50 mm GI pipe for lowering the riser pipe of submersible pump all complete as per the directions of the E/I. (Sub Estimate No.30) | [12 empty] | 1 | Job | 1512.506 | 1512.506
32 | Providing and fixing MS clamp consisting of 32mm x 5mm thick two no. rings spaced suitably distance apart around the tank and six nos. L type flats suitably connected with the rings and the other leg suitably connected with the top of the steel structure as per dirction of E/I. | [12 empty] | 1 | Job | 3000 | 3000
33 | Providing and fixixng of New PVC 5000 L Tank Cover with all accessories. | [12 empty] | 1 | Job | 300 | 300
34 | Providing and fixing M.S Stabiliser Stand near panel Board to keep stabiliser safe. | [12 empty] | 1 | Job | 2500 | 2500
35 | Renovation (Repairing and painting) of Attendent Cum Pump room & toilet. (As per sub Estimate no.- 31) | [12 empty] | 1 | Job | 31613.6063 | 31613.6063
36 | Renovation (Repairing and painting) of Existing Boundry wall of Length 29Mtr and height 1.5Mtr. all complete as per direction of E/I. (As per sub Estimate no.- 32) | [12 empty] | 1 | per meter | 1733.8226 | 1733.8226
37 | Campus development by land filling and brick soaling. (As per sub Est.no.-33) | [12 empty] | 1 | Job | 27302.8 | 27302.8
38 | Replacement of Existing Solar driven Pump with Electric driven single phase 2 H.P. submersible pump set having discharging capacity 3 lps at a total head of 45meter (approx) of KSB/ Kirloskar or equivalent make with all accessories & fittings etc including loading unloading and transportation of the pump set to the work site with all required labour, materials, tools and tackles installation, testing & commissioning as per standards specifications and direction of E/I. (As per sub Est. no.- 34) | [12 empty] | 1 | Job | Rs.88500.00 | 88500
39 | Supplying, installation Testing & commissioning of Solar Pannel plate etc all complete as per direction of E/I. (As per sub Est. no.- 35) | [12 empty] | 1 | Job | 15750 | 15750
40 | Supplying, installation Testing & commissioning of Variable Frequency Drive (VFD), Change over Switch and Net Energy Metering (NEM) system (As per sub Est. no.- 36) | [12 empty] | 1 | Job | 60450 | 60450
41 | Providing and Fixing 12 VOLT Solar Battery as per direction of E/I. (As per sub Est. no.- 37) | [12 empty] | 1 | Job | 35000 | 35000
42 | Providing all labours, tools and materials to repair the leakage of different sizes of pipe al different places including earthwork in excavation, opening of joint, dewatering of the trenches, making lead caulked joint & back filling the trenches etc. all complete work (As per sub Est. no.- 38)
40mm dia
| (i) without road cutting | [12 empty] | 1 | Nos. | 820 | 820
| (ii) with Pucca road cutting | [12 empty] | 1 | Nos. | 2006.7339 | 2006.7339
50mm dia
| (i) without road cutting | [12 empty] | 1 | Nos. | 890 | 890
| (ii) with Pucca road cutting | [12 empty] | 1 | Nos. | 2076.7339 | 2076.7339
65mm dia
| (i) without road cutting | [12 empty] | 1 | Nos. | 1180 | 1180
| (ii) with Pucca road cutting | [12 empty] | 1 | Nos. | 2366.7339 | 2366.7339
80mm dia
| (i) without road cutting | [12 empty] | 1 | Nos. | 1250 | 1250
| (ii) with Pucca road cutting | [12 empty] | 1 | Nos. | 2436.7339 | 2436.7339
43 | Repairing of 63/25 kva transformer inclusing LT pannel rapair in pump house Including Conductor,fuse relay,Timer as required,ST- CTBT pannel repair,Transformer Oil ( 630Ltr) Make-Servo etc all complete as per direction of engineer in charge. | [12 empty] | 1 | Nos. | 12000 | 12000
44 | Providing all labours, materials and cleaning of RCC water VAT from inside and doing chlorination etc. all complete work as per specification & direction of E/I. (As per sub Est. no.- 39) | [12 empty] | 1 | Nos. | 1053.6 | 1053.6
45 | Construction of 200 mm x 150 mm x 125 m deep T/W etc. with UPVC Pipe all complete and as per direction of E/I. (as per sub-estimate no.40). | [12 empty] | 1 | Nos. | 361106 | 361106
46 | Construction of 200 mm x 150 mm x 125 m deep T/W etc. with MS Pipe all complete and as per direction of E/I. (as per sub-estimate no.41). | [12 empty] | 1 | Nos. | 474807 | 474807
47 | Construction of 300 mm x 200 mm x 125 m deep T/W etc. with MS Pipe all complete and as per direction of E/I. (as per sub-estimate no.42). | [12 empty] | 1 | Nos. | 727318.15 | 727318.15
48 | Construction of 450 mm x 300 mm x 125 m deep T/W etc. with MS Pipe all complete and as per direction of E/I. (as per sub-estimate no.43). | [12 empty] | 1 | Nos. | 1390348 | 1390348
| Painting of 10000 Gallon Water Tower. (as per sub-estimate no.44). | [12 empty] | 1 | Nos. | 164266 | 164266
| Painting of 20000 Gallon Water Tower. (as per sub-estimate no.45). | [12 empty] | 1 | Nos. | 179058 | 179058
| Painting of 40000 Gallon Water Tower. (as per sub-estimate no.46). | [12 empty] | 1 | Nos. | 243020 | 243020
| Painting of 50000 Gallon Water Tower (as per sub-estimate no.47). | [12 empty] | 1 | Nos. | 312122 | 312122
49 | Provision of pump operator | [12 empty] | 1 | Nos. | 4000 | 4000
50 | Payment of electricity bills | [12 empty] | As per actual electricity bills.

## BoQ_2
Bill of Quantity 2 (Variable Cost)
1 | WATER SUPPLY: DUCTILE IRON (DI) SPECIALS
1.1 | Providing Ductile Iron Push on special confirming to IS 9523:2000
1.1.1 | 100mm | diameter | 11.25⁰ | Each | 1366
1.1.2 | 100mm | diameter | 22.50⁰ | Each | 1464
1.1.3 | 100mm | diameter | 45⁰ | Each | 2064
1.1.4 | 100mm | diameter | 90⁰ | Each | 1817
1.1.5 | 150mm | diameter | 11.25⁰ | Each | 2148
1.1.6 | 150mm | diameter | 22.50⁰ | Each | 2207
1.1.7 | 150mm | diameter | 45⁰ | Each | 2480
1.1.8 | 150mm | diameter | 90⁰ | Each | 3145
1.1.9 | 200mm | diameter | 11.25⁰ | Each | 3232
1.1.10 | 200mm | diameter | 22.50⁰ | Each | 3396
1.1.11 | 200mm | diameter | 45⁰ | Each | 4172
1.1.12 | 200mm | diameter | 90⁰ | Each | 5369
1.1.13 | 250mm | diameter | 11.25⁰ | Each | 4235
1.1.14 | 250mm | diameter | 22.50⁰ | Each | 4622
1.1.15 | 250mm | diameter | 45⁰ | Each | 5706
1.1.16 | 250mm | diameter | 90⁰ | Each | 7465
1.1.17 | 300mm | diameter | 11.25⁰ | Each | 5932
1.1.18 | 300mm | diameter | 22.50⁰ | Each | 7077
1.1.19 | 300mm | diameter | 45⁰ | Each | 8673
1.1.20 | 300mm | diameter | 90⁰ | Each | 11217
1.1.21 | 350mm | diameter | 11.25⁰ | Each | 7801
1.1.22 | 350mm | diameter | 22.50⁰ | Each | 9197
1.1.23 | 350mm | diameter | 45⁰ | Each | 11701
1.1.24 | 350mm | diameter | 90⁰ | Each | 16627
1.1.25 | 400mm | diameter | 11.25⁰ | Each | 11195
1.1.26 | 400mm | diameter | 22.50⁰ | Each | 12825
1.2 | Providing Ductile Iron(DI) push on specials confirming to IS 9523:2000
1.2.1 | 400mm | diameter | 45⁰ | Each | 16224
1.2.2 | 400mm | diameter | 90⁰ | Each | 22716
1.2.3 | 450mm | diameter | 11.25⁰ | Each | 13998
1.2.4 | 450mm | diameter | 22.50⁰ | Each | 15967
1.2.5 | 450mm | diameter | 45⁰ | Each | 20976
1.2.6 | 450mm | diameter | 90⁰ | Each | 28788
1.2.7 | 500mm | diameter | 11.25⁰ | Each | 16939
1.2.8 | 500mm | diameter | 22.50⁰ | Each | 20568
1.2.9 | 500mm | diameter | 45⁰ | Each | 28165
1.2.10 | 500mm | diameter | 90⁰ | Each | 39127
1.2.11 | 600mm | diameter | 11.25⁰ | Each | 25143
1.2.12 | 600mm | diameter | 22.50⁰ | Each | 31833
1.2.13 | 600mm | diameter | 45⁰ | Each | 41729
1.2.14 | 600mm | diameter | 90⁰ | Each | 60864
1.3 | Providing Ductile Iron push on specials confirming to IS 9523:2000 socketed DI equal tees
1.3.1 | 100mm | 100mm | 100mm | Each | 2499
1.3.2 | 150mm | 150mm | 150mm | Each | 3946
1.3.3 | 200mm | 200mm | 200mm | Each | 6423
1.3.4 | 250mm | 250mm | 250mm | Each | 6809
1.3.5 | 300mm | 300mm | 300mm | Each | 13825
1.3.6 | 450mm | 450mm | 450mm | Each | 31634
1.3.7 | 500mm | 500mm | 500mm | Each | 40497
1.3.8 | 600mm | 600mm | 600mm | Each | 57855
1.4 | Providing Ductile Iron push on specials confirming to IS 9523:2000 double socketed with flanged branch DI unequal Tees
1.4.1 | 150mm | 150mm | 100mm | Each | 2728
1.4.2 | 200mm | 200mm | 100mm | Each | 3836
1.4.3 | 250mm | 250mm | 100mm | Each | 5010
1.4.4 | 300mm | 300mm | 100mm | Each | 6528
1.4.5 | 350mm | 350mm | 100mm | Each | 10768
1.4.6 | 400mm | 400mm | 100mm | Each | 9436
1.4.7 | 450mm | 450mm | 100mm | Each | 13841
1.4.8 | 500mm | 500mm | 100mm | Each | 17346
1.4.9 | 600mm | 600mm | 150mm | Each | 21320
1.5 | Providing Ductile Iron push on specials confirming to IS 9523:2000 all socketed DI unequal Tees
1.5.1 | 100mm | X | 80mm | Each | 2413
1.5.2 | 150mm | X | 80mm | Each | 3521
1.5.3 | 150mm | X | 100mm | Each | 3417
1.5.4 | 200mm | X | 80mm | Each | 4804
1.5.5 | 200mm | X | 100mm | Each | 4867
1.5.6 | 200mm | X | 150mm | Each | 5585
1.5.7 | 250mm | X | 80mm | Each | 6299
1.5.8 | 250mm | X | 100mm | Each | 6258
1.5.9 | 250mm | X | 150mm | Each | 7445
1.5.10 | 250mm | X | 200mm | Each | 7978
1.5.11 | 300mm | X | 100mm | Each | 6874
1.5.12 | 300mm | X | 150mm | Each | 10085
1.5.13 | 300mm | X | 200mm | Each | 10902
1.5.14 | 300mm | X | 250mm | Each | 12088
1.5.15 | 350mm | X | 100mm | Each | 9996
1.5.16 | 350mm | X | 150mm | Each | 11729
1.5.17 | 350mm | X | 200mm | Each | 13716
1.5.18 | 350mm | X | 250mm | Each | 16159
1.6 | Providing Ductile Iron push on specials confirming to IS 9523:2000 all socketed DI reducers/tapers
1.6.1 | 100 | 80 | mm | Each | 1347
1.6.2 | 150 | 80 | mm | Each | 2217
1.6.3 | 150 | 100 | mm | Each | 2368
1.6.4 | 200 | 100 | mm | Each | 3416
1.6.5 | 200 | 150 | mm | Each | 3252
1.6.6 | 250 | 100 | mm | Each | 4684
1.6.7 | 250 | 150 | mm | Each | 4786
1.6.8 | 250 | 200 | mm | Each | 4356
1.6.9 | 300 | 100 | mm | Each | 6913
1.6.10 | 300 | 150 | mm | Each | 6913
1.6.11 | 300 | 200 | mm | Each | 6738
1.6.12 | 300 | 250 | mm | Each | 6347
1.6.13 | 350 | 150 | mm | Each | 9753
1.6.14 | 350 | 200 | mm | Each | 9075
1.6.15 | 350 | 250 | mm | Each | 8476
1.6.16 | 350 | 300 | mm | Each | 8023
1.7 | Providing Ductile Iron push on specials confirming to IS 9523:2000 all DI flanged socketed, DI flanged spigot, MS end plates
1.7.1 | D.I. flanged socketed
1.7.2 | D.I. flanged socketed | 100 | mm | Each | 1543
1.7.3 | D.I. flanged socketed | 150 | mm | Each | 2499
1.7.4 | D.I. flanged socketed | 200 | mm | Each | 3374
1.7.5 | D.I. flanged socketed | 250 | mm | Each | 4978
1.7.6 | D.I. flanged socketed | 300 | mm | Each | 6179
1.7.7 | D.I. flanged socketed | 350 | mm | Each | 8882
1.7.8 | D.I. flanged socketed | 400 | mm | Each | 10778
1.8 | Providing Ductile Iron push on specials confirming to IS 9523:2000 all DI flanged MJ collar
1.8.1 | 100 | mm |  | Each | 1231
1.8.2 | 150 | mm |  | Each | 1756
1.8.3 | 200 | mm |  | Each | 3171
1.8.4 | 250 | mm |  | Each | 5788
1.8.5 | 300 | mm |  | Each | 8449
1.8.6 | 350 | mm |  | Each | 7064
1.8.7 | 400 | mm |  | Each | 8498
2 | Water supply works
2.1 | Removing the GI pipes, cleaning, washing and using at spot or conveying from work site to office/store with all lead and lift i/c removal of all items such as collars, elbows, tees, bends etc,
2.1.1 | 15mm | to | 25mm | m | 26
2.1.2 | 32mm | to | 80mm | m | 48
2.1.3 | 100mm |  |  | m | 62
2.2 | Labour charges for laying and jointing GI pipes with earthwork i/c collars, elbows, tees, bends etc. with cuts and threads, white lead paint, conveying the material from store to work site and returning the surplus at store
2.2.1 | 15mm | dia. | GI | m | 10
2.2.2 | 20mm | dia. | GI | m | 13
2.2.3 | 25mm | dia. | GI | m | 19
2.2.4 | 40mm | dia. | GI | m | 24
2.2.5 | 50mm | dia. | GI | m | 32
2.2.6 | 65mm | dia. | GI | m | 32
2.2.7 | 80mm | dia. | GI | m | 32
2.2.8 | 100mm | dia. | GI | m | 53
2.3 | Cutting charges for CI/DI pipes laid in the ground with necessary tools
2.3.1 | 100mm | dia | pipes | Each | 75
2.3.2 | 125mm | dia | pipes | Each | 79
2.3.3 | 150mm | dia | pipes | Each | 83
2.3.4 | 175mm | dia | pipes | Each | 92
2.3.5 | 200mm | dia | pipes | Each | 117
2.3.6 | 225mm | dia | pipes | Each | 125
2.3.7 | 250mm | dia | pipes | Each | 167
2.3.8 | 300mm | dia | pipes | Each | 208
2.3.9 | 375mm | dia | pipes | Each | 229
2.3.10 | 400mm | dia | pipes | Each | 250
2.4 | Making cemenr mortar (1:1) and hemp yarn joint for CI pipes i/c cost of all materials viz. cement, sand, hemp, curing for 10 days complete
2.4.1 | 80 | mm | dia. |  | 97
2.4.2 | 100 | mm | dia. |  | 137
2.4.3 | 150 | mm | dia. |  | 169
2.4.4 | 200 | mm | dia. |  | 228
2.4.5 | 225 | mm | dia. |  | 255
2.4.6 | 250 | mm | dia. |  | 266
2.4.7 | 300 | mm | dia. |  | 319
2.4.8 | 350 | mm | dia. |  | 424
2.4.9 | 375 | mm | dia. |  | 458
2.4.10 | 400 | mm | dia. |  | 526
2.5 | Removing CI/DI valves and its tail piece from the pipeline, cleaning, washing, painting and returning the same at store
2.5.1 | 50mm | dia. |  | Each | 148
2.5.2 | 80mm | dia. |  | Each | 250
2.5.3 | 100mm | dia. |  | Each | 265
2.5.4 | 125mm | dia. |  | Each | 267
2.5.5 | 150mm | dia. |  | Each | 339
2.5.6 | 175mm | dia. |  | Each | 353
2.5.7 | 200mm | dia. |  | Each | 473
2.5.8 | 225mm | dia. |  | Each | 491
2.5.9 | 250mm | dia. |  | Each | 691
2.5.10 | 300mm | dia. |  | Each | 819
2.5.11 | 375mm | dia. |  | Each | 828
2.5.12 | 400mm | dia. |  | Each | 1166
2.6 | Removing and cleaning CI/DI pipes and specials i/c jointing materials, washing (excluding valves)
2.6.1 | 80mm | dia. |  | m | 67
2.6.2 | 100mm | dia. |  | m | 81
2.6.3 | 150mm | dia. |  | m | 98
2.6.4 | 200mm | dia. |  | m | 109
2.6.5 | 250mm | dia. |  | m | 126
2.6.6 | 300mm | dia. |  | m | 155
2.6.7 | 350mm | dia. |  | m | 178
2.6.8 | 400mm | dia. |  | m | 202
2.7 | Conveying CI/DI pipes and specials through transportation vehicles
2.7.1 | upto 5km i/c loading and unloading |  |  | qnt | 150
2.7.2 | upto 5km to 10 km excluding loading and unloading |  |  | qnt | 26
2.7.3 | beyond 10km excluding loading and unloading |  |  | qnt | 16
2.8 | Fixing DI/CI specials of mechanical jointing of different sizes after setting into the pipeline i/c cleaning, inserting rubber gasket, tightening with bolts & nuts i/c hire charges for T&P, appurtenances and lifting equipments
2.17.1 | 100mm to 200mm dia. |  | dia. | Each | 46
2.17.2 | 250mm to 400mm dia. |  | dia. | Each | 76
2.9 | Providing and fixing DI Resilient seated soft sealing SLUICE VALVE of variouis dia. with body bonnet of Ductile Iron (DI) conforming ti IS-1865 with the latest amendments and of grade GGG 40/50, shaft of stainless steel, wedge fully rubber lined with EDPM seals of NBR and the valves should be vacum tight and 100% leak proof with face to face dimensions as per IS 14846-2000 with the latest amendments only. The stem sealing should be with toroidal sealing rings (minimum 2 " O " rings). Body and bonnet should be coated with Electrostatically applied Epoxy Powder Coating with minimum coating thickness of 250 micron both inside and outside. The rate is inclusive of cost of valves, T.P set, galvanized bolts & nuts and rubber insertions etc. but excluding earth work. For PN-10: (Note: TP set should be considered only for DI pipes estimate. For MS pipes estimates, TP sets cost of corresponding dia shall be deducted from the SR rates of valves and provision for corresponding dia MS flanges should be made in the estimate.) etc. complete
2.9.1 | For sluice Valve of 50mm |  |  | Each | 5535
2.9.2 | For sluice Valve of 80mm |  |  | Each | 10393
2.9.3 | For sluice Valve of 100mm |  |  | Each | 10884
2.9.4 | For sluice Valve of 150mm |  |  | Each | 17490
2.9.5 | For sluice Valve of 200mm |  |  | Each | 28709
2.9.6 | For sluice Valve of 250mm |  |  | Each | 46491
2.9.7 | For sluice Valve of 300mm |  |  | Each | 60325
2.9.8 | For sluice Valve of 350mm |  |  | Each | 93233
2.9.9 | For sluice Valve of 400mm |  |  | Each | 125367
2.1 | Providing and fixing Wafer type single flange Butterfly valve conforming to relevant IS 13099/9991 EN GGG40/50 with latest amendments as detailed below of the following diameter and types with TP set and conveying to work site, loading and unloading, stacking etc. with all lead and lift. The rate is inclusive of the cost of valve, TP set, rubber insertion, bolts and nuts and excluding earth work excavation.For PN 10.0 (Note: TP set should be considered only for DI pipes estimate. For MS pipes estimates, TP sets cost of corresponding dia shall be deducted from the SR rates of valves and provision for corresponding dia MS flanges should be made in the estimate.
2.10.1 | For sluice Valve of 100mm |  |  | Each | 5849
2.10.2 | For sluice Valve of 150mm |  |  | Each | 12553
2.10.3 | For sluice Valve of 200mm |  |  | Each | 13971
2.10.4 | For sluice Valve of 250mm |  |  | Each | 15374
2.10.5 | For sluice Valve of 300mm |  |  | Each | 17346
2.10.6 | For sluice Valve of 350mm |  |  | Each | 23477
2.10.7 | For sluice Valve of 400mm |  |  | Each | 33092
2.11 | Providing and fixing of Double Flanged Resilient seated short body Butterfly valves of various dis. As per IS 13095/en 593 with integral DI seat face with approved soft sealing with body and disc of Ductile Iron (DI) of grade GGG-40/50, Body seat & Seal retaining ring of SS 304/CF8, Shaft of stainless steel AISI 410/420/431, Bronze shaft bearing, periferal disk, seal end "o" rings of EPDM, double eccentric disk. Body and disk should be coated with electrostatcially applied epoxy powder coating with a coating thickness of 250 micron both inside and out side. The rate is inclusive of cost of valve, TP set, galvanised bolts and nuts and rubber insertions. For PN 10.0 (All the drilled holes in the body shall be of through holes, no tapped holes will be allowed.) (Note: TP set should be considered only for DI pipes estimate. For MS pipes estimates, TP sets cost of corresponding dia shall be deducted from the SR rates of valves and provision for corresponding dia MS flanges should be made in the estimate.) etc. complete
2.11.1 | For Valve of PN 10.0 and 700mm |  |  | Each | 184739
2.11.2 | For Valve of PN 10.0 and 750mm |  |  | Each | 239773
2.11.3 | For Valve of PN 10.0 and 800mm |  |  | Each | 265385
2.11.4 | For Valve of PN 10.0 and 900mm |  |  | Each | 313821
2.11.5 | For Valve of PN 10.0 and 1000mm |  |  | Each | 407895
2.12 | Providing & Fixing sluice valves/ Butterfly Valves (labour charges only) conforming to relevant ISS with latest amendments as detailed below for the following diameter and types with two Each of MJ collars, two flanged spigots, conveying to work site, loading, unloading, stacking with appurtenances. with all lead and lifts, aligning, fixing and testing with appurtenances. etc. complete.
2.1.2.1 | For sluice valve with accessories - 50mm dia. |  |  | Each | 341
2.1.2.2 | For sluice valve with accessories - 80mm dia. |  |  | Each | 381
2.1.2.3 | For sluice valve with accessories - 100mm dia. |  |  | Each | 463
2.1.2.4 | For sluice valve with accessories - 150mm dia. |  |  | Each | 524
2.1.2.5 | For sluice valve with accessories - 200mm dia. |  |  | Each | 769
2.1.2.6 | For sluice valve with accessories - 250mm dia. |  |  | Each | 1167
2.1.2.7 | For sluice valve with accessories - 300mm dia. |  |  | Each | 1262
2.13 | Providing and fixing DI MJ specials such as branches and bends suitable for DI K7 and K9 pipes and CI LA class pipes, as per IS 13382 with latest amendments with complete accessories and fixing at site excluding earth work but including loading, unloading, freight charges etc. complete for:
2.13.1 | DI MJ specials - Branch 100 x 100mm |  |  | Each | 1701
2.13.2 | DI MJ specials - Branch 150 x 150mm |  |  | Each | 2673
2.38.3 | DI MJ specials - Branch 150 x 100mm |  |  | Each | 2322
2.38.4 | DI MJ specials - Bend 100 x 90 degree mm |  |  | Each | 1203
2.38.5 | DI MJ specials - Bend 100 x 45 degree |  |  | Each | 1174
2.38.6 | DI MJ specials - Bend 150 x 90 degree |  |  | Each | 2322
2.38.7 | DI MJ specials - collar 100mm dia. |  |  | Each | 2287
2.38.8 | DI MJ specials - collar 150mm dia. |  |  | Each | 4102
2.14 | Providing, fabricating and fixing at site various diameter MS MJ ends with dummy plates (END CAPS) to suit CI / DI spigots end as per the sketch. The cost is inclusive of all materials, i.e, rubber 'O' rings, flanges, bolts and nuts, dummy plates, consumables, hire charges, tools and welding equipments, lead and lifts, etc. complete as per the instructions of Engineer in charge.
2.14.1 | For CI / DI pipes of 100mm dia. |  |  | Each | 1158
2.14.2 | For CI / DI pipes of 150mm dia. |  |  | Each | 1609
2.14.3 | For CI / DI pipes of 200mm dia. |  |  | Each | 2226
2.14.4 | For CI / DI pipes of 250mm dia. |  |  | Each | 3213
2.14.5 | For CI / DI pipes of 300mm dia. |  |  | Each | 3230
2.14.6 | For CI / DI pipes of 400mm dia. |  |  | Each | 5077
2.15 | Providing and fixing of Extension spindle rods,PN 10 /16 suitable for Gate valve of following dia for open and closing application, Extension Spindle lengths shall be available on required sizes as per site conditions, spindle shall be of fixed type, suitable size of MS Square bar epoxy coated, bottom adaptor & Spindle cap (epoxy coated /galvanised) ductile iron Gr40. Protection tube of PVC, Top and Bottom cover / Bottom Connector shall be made by PVC, Bolt shall be made by Zinc coated steel 8.8 Split pin shall be made by Electro galvanized, this set up should help to have a buried application of Gate Valves etc. complete as per the directions of the Engineer-in-Charge.
2.15.1 | 50 - 150mm dia |  |  | m | 4762
2.15.2 | 200 - 450mm dia |  |  | m | 6449
2.16 | Providing & fixing RCC Pre-cast Cover Slab of size 0.8 m x 0.8 m x 0.15m of M25-Design mix concrete with 12 mm steel @ 120 mm c/c both ways, over Gate valve extension spindle with central opening along with lid for smooth operation with appurtenances., complete with all lead and lifts etc. complete |  |  | Each | 2386
2.17 | Conveying with all lead & lift and fixing C.I/D.I specials, bends, branches, tees,with appurtenances, all sizes and aligning.
2.17.1 | 50 mm dia to 100 mm dia |  |  | Each | 105
2.17.2 | 125 mm dia to 225 mm dia |  |  | Each | 131
2.17.3 | 250 mm dia to 600 mm dia |  |  | Each | 203
3 | Attendind leakages
3.1 | Providing & fixing CI/DI pipes socket leak repair MJ clamps for attending to leak joints in socket / spigot joints of CI / DI pipes with necessary earth work excavation including using of pneumatic breakers and JCB excavator wherever required and providing DI MJ leak repair clamp, including cost of all materials required for jointing comprising of DI MJ clamps and its accessories such as rubber gaskets made of SBR / EPDM on the socket face, making the socket / spigot joint water tight at the operating pressure, backfilling with available earth and consolidation and bailing out water wherever necessary etc. complete and In all types of road surfaces like Concrete, Asphalt roads etc, for:
3.1.1 | CI / DI pipes of 100mm dia. |  |  | Each | 2357
3.1.2 | CI / DI pipes of 150mm dia. |  |  | Each | 3563
3.1.3 | CI / DI pipes of 200mm dia. |  |  | Each | 4032
3.1.4 | CI / DI pipes of 250mm dia. |  |  | Each | 5255
3.1.5 | CI / DI pipes of 300mm dia. |  |  | Each | 6426
3.1.6 | CI / DI pipes of 400mm dia. |  |  | Each | 9059
3.1.7 | CI / DI pipes of 450mm dia. |  |  | Each | 11257
3.2 | Attending to leaking socket / spigots joints in CI / DI pipes in all types of road surfaces including concrete and asphalt roads, with necessary earth work excavation including using of pneumatic breakers and JCB excavator wherever required for jointing DI MJ clamp and its accessories such as rubber gaskets made of SBR / EPDM on the socket face, making the socket / spigot joint water tight at the operating pressure, backfilling with available earth and consolidation and bailing out water wherever necessary etc.complete.
3.2.1 | For CI / DI pipes of 100mm dia. |  |  | Each | 722
3.2.2 | For CI / DI pipes of 150mm dia. |  |  | Each | 814
3.2.3 | For CI / DI pipes of 200mm dia. |  |  | Each | 820
3.2.4 | For CI / DI pipes of 250mm dia. |  |  | Each | 954
3.2.5 | For CI / DI pipes of 300mm dia. |  |  | Each | 1254
3.2.6 | For CI / DI pipes of 400mm dia. |  |  | Each | 1289
3.2.7 | For CI / DI pipes of 450mm dia. |  |  | Each | 1406
3.3 | Cutting Asphalt /Concrete road surface using machine cutter for leakage pit with earth work excavation in all classifications of soil including all lead and lifts bailing out water with pumps including barricading, danger lighting etc., as per requirement and disposing of the excavated stuff as directed. After attending the leak, refilling the trench for 30 cm depth quarry dust above and around pipelines and balance with available earth in layers not exceeding 20 cms in depth, compacting Each deposited layer by ramming including watering and consolidation by mechanical means approved by Engineer Incharge. (Work to be carried out as per leak repair manual and the rate includes hire charges of dewatering Pump, tractor, Jeep with all kinds of Labour in a Complete manner). | m3 | 1157 | m2 | 1157
3.4 | Road Reinstatement of Asphalt /Concrete roads after leak attending with earth work excavation of compacted soil depositing on bank with all lead and lifts including danger lighting and barricading. Providing, laying, spreading and compacting graded stones aggregate as per wet mix macadam specifications. Applying tack coat on granular base such as WBM and WMM surface hot bitumen primer at 4 kg per 10 sqm, heating bitumen in layer to be laid with boiler fitted with spray set of 300 mm thickness. Above laid with bituminous concrete or M20 concrete premixed with bituminous binder at 5.4 to 5.6% of mix and filler, to achieve the desired compaction to give minimum of 45mm thickness compacted. The work shall be carried as per leak repair manual and includes all kinds of materials disposing off the excess excavated Earth with all lead and lifts by vehicle including loading, unloading, labour, HOM of machinery etc. in a complete manner. |  |  | m2 | 1690
4 | DI Pipes
4.1 | Providing and laying Ductile Iron pipes of class conforming to IS 8329:2000 with latest amendments, conveying to work site, rolling and lowering into trenches, laying true to line, level and perfect linking at joints, testing and commissioning, including loading and unloading at both destinations, cutting of pipes wherever necessary, jointing with DI specials (excluding cost of specials) and rubber gaskets, cleaning the socket and spigot end with soap solution, applying soft soap to the socket and spigot ends before insertion of rubber gaskets, jacking and fixing in perfect conditions etc. The cost to include soap solution, soft soap, waste etc. and giving necessary hydraulic test to the required pressure as per ISS with all lead and lifts and cost of all jointing materials. (The contractor will make his own arrangements for water for testing. Earth work excavation in trenches to be measured and paid for seperately) Note: In sewerage projects for internal cement mortal lining ( CML ) of DI pipes, if High Alumina Cement ( HAC ) as recommended in Annexure B clause 16.3 of IS8329:2000 is considered in place of Slag or Sulphate Resistance Cement ( SRC ), the cost of pipes may be increased by 5-6% from the prices listed. For DI K7 pipes:
4.1.1 | 100mm dia pipe |  |  | m | 1460
4.1.2 | 150mm dia pipe |  |  | m | 2016
4.1.3 | 200mm dia pipe |  |  | m | 2576
4.1.4 | 250mm dia pipe |  |  | m | 3140
4.1.5 | 300mm dia pipe |  |  | m | 3968
4.1.6 | 350mm dia pipe |  |  | m | 4999
4.1.7 | 400mm dia pipe |  |  | m | 5976
4.2 | Labour charges for laying & jointing of DI pipes of all classes rolling and lowering into trenches, laying true to line, level and perfect linking at joints and commissioning, including loading and unloading at both destinations and cuts of pipes wherever necessary including jointing of DI pipes and specials (excluding cost of pipes,rubber gasket and specials) with rubber gaskets including cleaning the sockets and spigot ends with saop solutions and applying soft soap to the spigot and socket end before insertion of rubber gaskets, jointing and fixing in perfect conditions including the cost of soap solution, soft soap, waste etc. and giving necessary hydraulic test to the required pressure as per ISS etc. with all leads and lifts (Earth work excavation in trenches,conveying of materials from stores to be measured and paid for separately) (Contractor will make his own arrangements for procuring water for testing) etc. complete for:
4.2.1 | 100mm dia pipe |  |  | m | 72
4.2.2 | 150mm dia pipe |  |  | m | 103
4.2.3 | 200mm dia pipe |  |  | m | 150
4.2.4 | 250mm dia pipe |  |  | m | 261
4.2.5 | 300mm dia pipe |  |  | m | 311
4.2.6 | 350mm dia pipe |  |  | m | 339
4.2.7 | 400mm dia pipe |  |  | m | 378
4.5 | Labour charges for making flanged joints including cost of jointing materials comprising of rubber insertion, galvanised bolts and nuts including giving hydraulic test to the required pressure as per ISS with all lead & lift (contractor will make his own arrangement for procuring water for testing) etc. complete
4.5.1 | Pipes and specials of dia 50mm. |  |  | Each | 113
4.5.2 | Pipes and specials of dia 80mm. |  |  | Each | 124
4.5.3 | Pipes and specials of dia 100mm. |  |  | Each | 208
4.5.4 | Pipes and specials of dia 150mm. |  |  | Each | 310
4.5.5 | Pipes and specials of dia 200mm. |  |  | Each | 334
4.5.6 | Pipes and specials of dia 250mm. |  |  | Each | 498
4.5.7 | Pipes and specials of dia 300mm. |  |  | Each | 520
4.5.8 | Pipes and specials of dia 350mm. |  |  | Each | 707
4.5.9 | Pipes and specials of dia 400mm. |  |  | Each | 1033
4.6 | Providing RUBBER JOINTING for CI / DI pipes with rubber gaskets including cleaning the socket and spigot ends with soap solution and applying soft soap to the spigot and socket ends before insertion of rubber gaskets, jacking and fixing in perfect conditions including cost of soap solution, soft soap, waste etc with all lead and lift including cost of jointing materials etc.complete for:
4.6.1 | 100mm |  |  | Each | 90
4.6.2 | 150mm |  |  | Each | 123
4.6.3 | 200mm |  |  | Each | 132
4.6.4 | 250mm |  |  | Each | 165
4.6.5 | 300mm |  |  | Each | 193
4.6.6 | 350mm |  |  | Each | 220
4.6.7 | 400mm |  |  | Each | 248
5 | RCC Overhead tanks
7.1 | Providing and fixing MS ladder between landings, 45 cms wide using angle iron of specified sizes, 20mm MS bars at 25 cms. centre to centre, with necessary supports of same angle iron etc. as directed, including hand railing on both sides with 25mm dia. GI pipes with angle iron props at 2 mtrs. intervals and 0.5M heigh, including fixing in ground with CC 1:2:4 and two coats of anticorrosive bituminous paint etc. with all lead and lifts etc. complete with:
7.1.1 | MS angle of 65 x 65 x 8mm |  |  | m | 4377
7.1.2 | MS angle of 65 x 65 x 10mm |  |  | m | 4801
7.6 | Providing, Laying and Jointing Cast Iron (CI) double flanged pipes true to line / hoisting of DI flanged pipe in position and aligning to correct plumb, including cost of jointing materials, conveying to work spot with all lead and lifts etc.complete.
7.6.1 | For double flanged CI pipes of 80mm dia. |  |  | m | 2245
7.6.2 | For double flanged CI pipes of 100mm dia. |  |  | m | 3010
7.6.3 | For double flanged CI pipes of 150mm dia. |  |  | m | 4808
7.6.4 | For double flanged CI pipes of 200mm dia. |  |  | m | 6592
7.6.5 | For double flanged CI pipes of 250mm dia. |  |  | m | 9272
7.7 | Providing and fixing lightening arrestor with aluminium strip 25mm x 3mm size including finial and grounding, aluminium strip to be embeded in one of the columns in and independent GI conduit of 40mm dia. pipe suitably jointed by collars with all specials with all lead and lifts etc. complete for:
7.7.1 | For Over Head Tanks upto 6 M staging |  |  | Each | 8088
7.7.2 | For Over Head Tanks upto 9 M staging |  |  | Each | 9387
7.7.3 | For Over Head Tanks upto 12M staging |  |  | Each | 11530
7.7.4 | For Over Head Tanks above 12M staging |  |  | Each | 13889
7.9 | Providing, of DI flanged pipe conforming to IS 8329 : 2000 with latest amendments with Cement Mortar Lining (CML) with Portland Slag Cement as per IS 455:1989 and Metallic Zinc Coating as per annexure A of IS 8329 with finishing layer of Bituminous Coating as per Annexure C of IS 8329 and Flanges: Metallic zinc rich epoxy paint & Bituminous Coating, laying true to line and hoisting in position and aligning to correct plumb including cost of jointing material, conveying to work spot with all lead and lifts etc., complete. For PN 10.0
7.9.1 | 100mm |  |  | m | 4671
7.9.2 | 150mm |  |  | m | 6635
7.9.3 | 200mm |  |  | m | 8978
7.9.4 | 250mm |  |  | m | 12996
7.9.5 | 300mm |  |  | m | 16360
7.11 | Providing Ductile Iron Push on special confirming to IS 9523:2000 - All Double Socket Duck Foot DI Bends:
7.11.1 | 80 X 90 |  |  | Each | 2365
7.11.2 | 100 X 90 |  |  | Each | 3063
7.11.3 | 150 X 90 |  |  | Each | 5162
7.11.4 | 200 X 90 |  |  | Each | 8750
7.11.5 | 250 X 90 |  |  | Each | 13770
7.11.6 | 300 X 90; |  |  | Each | 18320
8.2 | Providing and applying integral crystalline slurry of hydrophilic in nature for waterproofing treatment to RCC structures like floor and walls of reservoirs, sewe, effluent and water treatment plants, over head tanks, etc. prepared by mixing in the ratio of 5:2 (5 parts integral crystalline slurry 2 parts water) for horizontal and vertical surfaces and applying the same from negative (internal) side with the help of synthetic fibre brush. The material shall meet the requirements as specified in ACI - 212-3R-2010 ie. by reducing permeability of concrete by more than 90% compared with control concrete as per DIN 1048 and resistant to 16 Bar hydrostatic pressure on negative side. The crystalline slurry shall be capable of self healing of cracks upto a width of 0.50 mm. The work shall be carried out all complete as per specification and the direction of the Engineer in charge. The product performance shall carry guarantee for 10 years against any leakage. For horizontal and vertical surfaces in two coats @ 0.70 kg per sqm per coat |  |  | m2 | 433
6 | PE pipes
9.15 | Lowering and laying and fusion welding Jointing for HDPE Pipes Grade PE- 80 / PE-100 conforming to IS 4984-2016, of specified dia. including hydrualic testing and commissioning etc.(Contractor will make his own arrangements for procuring water for testing) for:
9.15.1 | 63mm dia |  |  | m | 64
9.15.2 | 75mm dia |  |  | m | 67
9.15.3 | 90mm dia |  |  | m | 71
9.15.4 | 110mm dia |  |  | m | 95
9.15.5 | 125mm dia |  |  | m | 107
7 | GI Pipes
11.1 | Providing, Laying and Fixing of GI pipes conforming to IS 1239:1990 with latest amendments complete with GI fittings (excluding the cost of fittings) with cuts and threads wherever necessary, including testing for water tightness, with all lead and commissioning. (contractor will make his own arrangements for procuring water for testing) For:Heavy Duty GI Pipe etc. complete.
11.2 | For Medium Duty GI pipe:
11.2.6 | Medium Duty GI pipe of 50mm dia |  |  | m | 584
11.2.7 | Medium Duty GI pipe of 65mm dia |  |  | m | 719
11.2.8 | Medium Duty GI pipe of 80mm dia |  |  | m | 891
11.2.9 | Medium Duty GI pipe of 100mm dia |  |  | m | 1245
11.3 | For Heavy Duty GI pipe:
11.3.6 | Heavy Duty GI pipe of 50mm dia |  |  | m | 679
11.3.7 | Heavy Duty GI pipe of 65mm dia |  |  | m | 834
11.3.8 | Heavy Duty GI pipe of 80mm dia |  |  | m | 1009
11.3.9 | Heavy Duty GI pipe of 100mm dia |  |  | m | 1412
11.4 | Providing and fixing GI union in existing GI pipe line, cutting and threading the pipe and making long screws including excavation, refilling the earth or cutting of wall and making good the same complete wherever required etc. complete for:
11.4.6 | 20.88.6: 50 mm nominal bore |  |  | Each | 660
11.4.7 | 20.88.7: 65 mm nominal bore |  |  | Each | 878
11.4.8 | 20.88.8: 80 mm nominal bore |  |  | Each | 1041
11.5 | Providing lead caulked joints to spun iron or CI pipes and specials with spun yarn and lead, including caulking and giving satisfactory hydraulic test corresponding to the required pressure etc. complete.for:
11.5.1 | Spun / CI / DI pipes 80MM |  |  | Each | 481
11.5.2 | Spun / CI / DI pipes 100MM |  |  | Each | 500
11.5.3 | Spun / CI / DI pipes 150MM |  |  | Each | 747
11.5.4 | Spun / CI / DI pipes 200MM |  |  | Each | 944
11.5.5 | Spun / CI / DI pipes 250MM |  |  | Each | 1210
11.5.6 | Spun / CI / DI pipes 300MM |  |  | Each | 1425
11.6 | Providing wrought mild steel (galvanized) GI collar confirming to IS 1239-II, 1991 with latest amendments if any.
11.6.6 | For 50 mm dia GI collar: |  |  | Each | 267
11.6.7 | For 65 mm dia GI collar: |  |  | Each | 312
11.6.8 | For 80 mm dia GI collar: |  |  | Each | 421
11.6.9 | For 100 mm dia GI collar: |  |  | Each | 505
11.6.10 | For 125 mm dia GI collar: |  |  | Each | 636
11.6.11 | For 150 mm dia GI collar: |  |  | Each | 695
11.7 | Supply and delivery at site wrought middle steel (galvanized) GI elbow confirming to IS 1239-II, 1991 with latest amendments if any for:
11.7.6 | For 50 mm dia GI elbow |  |  | Each | 267
11.7.7 | For 65 mm dia GI elbow |  |  | Each | 297
11.7.8 | For 80 mm dia GI elbow |  |  | Each | 417
11.7.9 | For 100 mm dia GI elbow |  |  | Each | 490
11.7.10 | For 125 mm dia GI elbow |  |  | Each | 578
11.7.11 | For 150 mm dia GI elbow |  |  | Each | 651
11.8 | Supply and delivery at site wrought middle steel (galvanized) GI bend confirming to IS 1239-II, 1991 with latest amendments if any.
11.8.6 | For 50 mm dia GI BEND |  |  | Each | 358
11.8.7 | For 65 mm dia GI BEND |  |  | Each | 404
11.8.8 | For 80 mm dia GI BEND |  |  | Each | 490
11.8.9 | For 100 mm dia GI BEND |  |  | Each | 600
11.8.10 | For 125 mm dia GI BEND |  |  | Each | 680
11.8.11 | For 150 mm dia GI BEND |  |  | Each | 724
11.9 | Supply and delivery at site wrought middle steel (galvanized) GI tee confirming to IS 1239-II, 1991 with latest amendments if any.
11.9.6 | For 50 mm dia GI TEE |  |  | Each | 297
11.9.7 | For 65 mm dia GI TEE |  |  | Each | 373
11.9.8 | For 80 mm dia GI TEE |  |  | Each | 434
11.9.9 | For 100 mm dia GI TEE |  |  | Each | 607
11.9.10 | For 125 mm dia GI TEE |  |  | Each | 775
11.9.11 | For 150 mm dia GI TEE |  |  | Each | 914
11.1 | Supply and delivery at site wrought middle steel (galvanized) GI socket confirming to IS 1239-II, 1991 with latest amendments if any.
11.10.6 | For 50 mm dia GI socket |  |  | Each | 297
11.10.7 | For 65 mm dia GI socket |  |  | Each | 373
11.10.8 | For 80 mm dia GI socket |  |  | Each | 454
11.10.9 | For 100 mm dia GI socket |  |  | Each | 563
11.10.10 | For 125 mm dia GI socket |  |  | Each | 614
11.10.11 | For 150 mm dia GI socket |  |  | Each | 731
11.11 | Supply and delivery at site wrought middle steel (galvanized) GI plugs confirming to IS 1239-II, 1991 with latest amendments if any.
11.11.6 | For 50 mm dia GI Plugs |  |  | Each | 199
11.11.7 | For 65 mm dia GI Plugs |  |  | Each | 237
11.11.8 | For 80 mm dia GI Plugs |  |  | Each | 256
11.11.9 | For 100 mm dia GI Plugs |  |  | Each | 358
11.11.10 | For 125 mm dia GI Plugs |  |  | Each | 432
11.11.11 | For 150 mm dia GI Plugs |  |  | Each | 490
11.12 | Supply and delivery at site wrought middle steel (galvanized) GI union confirming to IS 1239-II, 1991 with latest amendments if any.
11.12.6 | For 50 mm dia GI Union |  |  | Each | 267
11.12.7 | For 65 mm dia GI Union |  |  | Each | 351
11.12.8 | For 80 mm dia GI Union |  |  | Each | 578
11.12.9 | For 100 mm dia GI Union |  |  | Each | 622
11.12.10 | For 125 mm dia GI Union |  |  | Each | 666
11.12.11 | For 150 mm dia GI Union |  |  | Each | 783
11.2 | Lowering, Laying and Jointing GI pipes conforming to IS 1239:1990 with latest amendments complete with GI fittings (excluding the cost of fittings) with cuts and threads wherever necessary, including testing for water tightness, with all lead and commissioning. (contractor will make his own arrangements for procuring water for testing) for etc. complete.
11.20.6 | 50mm dia |  |  | m | 145
11.20.7 | 65mm dia |  |  | m | 163
11.20.8 | 80mm dia |  |  | m | 188
11.20.9 | 100mm dia |  |  | m | 216

## BoQ_3
Bill of Quantity 3 (Variable Cost)
13 SUBMERSIBLE PUMPSETS AND REPLACEMENT OF PARTS
13.1 | Rewinding of submersible pumpset with copper winding wires of appropriate guage, as per specifications and / or directions of the departmental officials, including all materials, labour, equipment and testing. for all types of submersible pumpsets etc.(with guarantee period not less than 6 months) for
13.1.1 | For all types of submersible pumpsets upto 3.0 H.P. | Each | 2710
13.1.2 | above 3 HP and upto 5.0 H.P. | Each | 2934
13.1.3 | above 5.0 HP and upto 5.5H.P. | Each | 3116
13.1.4 | above 5.5 HP and upto 6.0H.P. | Each | 3296
13.1.5 | above 6.0 HP and upto 6.5H.P. | Each | 3479
13.1.6 | above 6.5 HP and upto 7.0H.P. | Each | 3659
13.1.7 | above 7.0 HP and upto 7.5H.P. | Each | 3839
13.1.8 | above 7.5 HP and upto 8.0H.P. | Each | 4019
13.1.9 | above 8.0 HP and upto 8.5H.P. | Each | 4201
13.1.10 | above 8.5 HP and upto 9.0H.P. | Each | 4382
13.1.11 | above 9.0 HP and upto 9.5H.P. | Each | 4562
13.1.12 | above 9.5 HP and upto 10.0H.P. | Each | 4744
13.1.13 | above 10 HP and upto 11 H.P. | Each | 5157
13.1.14 | above 11 HP and upto 12 H.P. | Each | 5570
13.1.15 | above 12 HP and upto 13 H.P. | Each | 5983
13.1.16 | above 13 HP and upto 14 H.P. | Each | 6397
13.1.17 | above 14 HP and upto 15 H.P. | Each | 6811
13.1.18 | 15HP to 20 HP | Each | 8930
13.2 | Replace the components of submersible pump sets, requiring replacements decided by the departmental officials, with respective make of damaged ones, including all materials, labour, equipments and testing etc.(with gurantee of period not less than 1 year) for:
13.2.1 | The bowls of same type and make | Each | 1500
13.2.2 | The Intermediate piece (IP) with IP leaded bronze brush. | Each | 1050
13.2.3 | The Oil Seal. | Each | 350
13.2.4 | The Oil Seal.and steel bush | Each | 250
13.2.5 | The Guide Vane | Each | 700
13.2.6 | The Impeller (Shell moulded with aluminium and bronze.) | Each | 1500
13.2.7 | The discharge outlet (DO) bearing DO steel brush DO bearing. | Each | 2050
13.2.8 | The steel bearing bush (DO steel bush) | Each | 400
13.2.9 | The allen screw | Each | 1200
13.2.10 | The pump shaft made out of stainless steel counterless ground with key way (upto 8 stages). Extra for Each stage @ Rs.40/-. | Each | 1500
13.2.11 | The pump key (stainless steel) | Each | 650
13.2.12 | The pump coupling (stainless steel) | Each | 1500
13.2.13 | The Non Return Valve (NRV) assembly complete with rubber 'O' ring. | Each | 650
13.2.14 | The cable guard | Each | 350
13.2.15 | The strainer | Each | 450
13.2.16 | The brass filter | Each | 1050
13.2.17 | The Labour Charges for overhauling of the pump set. | Each | 900
13.3 | Replace the components of motor parts of submersible pump sets, items requiring replacements decided by the departmental officials, with respective make of damaged ones, including all materials, labour, equipments and testing etc and wtih guarantee/ warranty for one year for:
13.3.1 | The STATOR of motor upto 3 H.P | Each | 1500
13.3.2 | The STATOR of motor 3 to 4 H.P | Each | 2500
13.3.3 | The STATOR of motor 4 to 5 H.P | Each | 3500
13.3.4 | The ROTOR of motor upto 3.0 H.P | Each | 1200
13.3.5 | The ROTOR of motor 3 to 4 H.P | Each | 1500
13.3.6 | The ROTOR motor 4 to 5 H.P | Each | 2000
13.3.7 | The upper flange | Each | 650
13.3.8 | The lower flange | Each | 650
13.3.9 | upper/ lower housing | Each | 1200
13.3.10 | The Lock Ring | Each | 350
13.3.11 | The Carbon Housing | Each | 2000
13.3.12 | The Carbon Housing (Thrust bearing block assembly complete with segment bearing pad. | Each | 2200
13.3.13 | The Carbon Housing (Top carbond / ferrodo padding) | Each | 350
13.3.14 | The Stud and Nuts | Each | 200
13.3.15 | The Gun Metal bearing, centrifugally cast Aluminium Bronze bearing | Each | 850
bush
13.3.16 | The Circlips | Each | 200
13.3.17 | The Motor base with pin | Each | 500
13.3.18 | The Transportation of pumping machineries | Each | 1200
13.3.19 | The Re-errection charges of pumping machineries including overhauling | Each | 2000
and painting
13.3.20 | The lifting of submersible pumpset from well. | Each | 1500
13.3.21 | The Labour charges only for overhauling | Each | 3000
13.3.22 | Providing of Thermosetting Plastic i.e., Fibere Glass reinforced polyster sheet moulding compound(SMC) pump house with SMC door & canopy etc...,complete component as directed by the departmental officers. | Each | 12000
13.4 | Providing, Single Phase Submersible Pump Sets of 100mm dia (4 inch) suitable for bore well confirming to IS 8034-2000 specifications, to work site with testing of as per instructions of engineer incharge of work and latest amendments etc. complete.
13.4.1 | 0.50 HP/0.37kW - 5 STG(stage) | Each | 10170
13.4.2 | 0.50 HP/0.37kW - 7 STG(stage) | Each | 10855
13.5 | For 0.75 HP/0.55KW
13.5.1 | 5 STG | Each | 12280
13.5.2 | 6 STG | Each | 12630
13.5.3 | 7 STG | Each | 13113
13.5.4 | 10 STG | Each | 13373
13.5.5 | 13 STG | Each | 13918
13.6 | 1.00 HP/0.75KW
13.6.1 | 7 STG | Each | 13318
13.6.2 | 10 STG | Each | 13910
13.6.3 | 12 STG | Each | 14516
13.6.4 | 13 STG | Each | 15120
13.6.5 | 18 STG | Each | 15680
13.7 | 1.50 HP/1.1KW
13.7.1 | 7 STG | Each | 13910
13.7.2 | 10 STG | Each | 14187
13.7.3 | 12 STG | Each | 15418
13.7.4 | 14 STG | Each | 16119
13.7.5 | 15 STG | Each | 16940
13.7.6 | 18 STG | Each | 17546
13.7.7 | 20 STG | Each | 18218
13.7.8 | 26 STG | Each | 19410
13.8 | 2.00 HP/1.5KW
13.8.1 | 6 STG | Each | 16510
13.8.2 | 10 STG | Each | 16993
13.8.3 | 12 STG | Each | 17618
13.8.4 | 14 STG | Each | 17897
13.8.5 | 15 STG | Each | 18218
13.8.6 | 16 STG | Each | 18826
13.8.7 | 18 STG | Each | 19698
13.8.8 | 20 STG | Each | 19864
13.8.9 | 25 STG | Each | 20216
13.8.10 | 30 STG | Each | 20719
13.8.11 | 35 STG | Each | 21813
13.9 | 3.00 HP/2.2KW
13.9.1 | 9 STG | Each | 20113
13.9.2 | 15 STG | Each | 21530
13.9.3 | 20 STG | Each | 21996
13.9.4 | 21 STG | Each | 22478
13.9.5 | 23 STG | Each | 23860
13.9.6 | 30 STG | Each | 24530
13.9.7 | 35 STG | Each | 24816
13.9.8 | 40 STG | Each | 25773
13.9.9 | 50 STG | Each | 26775
13.1 | 5.00 HP/3.7KW
13.10.1 | 25 STG | Each | 26400
13.10.2 | 30 STG | Each | 27910
13.10.3 | 35 STG | Each | 28315
13.10.4 | 50 STG | Each | 29650
13.11 | Providing Submersible Pump Set of 150mm dia suitable for bore well and confirming to IS 8034-2000;3Phase, SS Bowl & Impeller with Low volt Motor as per specifications, to work site as per necessary ammendments and instructions of engineer incharge of work. For 3 HP etc. complete.
13.11.1 | 3.00 HP - 300 LPM @ 26 m = 5 STG Outlet Dia - 2.50" | Each | 23168
13.11.2 | 3.00 HP - 155 LPM @ 42 m = 7 STG Outlet Dia - 2.00" | Each | 24334
13.11.3 | 3.00 HP - 135 LPM @ 56 m = 8 STG Outlet Dia - 2.00" | Each | 25910
13.11.4 | 3.00 HP - 120 LPM @ 55 m = 9 STG Outlet Dia - 2.00" | Each | 26627
13.11.5 | 3.00 HP - 90 LPM @ 66 m = 10 STG Outlet Dia - 2.00" | Each | 28113
13.12 | For 4.00 HP
13.12.1 | 4.00 HP - 360 LPM @ 30 m = 6 STG Outlet Dia - 3.00" | Each | 22628
13.12.2 | 4.00 HP - 245 LPM @ 42 m = 8 STG Outlet Dia - 2.50" | Each | 23319
13.12.3 | 4.00 HP - 155 LPM @ 56 m = 9 STG Outlet Dia - 2.00" | Each | 24107
13.12.4 | 4.00 HP - 135 LPM @ 70 m = 5 STG Outlet Dia - 2.00" | Each | 24993
13.12.5 | 4.00 HP - 120 LPM @ 77 m = 11 STG Outlet Dia - 2.00" | Each | 25610
13.12.6 | 4.00 HP - 90 LPM @ 88 m = 12 STG Outlet Dia - 2.00" | Each | 26730
13.13 | For 5.00 HP
13.13.1 | 5.00 HP - 300 LPM @ 39 m = 5 STG Outlet Dia - 2.50" | Each | 26310
13.13.2 | 5.00 HP - 245 LPM @ 56 m = 8 STG Outlet Dia - 2.50" | Each | 27010
13.13.3 | 5.00 HP - 155 LPM @ 70 m = 10 STG Outlet Dia - 2.00" | Each | 27600
13.13.4 | 5.00 HP - 135 LPM @ 84 m = 12 STG Outlet Dia - 2.00" | Each | 28837
13.13.5 | 5.00 HP - 120 LPM @ 88 m = 14 STG Outlet Dia - 2.00" | Each | 30819
13.13.6 | 5.00 HP - 90 LPM @ 110 m = 15 STG Outlet Dia - 2.00" | Each | 32137
13.14 | For 6.50 HP
13.14.1 | 6.50 HP - 360 LPM @ 45 m = 5 STG Outlet Dia - 3.00" | Each | 26930
13.14.2 | 6.50 HP - 300 LPM @ 52 m = 6 STG Outlet Dia - 2.50" | Each | 27813
13.14.3 | 6.50 HP - 245 LPM @ 70 m = 8 STG Outlet Dia - 2.50" | Each | 29930
13.14.4 | 6.50 HP - 155 LPM @ 84 m = 10 STG Outlet Dia - 2.00" | Each | 30774
13.14.5 | 6.50 HP - 135 LPM @ 110 m = 12 STG Outlet Dia - 2.00" | Each | 32610
13.14.6 | 6.50 HP - 120 LPM @ 112 m = 14 STG Outlet Dia - 2.00" | Each | 34910
13.14.7 | 6.50 HP - 90 LPM @ 132 m = 15 STG Outlet Dia - 2.00" | Each | 36719
13.15 | For 7.50 HP
13.15.1 | 7.50 HP - 360 LPM @ 60 m = 5 STG Outlet Dia - 3.00" | Each | 28116
13.15.2 | 7.50 HP - 300 LPM @ 65 m = 6 STG Outlet Dia - 2.50" | Each | 30010
13.15.3 | 7.50 HP - 245 LPM @ 84 m = 8 STG Outlet Dia - 2.50" | Each | 32819
13.15.4 | 7.50 HP - 155 LPM @ 112 m = 10 STG Outlet Dia - 2.00" | Each | 34213
13.15.5 | 7.50 HP - 135 LPM @ 140 m = 12 STG Outlet Dia - 2.00" | Each | 36620
13.15.6 | 7.50 HP - 120 LPM @ 132 m = 14 STG Outlet Dia - 2.00" | Each | 38919
13.15.7 | 7.50 HP - 90 LPM @ 165 m = 16 STG Outlet Dia - 2.00" | Each | 40810
13.16 | For 10.00 HP
13.16.1 | 10.00 HP - 360 LPM @ 75 m = 5 STG Outlet Dia - 3.00" | Each | 31618
13.16.2 | 10.00 HP - 300 LPM @ 91 m = 6 STG Outlet Dia - 2.50" | Each | 34110
13.16.3 | 10.00 HP - 245 LPM @ 112 m = 8 STG Outlet Dia - 2.50" | Each | 37750
13.16.4 | 10.00 HP - 155 LPM @ 140 m = 10 STG Outlet Dia - 2.00" | Each | 40460
13.16.5 | 10.00 HP - 135 LPM @ 168 m = 12 STG Outlet Dia - 2.00" | Each | 43930
13.16.6 | 10.00 HP - 120 LPM @ 176 m = 16 STG Outlet Dia - 2.00" | Each | 47633
13.16.7 | 10.00 HP - 90 LPM @ 220 m = 20 STG Outlet Dia - 2.00" | Each | 54612
13.17 | For 12.50 HP
13.17.1 | 12.50 HP - 360 LPM @ 90 m = 6 STG Outlet Dia - 3.00" | Each | 35907
13.17.2 | 12.50 HP - 300 LPM @ 104 m = 8 STG Outlet Dia - 2.50" | Each | 39179
13.17.3 | 12.50 HP - 245 LPM @ 140 m = 10 STG Outlet Dia - 2.50" | Each | 45701
13.17.4 | 12.50 HP - 155 LPM @ 168 m = 12 STG Outlet Dia - 2.00" | Each | 49834
13.17.5 | 12.50 HP - 135 LPM @ 210 m = 15 STG Outlet Dia - 2.00" | Each | 55110
13.17.6 | 12.50 HP - 120 LPM @ 220 m = 20 STG Outlet Dia - 2.00" | Each | 59916
13.17.7 | 12.50 HP - 90 LPM @ 264 m = 24 STG Outlet Dia - 2.00" | Each | 64128
13.18 | For 15.00 HP
13.18.1 | 15.00 HP - 360 LPM @ 120 m = 8 STG Outlet Dia - 3.00" | Each | 45774
13.18.2 | 15.00 HP - 300 LPM @ 130 m = 10 STG Outlet Dia - 2.50" | Each | 50337
13.18.3 | 15.00 HP - 245 LPM @ 168 m = 12 STG Outlet Dia - 2.50" | Each | 55618
13.18.4 | 15.00 HP - 155 LPM @ 210 m = 15 STG Outlet Dia - 2.00" | Each | 61827
13.18.5 | 15.00 HP - 135 LPM @ 253 m = 19 STG Outlet Dia - 2.00" | Each | 66708
13.18.6 | 15.00 HP - 120 LPM @ 266 m = 23 STG Outlet Dia - 2.00" | Each | 69344
13.19 | For 17.50 HP
13.19.1 | 17.50 HP - 360 LPM @ 135 m = 9 STG Outlet Dia - 3.00" | Each | 54713
13.19.2 | 17.50 HP - 300 LPM @ 156 m = 12 STG Outlet Dia - 2.50" | Each | 58434
13.19.3 | 17.50 HP - 245 LPM @ 196 m = 14 STG Outlet Dia - 2.50" | Each | 64619
13.19.4 | 17.50 HP - 155 LPM @ 252 m = 18 STG Outlet Dia - 2.00" | Each | 69445
13.19.5 | 17.50 HP - 135 LPM @ 286 m = 22 STG Outlet Dia - 2.00" | Each | 73664
13.19.6 | 17.50 HP - 120 LPM @ 308 m = 26 STG Outlet Dia - 2.00" | Each | 77963
13.2 | For 20.00 HP
13.20.1 | 20.00 HP - 360 LPM @ 150 m = 10 STG Outlet Dia - 3.00" | Each | 63170
13.20.2 | 20.00 HP - 300 LPM @ 169 m = 13 STG Outlet Dia - 2.50" | Each | 68310
13.20.3 | 20.00 HP - 245 LPM @ 224 m = 16 STG Outlet Dia - 2.50" | Each | 73557
13.20.4 | 20.00 HP - 155 LPM @ 280 m = 20 STG Outlet Dia - 2.00" | Each | 78905
13.20.5 | 20.00 HP - 135 LPM @ 350 m = 25 STG Outlet Dia - 2.00" | Each | 81090
13.21 | For 25.00 HP
13.21.1 | 25.00 HP - 360 LPM @ 195 m = 13 STG Outlet Dia - 3.00" | Each | 58473
13.21.2 | 25.00 HP - 300 LPM @ 221 m = 17 STG Outlet Dia - 2.50" | Each | 64313
13.21.3 | 25.00 HP - 245 LPM @ 280 m = 20 STG Outlet Dia - 2.50" | Each | 69773
13.21.4 | 25.00 HP - 155 LPM @ 280 m = 20 STG Outlet Dia - 2.00" | Each | 75336
13.21.5 | 25.00 HP - 135 LPM @ 420 m = 30 STG Outlet Dia - 2.00" | Each | 82619
13.22 | Supply and delivery at site Brand new best make PVC insulated cable of Flat 3 core (sheathed) of nominal cross sectional area as per IS 694-1990 with ISI Mark and as per its latest amendments.
13.22.1 | 1x3x1.5 Sqm | m | 65
13.22.2 | 1x3x2.5 Sqm | m | 85
13.22.3 | 1x3x4 Sqm | m | 135
13.22.4 | 1x3x6 Sqm. | m | 185
13.22.5 | 1x3x10 Sqm | m | 280
13.23 | Supply and delivery at site of brand new best make pressure gauge bourdon type as per IS 778/1984 with ISI Mark and as per its latest amendments.
13.23.1 | Size 63 mm | Each | 416
13.23.2 | Size 80 mm | Each | 597
13.23.3 | Size 100 mm | Each | 654
13.24 | Supply and delivery at site of brand new best make gate valve as per IS 778/1984 with ISI Mark and as per its latest amendments
13.24.1 | Size 50 mm | Each | 1250
13.24.2 | Size 65 mm | Each | 1450
13.24.3 | Size 80 mm | Each | 1650
13.25 | Supply and delivery at site of brand new best make non-return valve as per IS 778/1984 with ISI Mark and as per its latest amendments
13.25.1 | Size 50 mm | Each | 1250
13.25.2 | Size 65 mm | Each | 1550
13.25.3 | Size 80 mm | Each | 1750
13.23 | Supply, installing,testing and commissioning COMMON control panel consisting of the following INCOMING:1 No set of Phase indicating lamps with SFU of suitable rating 1 No, Analog Ammeter, 1 No Analog Voltmeter 1ni with Phase selector switch, Isolating switch OUTGOING for Main Electrical Pump: 1 No. MCB 1 No. DOL of S/D Starter suitable for respective HP 1 No. Electrcal Protection Like single Phase preventor, under voltage over Volage, under current over current & dry run protection suitable for the pump described above 1 no Indoor type NOTE:
1) DOL- Direct Online Starter
2) S-D- Star Delta Starter etc. complete.
13.23.1 | Upto 3 HP pumps | Each | 6500
13.23.2 | 3 to 6 HP pumps | Each | 9550
13.23.3 | 6 to 15 HP pumps | Each | 15900
13.24 | for outdoor
13.24.1 | Upto 3 HP pumps | Each | 7500
13.24.2 | 3 to 6 HP pumps | Each | 10500
13.24.3 | 6 to 15 HP pumps | Each | 17500
13.25 | Supply and delivery at site best indigenous brand new power capacitor as per IS 2834/1986 with latest amendments with KPTCL authorities and erection, electrification and commissioning of the same at the location of respective pump sets. | kVAR | 550
13.26 | Supply and delivery at site delivery of best indigenous brand new MCB (Miniature Circuit Breakers) of required capacity as per IS 88228/1978 and its latest amendments and with ISI Mark of 6/10/16/20/25/40 Amps with scalable box. | per 3 poles | 1150
13.27 | Supply and delivery of galvanized mild steel tubes of 6mtr standard length heavy duty (C Class) as per IS 1239 (Part-I) 1990 with latest amendments with ISI Mark (one end fitted with Heavy Duty collar and other end fitted with protective cover)
13.27.1 | 50 mm | Each | 3050
13.27.2 | 65 mm | Each | 3575
13.27.3 | 80 mm | Each | 4158
13.28 | Supply and delivery at site 50mm(2”) dia heavy duty unplasticized PVC Column pipes with heavy duty collars,rubber profile ring,vibration control profile ring,freezing and turbulence free leak proof EPDM ring with ISI mark with its latest amendments | m | 550
13.29 | Supply and delivery at site 50mm(2”) dia heavy duty CI adopter set complete suitable for uPVC Column pipes for Submersible pumpsets | SET | 1550
13.3 | Supply and delivery at site Accessories for Single Phase pumpset like SS Groove Nipples,SS Studs & Nuts,Screw Clips &water proof Insulation Tape etc complete with ISI mark | SET | 4500
13.31 | Supply and delivery at site Stringing of heavy duty Naylone/PP rope with ISI etc complete suitable for Single phase Pumpsets. | m | 40
13.32 | Labour charges for Erection, Electrification and commissioning of Pump sets, including aligning and balancing of all items including supply and erection of two pair of supporting clamps, bore well caps, cable clips and water tight gland cable protectors, bolts, nuts, valve and gauges,tools and equipments etc., involved in the job as per specifications, with necessary tests as per specifications, with testing of as per instructions of engineer incharge of work. | Job | 6500
13.33 | Labour charges for erection of indoor type panel board and meter board units with all necessary materials and labour tools and equipments including cement concrete for foundation/bed etc,complete as per specification, with testing of as per instructions of engineer incharge of work. | Job | 1350
13.34 | Labour charges for erection of outdoor type panel board and meter board units with all necessary materials and labour, tools and equipments including providing cement concrete foundation bed etc., complete as per specification, with testing of as per instructions of engineer incharge of work. | Job | 1450
13.35 | Labour charges for providing connection using insulated sheathed steel wire cable as per IS 1554/ 1988 with latest amendments from KPTCL pole to meter board unit, with all necessary materials ,tools and equipments,as per specificationswith testing of as per instructions of engineer incharge of work. .
13.35.1 | 2 x 10 sqmm | m | 80
13.35.2 | 3½ x 6 sqmm | m | 160
13.35.3 | 3½ x 10 sqmm | m | 195
13.35.4 | 3 x 10 sqmm (suitable for over head mains) | m | 165
13.35.5 | 3½ x 16 sqmm | m | 270
13.36 | Providing main connection from pole PVC insulated sheathed steel wire cable in new trench as per IS 1554/ 1988 with latest amendments with ISI mark from KPTCL pole to meter board unit. | m | 135
13.37 | Providing main connection from pole PVC insulated sheathed steel wire cable in GI pipe as per IS 1554/ 1988 with latest amendments with ISI mark from KPTCL pole to meter board unit. | m | 85
13.38 | Providing and fixing suitable for 1.1 KV class UG cable filled with necessary bitumen/insulating compound complete with terminals, clamps,bolts,nuts and washers etc. with necessary materials and labour tools and equipments as per instructions of engineer incharge of work.
13.38.1 | 3½x6 Sqm | Each | 375
13.38.2 | 3½x10 Sqm | Each | 450
13.38.3 | 3½x25 Sqm | Each | 562
13.39 | Earthing: Providing and fixing and wiring earth electrode for grounding circuits IC cutouts and other equipments on the meter board in the pit. The pits should be filled up with equal proportion of salt and charcoal 150mm around the pipe to complete depth. The connection from the pipe to the conduits etc. is to established through GI wire of sizes as per clause 7.3.3 of IS 732 using 12mm bolts, nuts, washers and check nuts, the pipe shall have 16 through holes of 12mm dia. | Job | 3750
13.4 | Supply and delivery of Centrifugal pumpset at site brand new best make and with discharge duty confirming to ISI standards and its latest amendments. | Discuss
13.40.1 | 2 HP, Size 65x50 Head 13M, Discharge 462 LPM | Each | 15610
13.40.2 | 2 HP, Size 50x40 Head 22M, Discharge 186 LPM | Each | 16993
13.40.3 | 3 HP, size 50x40 Head 30M, Discharge 198 LPM | Each | 18816
13.40.4 | 5 HP, size 80x65 Head 23.50M, Discharge 600 LPM | Each | 22310
13.40.5 | 5 HP, size 50x40 Head 46M, Discharge 174 LPM | Each | 26417
13.40.6 | 7.5 HP, size 100x100 Head 195M, Discharge 1200 LPM | Each | 30520
13.40.7 | 7.5 HP, size 80x65 Head 195M, Discharge 1200 LPM | Each | 33619
13.40.8 | 7.5 HP, size 65x50 Head 46M, Discharge 360 LPM | Each | 35150
13.40.9 | 10 HP, size 80x65 Head 34.50M, Discharge 840 LPM | Each | 37623
13.40.10 | 12.5 HP, size 100x100 Head 25M, Discharge 1560 LPM | Each | 38331
13.40.11 | 12.5 HP, size 80x65 Head 40M, Discharge 780 LPM. | Each | 46710
13.40.12 | 15 HP, size 80x65 Head 44M, Discharge 900 LPM | Each | 53967
13.40.13 | 20 HP, size 100x80 and 42M, Discharge 1320 LPM | Each | 65918
13.41 | Supply and delivery at site brand new best make pressure guage suitable for centrifugal pump confirming to latest IS standards.
13.41.1 | pressure guage 80MM | Each | 597
13.41.2 | pressure guage 100MM | Each | 654
13.42 | Supply and delivery at site brand new best make level guage suitable for centrifugal pump confirming to latest IS standards. | Each | 750
13.43 | Supply and delivery at site brand new best make starter/ control panel suitable for following HP centrifugal pump confirming with ISI mark and its latest amendments.
13.43.1 | Upto 7.5 HP centrifugal pump | Each | 9500
13.43.2 | 7.5 to 10 HP centrifugal pump | Each | 15550
13.43.3 | 10 to 12 HP centrifugal pump | Each | 35650
13.44 | Supply, delivery, erection and commissioning at site lighting distribution board suitable for monoblock centrifugal pump confirming with ISI mark and its latest amendments. | Each | 3500
13.45 | Supply, delivery, erection and commissioning at site ELCB suitable for monoblock centrifugal pump confirming with ISI mark and its latest amendments. | Each | 4117
13.46 | Providing and fixing LT cable of size 4 x 25 Sqm suitable for centrifugal pump sets with ISI mark and its latest amendments. | m | 562
13.47 | Supply and delivery at site brand new best make Foot valve suitable for centrifugal pump upto 10HP confirming with ISI mark and its latest amendments. | Each | 1750
13.48 | Supply and delivery at site brand new best make Foot valve suitable for centrifugal pump above 12.50HP confirming with ISI mark and its latest amendments. | Each | 2200
13.49 | Rewinding of monoblock motor with copper insulaton wire suitable gauge as per ISI specification with all necessary materials and labour,tools and equipments with guarantee period of not less than 12 months
13.49.1 | 7.5 HP monobloc motor rewinding | Job | 4000
13.49.2 | 10 HP monobloc motor rewinding | Job | 6500
13.49.3 | 12.5 HP monobloc motor rewinding | Job | 8000
13.49.4 | 15 HP monobloc motor rewinding | Job | 12000
13.49.5 | 20 HP monobloc motor rewinding | Job | 15000
13.49.6 | 30 HP monobloc motor rewinding | Job | 20000
13.49.7 | 40 HP monobloc motor rewinding | Job | 22000
13.49.8 | 50 HP monobloc motor rewinding | Job | 25000
13.49.9 | 60 HP monobloc motor rewinding | Job | 35000
13.49.10 | 80 HP monobloc motor rewinding | Job | 38000
13.49.11 | 100HP monobloc motor rewinding | Job | 50000
13.49.12 | 120 HP monobloc motor rewinding | Job | 62000
13.49.13 | 150 HP monobloc motor rewinding | Job | 65000
13.49.14 | 180 HP monobloc motor rewinding | Job | 75000
13.49.15 | 200 HP monobloc motor rewinding | Job | 85000
13.5 | Providing Ball bearing as per ISI specifiction with guarantee period of not less than 12 months
13.50.1 | Bearing cost for 7.5 HP | Each | 1880
13.50.2 | Bearing cost for 10HP | Each | 2050
13.50.3 | Bearing cost for 12.5 HP | Each | 2050
13.50.4 | Bearing cost for 15 HP | Each | 2550
13.50.5 | Bearing cost for 20 HP | Each | 3080
13.50.6 | Bearing cost for 30HP | Each | 4050
13.50.7 | Bearing cost for 40 HP | Each | 4600
13.50.8 | Bearing cost for 50 HP | Each | 6250
13.50.9 | Bearing cost for 60 HP | Each | 6500
13.50.10 | Bearing cost for 80 HP | Each | 7000
13.50.11 | Bearing cost for 100 HP | Each | 7500
13.50.12 | Bearing cost for 120 HP | Each | 9000
13.50.13 | Bearing cost for 150 HP | Each | 11000
13.50.14 | Bearing cost for 180 HP | Each | 12500
13.50.15 | Bearing cost for 200 HP | Each | 13500
13.51 | Providing thrust bearing as per ISI specifiction with guarantee period of not less than 12 months
13.51.1 | Bearing cost for 30 HP | Each | 6500
13.51.2 | Bearing cost for 40HP | Each | 7500
13.51.3 | Bearing cost for 50 HP | Each | 8500
13.51.4 | Bearing cost for 60 HP | Each | 11000
13.51.5 | Bearing cost for 80 HP | Each | 13500
13.51.6 | Bearing cost for 100 HP | Each | 14000
13.51.7 | Bearing cost for 120 HP | Each | 16500
13.51.8 | Bearing cost for 150 HP | Each | 18000
13.51.9 | Bearing cost for 180 HP | Each | 19500
13.51.10 | Bearing cost for 200 HP | Each | 21000
13.52 | Providing terminal plate as per ISI specifiction with guarantee period of not less than 12 months
13.52.1 | terminal plate 7.5 to 12.5 | Each | 450
13.52.2 | terminal plate 15 to 30 | Each | 850
13.52.3 | terminal plate 40 to 60 | Each | 1050
13.52.4 | terminal plate 80 to 120 | Each | 2000
13.52.5 | terminal plate 150 to 200 | Each | 3500
13.53 | Repairs to Vertical turbine pumps as per ISI specifiction with guarantee period of not less than 12 months V- T Pump
13.53.1 | Phosphorous bronze bearing bush for 30 HP to 40 HP | Each | 4800
13.53.2 | Phosphorous bronze bearing bush for 50 HP to 60 HP | Each | 5500
13.53.3 | Phosphorous bronze bearing bush for 80 HP to 100 HP | Each | 7500
13.53.4 | Phosphorous bronze bearing bush for 100 HP to 150 HP | Each | 8200
13.53.5 | Phosphorous bronze bearing bush for 180 HP to 200 HP | Each | 9000
13.54 | Repairs to Vertical turbine pumps as per ISI specifiction with guarantee period of not less than 12 months V-T PUMP STAGE BUSHES
13.54.1 | Phosphorous bronze stage bushes for 30 to 40 HP | Each | 4500
13.54.2 | Phosphorous bronze stage bushes for 50 to 60 HP | Each | 5200
13.54.3 | Phosphorous bronze stage bushes for 80 to 100 HP | Each | 7500
13.54.4 | Phosphorous bronze stage bushes for 100 to 150 HP | Each | 8500
13.54.5 | Phosphorous bronze stage bushes for 180 to 200 HP | Each | 9500
13.55 | Repairs to Vertical turbine pumps as per ISI specifiction with guarantee period of not less than 12 months V-T PUMP IMPELLER AND NECK RING
13.55.1 | IMPELLER AND NECK RING for 30 HP to 40 HP | Each | 4800
13.55.2 | IMPELLER AND NECK RING for 50 HP to 60 HP | Each | 5200
13.55.3 | IMPELLER AND NECK RING for 80 HP to 100 HP | Each | 9000
13.55.4 | IMPELLER AND NECK RING for 100 HP to 150 HP | Each | 8000
13.55.5 | IMPELLER AND NECK RING for 180 HP to 200 HP | Each | 9500
13.56 | Repairs to Vertical turbine pumps as per ISI specifiction with guarantee period of not less than 12 months HORIZANTAL PUMP
13.56.1 | Phosphorous bronze bushes for 7.5 to 15 HP monoblock motor | Each | 800
13.56.2 | Phosphorous bronze bushes for 20 HP monoblock motor | Each | 1800
13.56.3 | Phosphorous bronze bushes for 40HP to 80HP monoblock motor | Each | 5800
13.56.4 | Phosphorous bronze bushes for 100HP to 120HP monoblock motor | Each | 6500
13.56.5 | Phosphorous bronze bushes for 150HP to 200 HP monoblock motor | Each | 8000
13.57 | BEARING FOR HORIZONTAL PUMP
13.57.1 | For 20 HP pump bearing | Each | 2500
13.57.2 | For 30 HP Pump bearing | Each | 3500
13.57.3 | For 40 to 80 HP pump bearing | Each | 4500
13.57.4 | For 60 to 80 HP pump bearing | Each | 8400
13.57.5 | For 100 to 150HP pump bearing | Each | 10200
13.57.6 | For 180 to 200 HP pump bearing | Each | 10800
13.58 | ALL TYPES OF JACK WELL V-T PUMP DETAILS as per ISI specifiction with guarantee period of not less than 12 months -For Pump dismentaling and refitting after attending repairs.
13.58.1 | Up to 60 HP | Each | 10000
13.58.2 | 60 HP to 120 HP | Each | 12000
13.58.3 | 120 HP to 200 HP | Each | 15000
13.58.4 | 200 HP to 250 HP | Each | 18000
13.59 | For Top body bush fitting
13.59.1 | Up to 60 HP | Each | 2000
13.59.2 | 60 HP to 120 HP | Each | 2500
13.59.3 | 120 HP to 200 HP | Each | 2800
13.59.4 | 200 HP to 250 HP | Each | 1675
13.6 | For Bottom body bush fitting
13.60.1 | Up to 60 HP | Each | 1450
13.60.2 | 60 HP to 120 HP | Each | 1850
13.60.3 | 120 HP to 200 HP | Each | 1975
13.60.4 | 200 HP to 250 HP | Each | 2075
13.61 | For Pumps stage body bush fitting Each
13.61.1 | Up to 60 HP | Each | 850
13.61.2 | 60 HP to 120 HP | Each | 1050
13.61.3 | 120 HP to 200 HP | Each | 1125
13.61.4 | 200 HP to 250 HP | Each | 1250
13.62 | For Pump body necking fitting Each
13.62.1 | Up to 60 HP | Each | 1200
13.62.2 | 60 HP to 120 HP | Each | 1475
13.62.3 | 120 HP to 200 HP | Each | 1650
13.62.4 | 200 HP to 250 HP | Each | 1850
13.63 | For Impeller breezing making
13.63.1 | Up to 60 HP | Each | 1050
13.63.2 | 60 HP to 120 HP | Each | 1175
13.63.3 | 120 HP to 200 HP | Each | 1250
13.63.4 | 200 HP to 250 HP | Each | 1280
13.64 | For Pump shaft press throwble
13.64.1 | Up to 60 HP | Each | 680
13.64.2 | 60 HP to 120 HP | Each | 700
13.64.3 | 120 HP to 200 HP | Each | 750
13.64.4 | 200 HP to 250 HP | Each | 850
13.65 | For Pump open & fitting at work shop
13.65.1 | Up to 60 HP | Each | 3500
13.65.2 | 60 HP to 120 HP | Each | 4000
13.65.3 | 120 HP to 200 HP | Each | 4500
13.65.4 | 200 HP to 250 HP | Each | 5000
13.66 | For Connecting bush G.M new making Each
13.66.1 | Up to 60 HP | Each | 1875
13.66.2 | 60 HP to 120 HP | Each | 1975
13.66.3 | 120 HP to 200 HP | Each | 2255
13.66.4 | 200 HP to 250 HP | Each | 2575
13.67 | For Line shaft seat welding making Each
13.67.1 | Up to 60 HP | Each | 450
13.67.2 | 60 HP to 120 HP | Each | 550
13.67.3 | 120 HP to 200 HP | Each | 500
13.67.4 | 200 HP to 250 HP | Each | 600
13.68 | For Oil inside new Fitting & threading Each
13.68.1 | Up to 60 HP | Each | 1400
13.68.2 | 60 HP to 120 HP | Each | 1600
13.68.3 | 120 HP to 200 HP | Each | 1850
13.68.4 | 200 HP to 250 HP | Each | 1950
13.69 | For Balancing spaider rubber guide Each
13.69.1 | Up to 60 HP | Each | 1200
13.69.2 | 60 HP to 120 HP | Each | 1300
13.69.3 | 120 HP to 200 HP | Each | 1450
13.69.4 | 200 HP to 250 HP | Each | 1570
13.7 | For New T.T nipple making
13.70.1 | Up to 60 HP | Each | 3050
13.70.2 | 60 HP to 120 HP | Each | 3250
13.70.3 | 120 HP to 200 HP | Each | 3500
13.70.4 | 200 HP to 250 HP | Each | 3800
13.71 | For Pump gear box body radial bearing
13.71.1 | Up to 60 HP | Each | 13575
13.71.2 | 60 HP to 120 HP | Each | 16575
13.71.3 | 120 HP to 200 HP | Each | 18075
13.71.4 | 200 HP to 250 HP | Each | 20750
13.72 | For Gear box ball bearing
13.72.1 | Up to 60 HP | Each | 1500
13.72.2 | 60 HP to 120 HP | Each | 1650
13.72.3 | 120 HP to 200 HP | Each | 1925
13.72.4 | 200 HP to 250 HP | Each | 2075
13.73 | For Pumping and clean pipe painting
13.73.1 | Up to 60 HP | Each | 1675
13.73.2 | 60 HP to 120 HP | Each | 1875
13.73.3 | 120 HP to 200 HP | Each | 2150
13.73.4 | 200 HP to 250 HP | Each | 2250
13.74 | For Transportation charges both side
13.74.1 | Up to 60 HP | Each | 2500
13.74.2 | 60 HP to 120 HP | Each | 3500
13.74.3 | 120 HP to 200 HP | Each | 4200
13.74.4 | 200 HP to 250 HP | Each | 4500
13.75 | Water Treatment Plants HORIZANTAL PUMP ALL TYPES-For Pump open & refitting after repairs
13.75.1 | Up to 25HP | Each | 4900
13.75.2 | 25 HP to 100 HP | Each | 5200
13.75.3 | 100 HP to 150 HP | Each | 5800
13.75.4 | 150 HP to 250 HP | Each | 6200
13.76 | For Side gland bush
13.76.1 | Up to 25HP | Each | 1500
13.76.2 | 25 HP to 100 HP | Each | 1800
13.76.3 | 100 HP to 150 HP | Each | 2000
13.76.4 | 150 HP to 250 HP | Each | 2100
13.77 | For Impeller breezing and making
13.77.1 | Up to 25HP | Each | 1100
13.77.2 | 25 HP to 100 HP | Each | 1450
13.77.3 | 100 HP to 150 HP | Each | 1600
13.77.4 | 150 HP to 250 HP | Each | 1700
13.78 | For Shaft steel welding and making bearing sheet Each
13.78.1 | Up to 25HP | Each | 1100
13.78.2 | 25 HP to 100 HP | Each | 1450
13.78.3 | 100 HP to 150 HP | Each | 1600
13.78.4 | 150 HP to 250 HP | Each | 1850
13.79 | For Shaft threading making Each
13.79.1 | Up to 25HP | Each | 1250
13.79.2 | 25 HP to 100 HP | Each | 1650
13.79.3 | 100 HP to 150 HP | Each | 1815
13.79.4 | 150 HP to 250 HP | Each | 2015
13.8 | For Joint rope of 1kg
13.80.1 | Up to 25HP | Each | 700
13.80.2 | 25 HP to 100 HP | Each | 815
13.80.3 | 100 HP to 150 HP | Each | 915
13.80.4 | 150 HP to 250 HP | Each | 1050
13.81 | For Pump shaft bend thrown
13.81.1 | Up to 25HP | Each | 950
13.81.2 | 25 HP to 100 HP | Each | 1150
13.81.3 | 100 HP to 150 HP | Each | 1350
13.81.4 | 150 HP to 250 HP | Each | 1650
13.82 | For Transportation
13.82.1 | Up to 25HP | Each | 2715
13.82.2 | 25 HP to 100 HP | Each | 3050
13.82.3 | 100 HP to 150 HP | Each | 3250
13.82.4 | 150 HP to 250 HP | Each | 3650
13.83 | For Pump shaft getting check nut Each
13.83.1 | Up to 25HP | Each | 1050
13.83.2 | 25 HP to 100 HP | Each | 1050
13.83.3 | 100 HP to 150 HP | Each | 1115
13.83.4 | 150 HP to 250 HP | Each | 1250
13.84 | For Both coupling new set
13.84.1 | Up to 25HP | Each | 8500
13.84.2 | 25 HP to 100 HP | Each | 10200
13.84.3 | 100 HP to 150 HP | Each | 11000
13.84.4 | 150 HP to 250 HP | Each | 12000
13.85 | Providing and installing of solar photo voltaic (SPV) water pumping system INDUCTION MOTOR, PUMPSETS AND A SUITABLE INVERTER
as per IS specification and instruction of Engineer incharge of work as per IS specification- For 3000 wp/ 3HP submersible with controller
13.85.1 | Total head 30 mtrs and shut off dynamic Head 45 mtr and water out put 96000 ltrs/day. | Each | 267000
13.85.2 | Total head 50 mtrs and shut off dynamic Head 75 mtr and water out put 57000 ltrs/day. | Each | 270000
13.85.3 | Total head 70 mtrs and shut off dynamic Head 100 mtr and water out put 39000 ltrs/day | Each | 273000
13.86 | For 4800 wp/ 5HP submersible with controller
13.86.1 | Total head 50 mtrs and shut off dynamic Head 70 mtr and water out put 91200 ltrs/day. | Each | 383000
13.86.2 | Total head 70 mtrs and shut off dynamic Head 100 mtr and water out put 62400 ltrs/day. | Each | 386000
13.86.3 | Total head 100 mtrs and shut off dynamic Head 150 mtr and water out put 40800 ltrs/day. | Each | 389000
13.87 | For 6750 wp/ 7.5 HP submersible with controller
13.87.1 | Total head 50 mtrs and shut off dynamic Head 70 mtr and water out put 128250 ltrs/day. | Each | 565000
13.87.2 | Total head 70 mtrs and shut off dynamic Head 100 mtr and water out put 87750 ltrs/day. | Each | 568000
13.87.3 | Total head 100 mtrs and shut off dynamic Head 150 mtr and water out put 57375 ltrs/day. | Each | 571000
13.88 | For 9000 wp/ 10HP submersible with controller
13.88.1 | Total head 50 mtrs and shut off dynamic Head 70 mtr and water out put 171000 ltrs/day. | Each | 714000 | Cable Selection chart for 415 volts, 50 Hz, 3 phase motors (considering Ambient Temp. 50deegre & 3% Voltage Drop)
13.88.2 | Total head 70 mtrs and shut off dynamic Head 100 mtr and water out put 117000 ltrs/day. | Each | 717000 | MOTOR RATING |  | FULL LOAD CURRENT | CABLE SIZE
13.88.3 | Total head 100 mtrs and shut off dynamic Head 150 mtr and water out put 76500 ltrs/day. | Each | 720000 |  |  |  | LENGTH OF CABLE IN METERS
|  |  |  | kw | HP | (AMPS) | 1.5 | 2.5 | 4 | 6 | 10 | 16
|  |  |  | 2.2 | 3 | 6.3 | 87 | 145 | 230 | - | - | -
|  |  |  | 3.7 | 5 | 9.3 | 63 | 100 | 160 | 238 | - | -
|  |  |  | 4.5 | 6 | 11.8 | 47 | 78 | 125 | 185 | 300 | -
|  |  |  | 5.5 | 7.5 | 14.5 | 41 | 68 | 107 | 158 | 262 | -
|  |  |  | 7.5 | 10 | 18 | - | 51 | 80 | 120 | 200 | 297
|  |  |  | 9.3 | 12.5 | 22.5 | - | - | 65 | 97 | 160 | 253
|  |  |  | 11 | 15 | 26 | - | - | 56 | 84 | 137 | 216
|  |  |  | 12.9 | 17.5 | 32.5 | - | - | - | - | 110 | 175
|  |  |  | 15 | 20 | 36.5 | - | - | - | - | 98 | 155
|  |  |  | 18.5 | 25 | 39 | - | - | - | - | 93 | 150
|  |  |  | 22 | 30 | 45 | - | - | - | - | 81 | 130
|  |  |  | 25.7 | 35 | 52 | - | - | - | - | 70 | 112
Cable Size Selection for 3 dia 150 mm submersibles
[6 empty] | Cable size recommended for | Cable size recommended for | Cable size recommended for
|  |  |  | Motor HP | Starting | up to 45 M cable length | up to 75 M cable length | up to 95 M cable length
|  |  |  | 35 | S/D | 2x3x4mm2 | 2x3x6mm2 | 2x3x10mm2
|  |  |  | 30 | S/D | 2x3x4mm2 | 2x3x6mm2 | 2x3x10mm2
|  |  |  | 25 | S/D | 2x3x4mm2 | 2x3x6mm2 | 2x3x10mm2
|  |  |  | 20 | S/D | 2x3x4mm2 | 2x3x6mm2 | 2x3x10mm2
|  |  |  | 17.5 | S/D | 2x3x2.5mm2 | 2x3x4mm2 | 2x3x6mm2
|  |  |  | 15 | S/D | 2x3x2.5mm2 | 2x3x4mm2 | 2x3x6mm2
|  |  |  | 12.5 | S/D | 2x3x2.5mm2 | 2x3x4mm2 | 2x3x6mm2
|  |  |  | 10 | S/D | 2x3x2.5mm2 | 2x3x4mm2 | 2x3x6mm2
|  |  |  | 7.5 | DOL | 1x3x2.5mm2 | 1x3x4mm2 | 1x3x6mm2
|  |  |  | 6 | DOL | 1x3x2.5mm2 | 1x3x2.5mm2 | 1x3x4mm2
|  |  |  | 5 | DOL | 1x3x1.5xmm2 | 1x3x2.5mm2 | 1x3x2.5mm2
|  |  |  | 4 | DOL | 1x3x1.5mm2 | 1x3x2.5mm2 | 1x3x2.5mm2
|  |  |  | 3 | DOL | 2x3x1.5mm2 | 1x3x2.5mm2 | 1x3x2.5mm2

## BoQ_4
Bill of Quantity 4 (Variable Cost)
ELECTRICAL WORKS
19.1 | Work of rewinding of HV side upto 100KVA power transformer as specified below: a. Switch off Power supply of transformer Isolator feeder and discharge with discharge rod. b. Disconnect the input and output cables form 100 Kva transformer. c. Drain old transformer oil from transformers, and flush the winding jet force with good BDV valve transformer oil. d. Manually lead up to crane rEach and load to truck to shift factory. e. After rewinding the burnt out HV windings of transformer and replace the gaskets carbonized bolts and Nuts check the necessary tests. f. Fill the new transformer oil (BWSSB Supply) & replace the silica gel breather. g. Re install transformer after received form factory. h. Switch ON power supply and check the transformer, No load and on load. | Job | 75178
19.2 | Work of repair and rewinding of LV side upto 100 KVA power transformer as specified below: a. Drain out the contaminated transit oil completely from the reactor; flush the windings of the transformer with jet force of good BDV value transit oil. b. Removing the burnt out windings from all the three phases of the transformer provide new windings of LV side in all three phases. c. Clean the terminal connection with carbon tetra chloride solution. d. Fill the new transit oil (departmental supply) replace the bolts, nuts, washers and provide gasket etc., wherever necessary provide silica gel breather. e. Fix the transformer in the bet and charge the transformer and observe Performance “ON LOAD” and ensure for trueness of the transformer performance. | Job | 70641
19.3 | Work of servicing, leak arresting and oil filtration upto 400 KVA power transformers as specified below: a. Removing cable connection of transformer after isolating the supply dismantling the cable connection | Job | 69540
b. Replacing the existing leakage L.V side H.T Busing Gasket, oil seal, bots and nuts etc. of the power transformer. c. Replacing the existing non-functioned damaged Dehydrating Breather by a new breather with new silica gel for the above transformer d. Arresting oil leak from exclusive vent, neutral bushing of valves, flanges, is drying arresting the leakage for L.V and HV side of power transformer and refilling of the transformer oil including cost of labour and necessary repaired materials.
e. Repaint the Transformer using light grey epoxy paint of 2 coated as original. f. Filtering of oil in the transformer at the transformer center by hot process using stream line filter such that the dielectric strength of oil in the transformer conforms to ISI specification. g. Painting of entire structure of transformer yard including fencing using silver paint.
19.4 | Work of repairs/servicing and overhauling of on load tap changer (OLTC) of upto 66KV/6.6KV 8MVA transformer as specified below: A). Removing the supply connection of diverter switch draining out the diluted oil of OLTC chamber, removing the diverter switch one by one carefully by using tripped and chain pulley block. Dismantling the moving and fixing contacts and cleaning with good quality cleaning agents to remove the carbon deposit, replacing the worn-out compression spring micros switch tap changing contacts, of worn gear assembly, replacing of worn out bearing oil seals, ‘O’ rings, gaskets, etc., in order to ensure fiction from operations of tap changing and oil leakage from diverter switch mechanism housing resistance by new one which will be supplied by departmentally, cleaning the diverter switch housing chamber to remove the carbon deposit lowering the serviced diverter switch inside the housing chamber and aligning the centre shaft by using lock nut, bolt and washers tighting of resistor conductors carefully without causing damaged to the nearby the contact refilling the good quality high BDV value insulation oil to the diverter switch housing chamber (oil will be supplied by the department adjusting the micro switch NO NC contacts and lifting liver for its proper function and covering the chamber by fixing the lid on the top and cleaning the oil gauge indicator with soap water, after drying refix the same testing the operation of tap changing system by giving upto 440 Volts supply from tap position 1 to 25 after satisfactory charging over of all 25 taps in forward and reverse direction. | Job | 46977
19.5 | Work of repairs/servicing and overhauling of on load tap changer (OLTC) of upto 66KV/6.6KV 8MVA transformer as specified below: Painting of transformer including platform CTS etc., with one cost of red oxide to the rusted portion of transformer, 2 coats of M/s grey enamel paint, RYB color paint to CT caps for identification etc., Rates should coat inclusive of cleaning of the transformer of all sizes. | Job | 28257
19.6 | Work of repairing of diverter switch and replacement of resistance upto 66KV/6.6KV 8MVA Transformer as specified below: Removing the supply connection of diverter switch draining out the diluted oil of OLTC chamber, removing the diverter switch one by one carefully by using tripped and chain pulley block. Dismantling the diverter switch unit, removing the worn-out resistance from the diverter switch Supply and fixing of new resistance of same capacity as original to the diverter switch without disturbing the other running equipment, cleaning the diverter switch housing chamber to remove the carbon deposit, lowering the repaired diverter switch inside the housing chamber and aligning the centre shaft by using link nut, bolt and washers tighting of resistor conductors carefully without causing damaged to the nearby the contact refilling the good quality high BDV value insulation oil to the diverter switch housing chamber (oil will be supplied by the department) adjusting he micro switch NO, NC contacts and lifting liver for its proper function and covering the chamber by fixing the lid on the top. Testing the operation of tap changing system by giving upto 440 Volts supply from tap position 1 to 25 after satisfactory charging over all 25 taps in forward and reverse direction. | Job | 75152
19.7 | Works of Supply fixing and wiring of tap position indicator to RTCC panel transformer as detailed:. Tap position indicator Aux supply: -110V or 230V AC +15% 50HZ, Resistance: - 1 Kilo ohms per step, Tele- transmitter: - 3Wire connection 1 to 99 position, Display: -2Digit 7 segment LED, Accuracy -Tolerance +2%, Type of mounting: -Panel mounting 90x90x70mm, Dimension: -96mm x 96mm x 70mm, Accuracy: -Class 11 | Each | 20167
19.8 | Works of Supply fixing and wiring of digital kilowatt meter to RTCC panel upto 5MVA transformer as detailed: Aux supply -606KV -110V OR 230V AC, Range - 0 to 9 KW, Burden - 4VA, Display -3.1/2 digital for nominal full seals, Voltage input -110V from P.T, Mountry -Panel type, Cut out size - 90x90mm, Ambient Emp -0.50degree C, Model | Each | 17385
- DM 3257 ACC.CL:1.0, Accuracy -Class -1.0
19.9 | Work of supply, erection and commissioning of indoor upto 250 Amps distribution panel as specified below: Supply, erection and commissioning of Indoor type upto 250 Amps MCCB distribution panel with outgoing copper bus bar, having, accessories like MCCB, incoming and outgoing entry bus bar, ammeter volt meter, ammeter selector switch, LED indication lamp, and with suitable M.S box with required stand unit set. Suitable for Indoor type complete as per latest IS standard specification. | Each | 68498
19.1 | Work of supply and fixing of 85W, LED high way fitting to top of panel board, soft starter and breaker as specified below: Providing High pressure high way 85W LED fitting die cast aluminum canopy with aluminum housing to control gear, finished stove enamel gray glassy white canopy interior with a pair of anodized aluminum reflectors clear acrylic bowl, gasket lining for dip inseat resistance duly wired with single or multi LEDS. | Each | 18560
19.11 | Work of supply and fixing of isolator panel and capacitor panel fuses to motor. as specified below: A) Removing the damaged burnt out fuses upto 63Amps 7.2 /11 K.V isolator fuses form isolator panel for motor cleaning the fuse carriers with CTC and apply petroleum jelly for fuse contacts and rectify the faulty in the isolator panel. Supply and fixing new fuses upto 7.2/11 K.V isolator fuses to the fuse carrier and checking its working. B) Removing the damaged burnt out fuses upto 30Amps | Each | 15062
7.2/11 K.V capacitor fuses form capacitor panel of motor cleaning the fuse carriers with CTC and apply petroleum jelly for fuse contacts and rectify the faulty in the isolator panel. Supply and fixing new fuses upto
7.2/11 K.V capacitor fuse to the fuse carrier and checking its working
19.12 | Work of repairing and servicing of capacitor isolator panel of motors as specified below: A) Dismantling the closing and tripping mechanism, removing the broken, closing lever, cylinder, moving contact tips, and service the entire mechanism, Providing and fixing the new closing lever full set cylinder, moving contact tips, etc., check the electrical circuit, | Job | 34231
replacement of burnt out LED Indication lamps etc., finally the panel should be tested for its running satisfactorily. B) Draining out contaminated breakdown oil completely form reactors, flushing of windings in the reactors with jet force of good BDV. Value transformer oil, cleaning of windings and flushing of carbon deposition over the windings in all the three phase of reactors, removing the terminals and cleaning the terminal bushings with carbon tetrachloride solution, checking of resistance of the windings of the correct value in all the three phases, filling the new oil with break down voltage value.
19.13 | Work of replacement of faulty control components and modification and rewiring of soft starter panel upto 1250KW/6.6KV motor as specified below: a. Disconnecting the power cables and control cables. b. Removal of faulty control components and cable disconnections. c. Supply and fixing Auxiliary contractors, upto 110Volt DC coil Supply with 2 NO, 2NC. d. Supply and fixing of Electronic Timers, 24 Volt AC Range 0 to 30 seconds. e. Supply and fixing of MCBs, 2 pole, 10A. f. Supply and fixing of suitable color LED indication Bulbs and reset Push Buttons Red in color. g. Supply and fixing of temperature Scanner. Along with RTDs | Job | 69031
3.5 Mtr Each. h. The necessary tapping/drilling work has to be done for fixing the above components and rewiring to be done etc., i. Testing the soft starter with above supplied components. j. Commissioning the soft starter and handing over the system to department.
19.14 | Work of supply and fixing of 40 amps star delta panel Boards upto 15Hp backwash pump motor as specified below: a. Supply and fixing of new upto 15 Hp star delta starter panel board for back wash motor with the following materials. b. Power connector upto 40 A. c. On delay, off delay automatic timer. d. Over current relay upto 20-60 amps e. Upto 10 amps MCB 3 Pole for control circuit. f. Contactor 2 No+ 2 Nc upto 25 amps g. Single phase preventer. h. On and off push button switch. | Job | 33727
i. LED indication lamps RYB motor on, off and trip. j. 0 to 600 volts meter upto 96/96 mm. k. Amps meter C.T Ratio upto 100/5A. l. Current Transformer for metering upto 100/5A. m. upto 30mmx10mm Electronic Grad Aluminum bus bar for RYB phases. n. Internal main wiring using upto 95 sq.mm Copper wire. o. Volts and ammeter selector switch.
19.15 | Work of overhauling and servicing and repairing of southern switch gear make breakers of motor as specified below: Lowering the breaker from the panel after isolating the supply, draw out the breaker truck from the panel, checking the fixed and moving contacts. Removing the burnt out parts from the breaker. Supply and fixing of new closing assembly, rose contact, copper poker, banana link, lifting awwembly. Checking the mechanical parts such as moving cam, lifting bar assembly, tripping mechanism and closing mechanism of the breaker and servicing the entire breaker. Check the trip and closing coil of the breaker replace the same if required. Replace the oil (Supply by departmentally). The breaker has to be checked in test position after complete servicing for proper operation and satisfaction. | Job | 75122
19.16 | Work of repair and servicing of LOCB breakers of motor feeders and spare breakers as specified below: MECHANICAL PORTION: Removing the complete unit breaker mechanism from the breaker without damaging the arc chamber, wiring to be recorded before removing the breaker mechanism. Dismantling the tension spring latching unit etc., inspecting the alignment and rectify the fault in breakers for proper closing and opening cleaning all moving contact finger contact and fixed contact by C.T.C replace the oil by new oil (Oil will be supplied by the departments). ELECTRICAL PORTION: Checking of entire electrical operation of the breaker panel checking ON & OFF circuit, change over scheme replacement of closing coil, tripping coil, closing contactor wiring should be checked as per drawing, damaged wire should be replaced by new one, all the required spare will be supplied by departmentally. The work should be carried out without disturbing other running equipment. | Job | 18325
19.17 | Work of repair, overhauling & servicing of southern switch gear breakers of capacitor bank as specified below: Lowering the breaker from the panel after isolating the supply, draw out the breaker truck from the panel, checking the fixed and moving contacts and replace with new contacts wherever necessary. Repair the worn out rose contacts and poker tips. Checking the mechanical parts such as moving cam, lifting bar assembly, tripping mechanism and closing mechanism of the breaker and servicing. Check the trip and closing coil of the breaker. The breaker has to be checked in test position after complete servicing for proper operation and satisfaction | Job | 33727
19.18 | Working of repairing and overhauling of upto 800amps as specified below: Complete dismantling of breaker units of upto 800 amps breaker of filter house taking out the fixed and moving contacts of all the poles, cleaning and putting back with necessary lubrication and checking of complete electrical circuit for proper closing and tripping including necessary replacement of ‘V’ bar contact, finger contact, contact tips, arching contact, tripping and closing coil, back housing set, with female contacts, panel fixed contact set including hylem sheet with contacts, gasket and dash pit oil etc., Testing of tripping and closing mechanism in order to ensure easy of operation of the breaker and commissioning of the system as per the standard practice without interruption of power supply. | Job | 67859
19.19 | Work of repairing and overhauling of upto 400 amps LT breaker bus coupler as specified below: Complete dismantling of breaker units of 400 amps, breaker of compressor room taking out the fixed and moving contacts of al limbs, cleaning and putting back with necessary lubrication and checking of complete electrical circuit for proper closing and tripping including necessary replacement of V bar contact finger contact, contact tips of arcing, contacts of tripping and closing coil, back housing set, gasket and dash pot oil etc.. Testing and tripping and closing mechanism in order to ensure easy operation of the breaker and commissioning of the system as per the standard practice without interruption of power supply. | Job | 67859
19.2 | Work of repair and rewinding of reactor provided to isolator of motor as specified below: A) Drain out the contaminated transit oil completely form the reactor; flush the windings of the reactor with jet force of good BDV value transit oil. B) Removing the burnt out from all the three phased of the reactor provide new windings in all three phases. C) Clean the terminal connection with carbon tetra chloride solution. D) Fill the new transit oil (departmental supply) replace the bolts, nuts, washers and provide gasket etc., wherever necessary provide silica jel breather. | Job | 68591
E) Fix the reactor in the isolator panel and charge the capacitor bank and observe performance “ON LOAD” and ensure for trueness of the reactor performance.
19.21 | Work of overhauling and servicing upto 1250KW, 6.6KV, motor as specified below: a. Disconnect the HT/LT, Cable and record motor details take out the motor from bed b. Check alignment and record details c. Check IR values before removing motor. d. De-couple the motor from pump & taken out from removing anchor bolts e. Dismantling motor end shields f. Removing rotor from stator, checking IR values of stator cleaning stator with thinner, and petrol, g. Removing the moisture of stator by using heaters(oven) h. Revarnishing of stator & rotor baking in oven, applying becktol red on windings on both stator & rotor i. Greasing of bearings, j. Assembling of motor k. Checking IR values of motor and recording the same l. Alignment of motors with pump, and commissioning the motor on No-Load and load trial. | Job | 68006
19.22 | Cutting of the damaged portion of upto 3x150sq.mm XLPE cable Providing one number of indoor termination kit upto 3x150 sq.mm HT XLPE cable and attending the termination work upto 3x150sq.mm HT cable of Neutral side cable by using upto 150sq.mm copper lugs, self adhesive HT tape, crimping tool, heat shrinkable termination kit and required bolts and nuts etc., and Commissioning the motor on load. The work including the cost of materials, labour charges, taxes and the rebate towards the cost of released materials etc. | Job | 11574
19.23 | Supply and brazing of motor end lead cable by using H.T Copper lugs, brazing materials, gas, soldering past, etc as original for all the three phases for motor. | Job | 33727
19.24 | Removing the burnt out supporting insulator from motor of main side Supply and fixing of new insulator to same place as original. | Job | 17406
19.25 | Removing the burnt out copper flats form all the 3 phases of neutral side motor. Providing. copper flats copper flats to neutral side connection. Re connect the motor end cable & cable connection using bolts nuts and washers etc as original | Job | 16577
19.26 | Removing & refixing the pump after repairing of existing horizontal mounting/ monoblock pump with following spares, etc. including aligning of pump with reference to motor & running the pump on load.
19.26.1 | Repairs of Booster Pumps Upto 5HP | Job | 3042
19.26.2 | Repairs of Booster Pumps 5 HP to 10 HP | Job | 3682
19.26.3 | Repairs of Booster Pumps 10 HP to 15 HP | Job | 5028
19.26.4 | Repairs of Booster Pumps 15 HP to 20 HP | Job | 15739
19.26.5 | Repairs of Booster Pumps 20 HP to 30 HP | Job | 20811
19.26.6 | Repairs of Booster Pumps 30 HP to 40 HP | Job | 25823
19.26.7 | Repairs of Booster Pumps 40 HP to 50 HP | Job | 33218
19.26.8 | Repairs of Booster Pumps 50 HP to 60 HP | Job | 38077
19.26.9 | Repairs of Booster Pumps 60 HP to 75 HP | Job | 48193
19.26.10 | Repairs of Booster Pumps 75 HP to 100 HP | Job | 62638
19.26.11 | Repairs of Booster Pumps 100 HP to 150 HP | Job | 71454
19.26.12 | Repairs of Booster Pumps 150 HP to 200 HP | Job | 85912
19.26.13 | Repairs of Booster Pumps 200 HP to 250 HP | Job | 99230
19.26.14 | Repairs of Booster Pumps 250 HP to 300 HP | Job | 112712
19.26.15 | Repairs of Booster Pumps 300 HP to 350 HP | Job | 126539
19.26.16 | Repairs of Booster Pumps 350 HP to 400 HP | Job | 137405
19.27 | Removing and refixing the 230/415 v 50 hz I phase/III phase suitable capacity suitable speed horizontal foot mounted screen protected drip proof continous rated monoblock/squrrel cage induction motor with F class insulation, class H super enamelled copper wire with as per standards including transportation charges etc.,
19.27.1 | Repairs of Booster Motors Upto 5HP | Job | 4949
19.27.2 | Repairs of Booster Motors 5 HP to 10 HP | Job | 6277
19.27.3 | Repairs of Booster Motors 10 HP to 15 HP | Job | 9705
19.27.4 | Repairs of Booster Motors 15 HP to 20 HP | Job | 16836
19.27.5 | Repairs of Booster Motors 20 HP to 30 HP | Job | 25747
19.27.6 | Repairs of Booster Motors 30 HP to 40 HP | Job | 30907
19.27.7 | Repairs of Booster Motors 40 HP to 50 HP | Job | 36915
19.27.8 | Repairs of Booster Motors 50 HP to 60 HP | Job | 44108
19.27.9 | Repairs of Booster Motors 60 HP to 75 HP | Job | 54262
19.27.10 | Repairs of Booster Motors 75 HP to 100 HP | Job | 70287
19.27.11 | Repairs of Booster Motors 100 HP to 150 HP | Job | 96069
19.27.12 | Repairs of Booster Motors 150 HP to 200 HP | Job | 117231
19.27.13 | Repairs of Booster Motors 200 HP to 250 HP | Job | 142362
19.27.14 | Repairs of Booster Motors 250 HP to 300 HP | Job | 164270
19.27.15 | Repairs of Booster Motors 300 HP to 350 HP | Job | 192293
19.27.16 | Repairs of Booster Motors 350 HP to 400 HP | Job | 224229

## 1. Boring1A
(Sub Estimate - 1A)
For HH-200, 225, 250
CONSTRUCTION OF 150MM X 100MM DIA & 125M DEEP TUBE WELL
S.No. | Description | Qty. |  | Unit | Rate | Amount
1 | Boring/drilling bore well of required dia for casing/strainer pipe, by suitable method prescribed in IS: 2800 (part I), including collecting samples from different strata, preparing and submitting strata chart/ bore log, including hire & running charges of all equipments, tools, plants & machineries required for the job, all complete as per direction of Engineer -in-charge, upto 150 metre depth below ground level. (All types of soil)
24.1.1.2 | (a) 350mm dia bore from G.L. to 30.0M | 30 | M | P/M | 532.4 | 15972
24.1.1.1 | (b) 300mm dia bore from 30.0 m to 60.0M | 30 | M | P/M | 486.8 | 14604
| (c) 300mm dia bore from 60M to 90.0M | 30 | M | P/M | 486.8 | 14604
24.2.1 | (d) 300mm dia bore from 90.0M to 150.0M | 35 | M | P/M | 567.9 | 19876.5
2A | Supplying, assembling, lowering and fixing in vertical position in bore well, unplasticized PVC (UPVC) medium well casing (CM) pipe of required dia, conforming to IS: 12818, including required hire and labour charges, fittings & accessories etc. all complete, for all depths, as per direction of Engineer -in-charge.
24.3.2 | (a) 150 mm nominal size dia | 30 | M | P/M | 660.1 | 19803
24.3.1 | (b) 100 mm nominal size dia | 60 | M | P/M | 546.1 | 32766
2B | Supplying, assembling, lowering and fixing in vertical position in bore well unplasticized PVC (UPVC) medium well screen (RMS) pipes with ribs, conforming to IS: 12818, including hire & labour charges, fittings & accessories etc. all complete, for all depths, as per direction of Engineer-in-charge.
24.4.1 | 100 mm nominal size dia | 30 | M | P/M | 573.1 | 17193
3 | Supplying the following fittings & fixing the same in position as per approved lowering assembly and strata chart including providing all equipments and welding the same on process of lowering the assay etc. all complete as per S/D of E/I.
24.13.2 | (a) 150 mm dia well cap | 1 | No. | Each | 210.7 | 210.7
24.14.2 | (b) 150 mm dia M.S. Clamp 1.6 M long (one Pair) | 1 | No. | Each | 1531.4 | 1531.4
Rate as per cost index @15.06% | (c) 150 mm dia center guide | 4 | Nos. | Each | 150 | 600
| (d) 100 mm dia center guide | 6 | Nos. | Each | 100 | 600
| (e) 150 mm x 100 mm dia 6mm wall thickness MS reducer | 1 | No. | Each | 500 | 500
24.15.1 | (f) 100mm dia & 6mm thick M.S. well shoe plug | 1 | No. | Each | 228.3 | 228.3
4a 24.8 | Gravel packing in tubewell construction in accordance with IS:4097,including providing gravel fine/ medium/ coarse, in required grading & sizes as per actual requirement, all complete as per direction of Engineer-in-charge. | 9 | M3 | P/M3 | 1343.2 | 12088.8
4b | Carriage of Pea Gravel from Dalbhumigarh to Patna (taken av distance 395+ 5km.) {8/5 (395 x 11.2+ 5 X 27.2) + 195.1}*1.01 | 9 | M3 | P/M3 | 10062.31 | 90560.79 | 7566.011 | 2496.3 | 7566.011
5 24.12 | Development of tube well in accordance with IS : 2800 (part I) and IS: 11189, to establish maximum rate of usable water yield without sand content (beyond permissible limit), with required capacity air compressor, running the compressor for required time till well is fully develo ped, measuring yield of well by "V" notch method or any other approved method, measuring static level & draw down etc. by step draw down method, collecting water sampl &getting tested in approved laboratory, disinfection of tubewell, all complete,including hire & labour charges of air compressor, tools & accessories etc., all as per requirement and direction of Engineer-in-charge. | 24 | Hrs. | P/H | 916.8 | 22003.2
6 Rate as per cost index @15.06% | Transportation of drilling plants, developing equipments & all other required tools and M/c by and suitable mechanical means including all cost of loading, unloading, placing at work site and back after completion of work as per S/D of E/I | 1 | No. | Each | 9200 | 9200
7 Rate as per cost index @15.06% | Supplying all materials and labours for arrangement for additional water required during the drilling period for 70 Hrs & site clearance & leveling etc. And providing the soap duster etc. to staff engaged in drilling etc. all complete work as per specification & direction of E.I. | 1 | No. | Each | 7000 | 7000
|  | TOTAL |  |  |  | 279341.69
[5 empty] | say | 279342

## O & M (F2) (hidden)
Sub Estimate No.- 8A
#REF!
Operation & maintance cost based on PHED compendium guidelines
Sl No | Description | Unit | Cost as DPR | As per yard stick publised in compendium page 203-205 dept(2001) | % annual Depreciation | Base year (After Trial ) cost | Quantity | Rate | Total Amount
1 | 2 | 3 | 4 | 5 |  | 6 | 7 | 8 | 9
Formula |  | Rt=[ 1+(r/100)]^t x (Base year O&M cost) |  | t= | 5 | Years | Proposal is for 5 years O & M
Total House Connection in Scheme |  |  |  | 150 |  | Total Population Surveyed |  | 750
A | Honorarium of pump operator 1 Nos. for 12 Month | per month |  |  |  |  | 12 | 4000 | 48000
| Sub Total(A) | [7 empty] | 48000 | (Final Rate)
B | Infrastruture Maintance
Formula 2 (With 5 years interval and constant component wise annual variable component wise depreciation rate:
| Masonary Chamber | per year | 15314.076 | 1% | 2 | 153.1408 | 169.0798 |  | 169.0798
| Steel Staging | per year | 734253.84 | 0.5% | 1.5 | 3671.2692 | 3954.9996 |  | 3954.9996
| Distrubution line | per year | #REF! | 0.25% | 2 | #REF! | #REF! |  | #REF! |  | Masonary chamber+distribution+waste disposal pit
| House conection | per year | 2623 | 1% | 5 | 26.23 | 33.4769 |  | 33.4769
| Chloronation/WTP | per year | 24775.404 | 0.5% | 2.5 | 123.877 | 140.1555 |  | 140.1555
[5 empty] | Sub Total | #REF! | #REF! |  | #REF! | civil work
| Pump Motar | per year | 110628 | 2.5% | 5 | 2765.7 | 3529.8119 |  | 3529.8119 | Elect. & Mech.
| Sub Total B | [7 empty] | #REF!
|  |  | #REF! |  | Sub Total B= | #REF! | #REF! |  | #REF!
C | Cost of Chemical For 2PPM& 30% CL Solution
| (Total Population*81*2/1000000)*(100/30)*365 | Per litre |  |  |  |  | 147.825 | 150 | 22173.75 |  |  | 16984.35 | 3057.183 | 13927.167 | 13927.167
| Sub Total C | [7 empty] | 22173.75
D | Cleaning of OHT including at an interval of 6 months and regular cleaning of campus | Job |  |  |  |  | 1 | 1000 | 1000
| Sub Total(D) | [7 empty] | 1000
[9 empty] | 23173.75 | (Including 18% GST)
| Total A+B+C+D | [7 empty] | #REF! |  | 128419.738
E | Provision for water charges, 18% GST, 15% CPOH and 1 % Labour Cess (multiplying factor 1.4226 of Base Rate)=1.4226*(A+B+C+D) | [7 empty] | #REF!
| Operation & Maintenance for One Year | [7 empty] | #REF!
F | Operation & Maintenance for Five Year | [7 empty] | #REF!
Executive Engineer
P.H. Division, Hajipur

## 2.Chamber TW
(Sub Estimate - 2)
Chamber for TW
Supplying materials, labours and constructing chamber of following dimension having 250mm thick wall in C.M. (1:4) in cluding 12mm C.P. (1:3) with punning inside, R.C.C. cover slab with C.I. Surface box , 20mm dia foot rest at 150mm interval 10mm dia lifting ring etc. all complete.
| SIZE | 1 | M | x | 1 | M | x | 0.75 | M deep
S.O.R. No. | Particulars | No. | L | W | H | Qty. |  | Unit | Rate | Amount
1 | Earth work in excavation | 1 | 1.75 | 1.75 | 1 | 3.0625 | M3 | P/M3 | 360.7 | 1104.6437 | 1104.6437 | 0 | 360.7
2.8 | [11 empty] | 0
2 | Sand filling | 1 | 1.75 | 1.75 | 0.075 | 0.22969 | M3 | P/M3 | 287.3 | 65.9892 | 65.9892 | 0 | 287.3
2.28 | [11 empty] | 0
3 | Brick flat soling | 1 | 1.75 | 1.75 |  | 3.0625 | M2 | P/M2 | 283.3 | 867.6063 | 867.6063 | 0 | 283.3
11.72 | [11 empty] | 0
4 | P.C.C. (1:2:4) in foundation | 1 | 1.75 | 1.75 | 0.1 | 0.30625 | M3 |  |  |  |  | 0
4.1.3 | [11 empty] | 0
[6 empty] | 0.30625 | M3 | P/M3 | 3998.1 | 1224.4181 | 1224.4181 | 0 | 3998.1
5 | B/Work in (1:4) C.M. | 2 | 2.5 | 0.25 | 0.75 | 0.9375 | M3 | P/M3 | 5017.9 | 4704.2812 | 4704.2812 | 0 | 5017.9
6.1.12/1 | [11 empty] | 0
6 | R.C.C. Cover slab(1:1.5:3) | 1 | 1.5 | 1.5 | 0.15 | 0.3375 | M3 | P/M3 | 5670 | 1913.625 | 1913.625 | 0 | 5670 | 0.338 | 0.3042 | 2200 | 669.24
5.2.2 & 5.9.3 | [11 empty] | 0 |  |  | 0.28342 | 1000 | 283.42
| shuttering | 2 | 1.5 | 1.5 | 0.15 | 0.9 | M2 | P/M2 | 437.5 | 393.75 | 1378.125 | -984.375 | 437.5 |  | 98.8065 | 1000 | 117.6
7 | C.P. (1:3) with 5% Cico & neat cement | [10 empty] | 0 |  |  |  |  | 1070.26
13.17.1 | Internal face | 2 | 1 | 1 | 1 | 4 | M2 |  |  |  |  | 0
| Bed surface | 1 | 1 | 1 |  | 1 | M2 |  |  |  |  | 0
+13.36.1 | [5 empty] | 5 | M2 | P/M2 | 203.6 | 1018 | 1063 | -45 | 212.6
0
8 | C.P. (1:4) out side of wall | 2 | 1.5 | 1.5 | 0.75 | 0.9 | M2 | P/M2 | 152.9 | 137.61 | 688.05 | -550.44 | 152.9
. 13.11.2 | [11 empty] | 0
9 | 8mm dia T.S. Rod | [10 empty] | 0
5.22.7A | [11 empty] | 0
|  | 0.3375 | M3 x | 70 | Kg/ M3 | 23.625 | Kg. | P/Kg | 94.5 | 2232.5625 | 2232.5625 | 0 | 94.5
10 | Lifting Ring of 10mm dia Rod |  |  |  |  | 4 | No. | Each | 45 | 180 | 240 | -60 | 60
[9 empty] | Total | 13842.4861 | 13977.4861 | -135
11 | Carriage of materials= 5% of cost of Items. | [8 empty] | 692.1243 | 698.8743 | -6.75
| Total | [8 empty] | 14534.6104 | 14676.3604 | -141.75
| Say | [8 empty] | 14535 | 15463 | -928
Executive Engineer
Begusarai

## 1.Boring.DT.1B
(Sub Estimate - 1B)
CONSTRUCTION OF 150MM DIA & 90 M DEEP DRILLED TUBE WELL.
S.No. | Description | Qty. |  | Unit | Rate | Amount
1 | Boring/drilling bore well of required dia for casing/strainer pipe, by suitable method prescribed in IS: 2800 (part I), including collecting samples from different strata, preparing and submitting strata chart/ bore log, including hire & running charges of all equipments, tools, plants & machineries required for the job, all complete as per direction of Engineer -in-charge, upto 90 metre depth below ground level. Rocky strata including Boulders).
24.1.2.1 | (b) 300mm dia bore from 00.0 m to 60.0M | 90 | M | P/M | 1118.6 | 100674
2 | Supplying, assembling, lowering and fixing in vertical position in bore well, unplasticized PVC (UPVC) medium well casing (CM) pipe of required dia, conforming to IS: 12818, including required hire and labour charges, fittings & accessories etc. all complete, for all depths, as per direction of Engineer -in-charge.
24.3.2 | (a) 150 mm nominal size dia | 36 | M | P/M | 660.1 | 23763.6
3 | Supplying the following fittings & fixing the same in position as per approved lowering assembly and strata chart including providing all equipments and welding the same on process of lowering the assay etc. all complete as per S/D of E/I.
24.13.2 | (a) 150 mm dia well cap | 1 | No. | Each | 210.7 | 210.7
24.14.2 | (b) 150 mm dia M.S. Clamp 1.6 M long (one Pair) | 1 | No. | Each | 1531.4 | 1531.4
5 24.12 | Development of tube well in accordance with IS : 2800 (part I) and IS: 11189, to establish maximum rate of usable water yield without sand content (beyond permissible limit), with required capacity air compressor, running the compressor for required time till well is fully develo ped, measuring yield of well by "V" notch method or any other approved method, measuring static level & draw down etc. by step draw down method, collecting water sampl &getting tested in approved laboratory, disinfection of tubewell, all complete,including hire & labour charges of air compressor, tools & accessories etc., all as per requirement and direction of Engineer-in-charge. | 24 | Hrs. | Each | 916.8 | 22003.2
6 | Transportation of drilling plants, developing equipments & all other required tools and M/c by and suitable mechanical means including all cost of loading, unloading, placing at work site and back after completion of work as per S/D of E/I | 1 | No. | Each | 12600 | 12600
7 | Supplying all materials and labours for arrangement for additional water required during the drilling period for 70 Hrs & site clearance & leveling etc. And providing the soap duster etc. to staff engaged in drilling etc. all complete work as per specification & direction of E.I. | 1 | No. | Each | 10200 | 10200 | 8500
| TOTAL |  |  |  |  | 170982.9
| Say |  |  |  |  | 170983
JE | Assistant Engineer |  |  | Executive Engineer
P.H. Division, Begusarai

## 3a HP moter new
Sub Est. No. 3a
Estimate for supply, installation & commissioning of single phase 3 H.P submersible motor pump set with all accessories including extension of L.T. line from nearest source up-to pumping station.
Sl. No. | Particulars | Quantity |  | Unit | Rate | Amount
1 | 2 | 3 |  | 4 | 5 | 6 |  | 1.1506
1 | Supply Installation, commissioning and testing of single phase 3 H.P. submersible pump set having discharging capacity 3.35 lps at a total head of 35 meter(approx) of KSB/ Kirloskar or equivalent make with all accessories & fittings etc including loading unloading and transportation of the pump set to the work site with all required labour, materials, tools and tackles installation, testing & commissioning as per standards specifications and direction of E/I. | 1 | (one) job | p/job | 50250 | 50250
| (i) 50 mm dia x 3 mtrs long medium class G.I column pipe both end thread and one end socketed- 6(six)nos | [5 empty] | 42700 | 49130.62
| (ii) 1x3x2.5 mm2 flat copper conductor submersible cable -40 (forty) mtrs. | [6 empty] | 0
| (iii) 50 mm dia union socket- 1(one) no. | [6 empty] | 0
| (iv) 65 mm dia x 250 mm long G.I. nipple- 1 (one) no. | [6 empty] | 0
| (v) 50 mm dia G.I Elbow—1(One) no. | [6 empty] | 0
| (vi) 50 mm dia M.S. clamps—2(Two) Pairs. | [6 empty] | 0
| (vii) 50 mmx 250 mm long G.I nipple- 1(One) no. | [6 empty] | 0
| (viii) Tube well cap for T/Well – 1(one) no. | [6 empty] | 0
| (ix) 50 mm dia x 65 mm dia reducer socket –1(one) no. | [6 empty] | 0
2 | Supply Installation, commissioning and testing of floor mounted outdoor type L.T feeder pillar single phase starter controll pannel operated on 220 V, 3 phase , 50 c/s for 3 HP Submersible pump set made of MS sheet (minimum 2 mm thick) duly spray power coated painting with following accessories made of M.S sheet (minimum 2mm thick) duly spray powder coated painting with following accessories | [6 empty] | 0 | Supply Installation, commissioning and testing of floor mounted outdoor type L.T feeder pillar single phase starter controll pannel operated on 220 V, 3 phase , 50 c/s for 3 HP Submersible pump set made of MS sheet (minimum 2 mm thick) duly spray power coated painting with following accessories made of M.S sheet (minimum 2mm thick) duly spray powder coated painting with following accessories
| (i) 90-220 V range single phase7. 5 KVA automatic voltage stabilizer make- Sen & Pandit/ Vertex/ISI marked If any. 1 No. | [6 empty] | 0
| (ii) Suitable single phase starter control panel for above motor of BCH /L&Tmake – 1(one) no. | 1 | (one) job | p/job | 49000 | 49000 |  | 0
3 | Supplying & fitting 2.5 mm2 copper service cable from power point from nearest source up-to pumping station. | 20 | mtrs | P/Mt | 130 | 2600 | 45500 | 52352.3
4 | Providing all materials and labour required for doing earthing station with G.I earth pipe of 40 mm dia x 4.5 mtrs 20fts. long G.I pipe including accessories excavation of earth , providing masonry enclosure with cover plate having locking arrangement and watering pipe etc.with salt, charcoal,etc.as per IE & IS specification. | 1 | job | p/job | 3150 | 3150 | 130 | 149.578
[5 empty] | Total Rs. | 105000 | 2803 | 3225.1318
| Junior Engineer Assistant Engineer |  |  |  | Executive Engineer
Begusarai

## 3b 2HP moter
Sub Est. No. 3b
Estimate for supply, installation & commissioning of single phase 2 H.P submersible motor pump set with all accessories including extension of L.T. line from nearest source up-to pumping station.
Sl. No. | Particulars | Quantity |  | Unit | Rate | Amount
1 | 2 | 3 |  | 4 | 5 | 6 |  | 1.1506
1 | Supply Installation, commissioning and testing of single phase 2 H.P. submersible pump set having discharging capacity 2.25 lps at a total head of 35 meter(approx) of KSB/ Kirloskar or equivalent make with all accessories & fittings etc including loading unloading and transportation of the pump set to the work site with all required labour, materials, tools and tackles installation, testing & commissioning as per standards specifications and direction of E/I. | 1 | (one) job | p/job | 30500 | 30500
| (i) 50 mm dia x 3 mtrs long medium class G.I column pipe both end thread and one end socketed- 6(six)nos | [5 empty] | 42700 | 49130.62
| (ii) 1x3x2.5 mm2 flat copper conductor submersible cable -40 (forty) mtrs. | [6 empty] | 0
| (iii) 50 mm dia union socket- 1(one) no. | [6 empty] | 0
| (iv) 65 mm dia x 250 mm long G.I. nipple- 1 (one) no. | [6 empty] | 0
| (v) 50 mm dia G.I Elbow—1(One) no. | [6 empty] | 0
| (vi) 50 mm dia M.S. clamps—2(Two) Pairs. | [6 empty] | 0
| (vii) 50 mmx 250 mm long G.I nipple- 1(One) no. | [6 empty] | 0
| (viii) Tube well cap for T/Well – 1(one) no. | [6 empty] | 0
| (ix) 50 mm dia x 65 mm dia reducer socket –1(one) no. | [6 empty] | 0
2 | Supply Installation, commissioning and testing of floor mounted outdoor type L.T feeder pillar single phase starter controll pannel operated on 220 V, 3 phase , 50 c/s for 3 HP Submersible pump set made of MS sheet (minimum 2 mm thick) duly spray power coated painting with following accessories made of M.S sheet (minimum 2mm thick) duly spray powder coated painting with following accessories | [6 empty] | 0 | Supply Installation, commissioning and testing of floor mounted outdoor type L.T feeder pillar single phase starter controll pannel operated on 220 V, 3 phase , 50 c/s for 3 HP Submersible pump set made of MS sheet (minimum 2 mm thick) duly spray power coated painting with following accessories made of M.S sheet (minimum 2mm thick) duly spray powder coated painting with following accessories
| (i) 90-220 V range single phase7. 5 KVA automatic voltage stabilizer make- Sen & Pandit/ Vertex/ISI marked If any. 1 No. | [6 empty] | 0
| (ii) Suitable single phase starter control panel for above motor of BCH /L&Tmake – 1(one) no. | 1 | (one) job | p/job | 28500 | 28500 |  | 0
3 | Supplying & fitting 2.5 mm2 copper service cable from power point from nearest source up-to pumping station. | 20 | mtrs | P/Mt | 130 | 2600 | 45500 | 52352.3
4 | Providing all materials and labour required for doing earthing station with G.I earth pipe of 40 mm dia x 4.5 mtrs 20fts. long G.I pipe including accessories excavation of earth , providing masonry enclosure with cover plate having locking arrangement and watering pipe etc.with salt, charcoal,etc.as per IE & IS specification. | 1 | job | p/job | 3150 | 3150 | 130 | 149.578
[5 empty] | Total Rs. | 64750 | 2803 | 3225.1318
| Junior Engineer Assistant Engineer |  |  |  | Executive Engineer
Begusarai

## 3c 5HP moter
Sub Estimate-3C
Name of work. Supplying, Installation, commissioning & testing of 5 HP 3 phase submersible pump set with all accessories including light wiring, power wiring and extension of over head L.T. line from nearest point of electric line up to pump chamber etc. at electric based WIMC Scheme
SI no | Particulars | Quantity |  | unit | rate | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7
A | Submersible ump set and other accessories
1 | Supply of 3 phase 50 C/sec 2900 rpm submersible pump set with following accessorels including laoding unloading including transportation of the pump set to destination with all required labour etc. | 1 | set | p/set | 102500 | 102500
(i) Submersible pump set having discharging capacity 11 m3/hr at a total head of 65 meter (approx) of KSB or as per departmental approved make-1 set
(ii) 50 mm dia x 3 mtrs long medium class Gl column ppe both end thread and one end socketed 36 meter (each length of 3 meter)
(iii) (1x3x2.5 mm² flat copper conductor submersible cable 90 (Fifty) meter
(iv)50 mm dia M.S. clamps with nut bulls & washer 1/2"x2.5 "two pair
(v) 50 mm dia ISI marked heavy duty GM wheel valve-1 No.
(vi) 50 dia Si marked heavy duty GM relux valve-1 No.
(vii) Fully automatic alr break control pannel stater consisting 17.5 HP DOL starter having contator with coll voltage 380 +-10%V & suitable thermal relay range-1 No.
(vii) Safety steel wire rope 4 mm2 size-58 meter
(ix) Pressure gauge (0 to 7.5 kg/cm2) 11 nos
B | Service Cable, Pwer wiring and Light wiring
3 | Kit-kat Supplying & fixing of 63 Amp kit kat fuse-3 nos Eted on a appropriate wooden board including drilling holes in board, making connection etc. as required make anchonhavels/ISI marked if any | 3 | No. | Each | 374 | 1122
4 | Service Cable & Power wining Supplying & fitting of 2x6 mm2 X 3 Core copper cable for service cable & power wiring from power point outside the pump chamber through Kit-kal to main switch to voltage stabilizer to starter control panel and through all electrical equipment | 60 | M | P/M | 304 | 18240
5 | Light wiring-Wiring for light point with 1.5 mm2 FR PVC insulated copper conductor signel core cable in surface/frocessed PVC conduct with plano type switch, phenolic taminated sheet, suitable size PVC/GI box etc as required | 3 | pt | each point | 681 | 2043
6 | Supplying and fixing 2 pin, 6 amps ceiling rose on junction boxPVC box including connection etc. os requirede | 1 | No. | each | 42 | 42
7 | Supplying and fixing Batten/angle holder (One outside the pump chamber and one on junction box/PVC box inside the pump chamber) | 2 | No. | each | 46 | 92
8 | LED Bulb Supplying and fitting 9 W LED bulb inside the paump chamber make Syska/Phlips/Havells/Bajaj/SI marked if any | 1 | No. | each | 150 | 150
9 | LED Bulb Supplying and fitting 20 W LED bulb inside the paump chamber make Syska/Phlips/Havelis/Bajaj/SI marked if any | 1 | No. | each | 450 | 450
C | Earthing
10 | Supplying all materials and labours for doing earthing such 10 as 40 mm dia and 4.5 mr. length M.S. pipe, charcol salt etc. | 1 | Job | p/job | 5125 | 5125
E | Rubber matting sheet
11 | Supplying and fitting of rubber matting sheet size 3 ft. x 2 ft for preventing from the electric shock during operating the motor | 1 | job | p/job | 2200 | 2200
F | Extension of over head single phase LT Line (0.16 Km) from nearest power point up to pump chamber by supplying all labour tools and tackles including loading, unloading with T&P and transposition cost with following materials.
12 | Supplying and fitting of LT Ploe top bracket | 4 | no. | each | 253 | 1012
13 | Supplying and laying of 10 mm³ 2 core Aluminium conduxtor PVC insulated around cable will be laid in air or under the ground from availability of single phase line up to pump chamber
132976
| say |  |  |  |  | 132980
Executive Engineer P.H Division, Begusarai

## 4a. 3HP Starter
Sub Estimate - 04A
Name of Work :- Providing & Fixing BIS approved 3 HP submersible motor starter all complete as per direction of engineer in charge.
Sl. No. | Particulars | Quantity |  | Unit | Rate | Amount
1 | 2 | 3 |  | 4 | 5 | 6
1 | Supplying and fixing of top quality 3 HP motor starter. (As per rate given in GeM portal; copy attached) | 1 | No | Each | 5200 | 5200
[5 empty] | Total Rs. | 5200
Junior Engineer Assistant Engineer |  |  |  |  | Executive Engineer
Begusarai

## 4b. 2HP Starter
Sub Estimate - 04B
Name of Work :- Providing & Fixing BIS approved 2 HP submersible motor starter all complete as per direction of engineer in charge.
Sl. No. | Particulars | Quantity |  | Unit | Rate | Amount
1 | 2 | 3 |  | 4 | 5 | 6
1 | Supplying and fixing of top quality 3 HP motor starter. (As per rate given in GeM portal; copy attached) | 1 | No | Each | 4500 | 4500
[5 empty] | Total Rs. | 4500
Junior Engineer Assistant Engineer |  |  |  |  | Executive Engineer
Begusarai

## 4c. 5HP starter
Sub Estimate - 04C
Name of Work :- Providing & Fixing BIS approved 2 HP submersible motor starter all complete as per direction of engineer in charge.
Sl. No. | Particulars | Quantity |  | Unit | Rate | Amount
1 | 2 | 3 |  | 4 | 5 | 6
1 | Supplying and fixing of top quality 3 HP motor starter. (As per rate given in GeM portal; copy attached) | 1 | No | Each | 6000 | 6000
[5 empty] | Total Rs. | 6000
Junior Engineer Assistant Engineer |  |  |  |  | Executive Engineer
Begusarai

## 5. New Stablizer
Sub Estimate - 05a
90-220 V range single phase 7. 5 KVA automatic voltage stabilizer make- Sen & Pandit/ Vertex/ISI marke.
Sl. No. | Particulars | Quantity |  | Unit | Rate | Amount
1 | 2 | 3 |  | 4 | 5 | 6
| (i) 90-220 V range single phase7. 5 KVA automatic voltage stabilizer make- Sen & Pandit/ Vertex/ISI marked If any. 1 No. | 1 | (one) job | p/job | 25000 | 25000
[5 empty] | Total Rs. | 25000
| J E Assistant Engineer |  |  |  | Executive Engineer
Begusarai

## stablizer 5 kva
Sub Estimate - 05B
90-220 V range single phase 5.0 KVA automatic voltage stabilizer make- Sen & Pandit/ Vertex/ISI marke.
Sl. No. | Particulars | Quantity |  | Unit | Rate | Amount
1 | 2 | 3 |  | 4 | 5 | 6
| (i) 90-220 V range single phase 5.0 KVA automatic voltage stabilizer make- Sen & Pandit/ Vertex/ISI marked If any. 1 No. | 1 | (one) job | p/job | 20000 | 20000
[5 empty] | Total Rs. | 20000
| J E Assistant Engineer |  |  |  | Executive Engineer
Begusarai

## 6A
Sub Est. No. 06A
ANALYSIS OF 100 METER WATER SUPPLY DISTRIBUTION SYSTEM FOR 90 MM DIA HDPE PIPELINE. | [10 empty] | 2
S.N. | Particulars |  |  |  |  | Quantity |  | Unit | Rate | Amount
1A 2.8 | Earthwork in excavation over areas (exceeding 30 cm in depth 1.5 in width as well as 10 sqm on plan) including disposal of excavated earth lead upto 50m and lift upto 1.5m, disposal earth to be levelled and neatly dressed. | [6 empty] | P/M3 | 360.7 | 12498.255
| 90mm dia Pipe | 100 | 0.3 | 1.1 | = | 33
| 75mm dia Pipe | 0 | 0.3 | 1.1 | = | 0
| 63mm dia Pipe | 0 | 0.3 | 1.1 | = | 0
| 50mm dia Pipe | 0 | 0.3 | 1.1 | = | 0
| 40mm dia Pipe | 0 | 0.3 | 1.1 | = | 0
|  | 100 |  |  |  | 33 | M3
| Add 5% extra for fittings = |  |  |  |  | 1.65 | M3
[6 empty] | 34.65 | M3
1B 2.26 | Filling available excavated earth (excluding rock) in trenches, plinth, sides of foundations etc. in layers not exceeding 20cm in depth, consolidating each deposited layer by ramming and watering, lead up to 50 m and lift upto 1.5 m. |  |  |  |  | 33.957 | M3 | P/M3 | 123.9 | 4207.2723
2 15.2.1 | Demolishing cement concrete manually/ by mechanical means including disposal of material within 50 metres lead as per direction of Engineer - in - charge. | [5 empty] | M3 | P/M3 | 970.9 | 1310.715
1:3:6 or richer mix
| 1 | 30 | 0.3 | 0.15 | = | 1.35
1.35
3 4.1.3 | Providing and laying in position cement concrete of specified grade excluding the cost of centering and shuttering all work upto plinth
| 1:2:4 (1 cement: 2 coarse sand : 4 graded stone aggregate 20mm nominal size) |  |  |  |  | 1.35 | M3 | P/M3 | 3998.1 | 5397.435
4 | Carriage of materials
| (a) Coarse sand (44 Km pucca +1 KM Kacha Carriage) |  |  |  |  | 0.621 | M3 | P/M3 | 1160.62 | 720.745
| (b) Stone Chips(195 Km pucca + 5KM Kacha Carriage) |  |  |  |  | 1.242 | M3 | P/M3 | 4291.17 | 5329.6331
5 | Providing and laying High Density Polyethyene pipe (HDPE pipe) of 20 mm to 225 mm OD and pressure 6.0 Kg/cm2 and 10 Kg/cm2 sutable for water supply which is available in all standard, like ISI-4984/1995 and various grades like PE-80, PE-100 including required specials. Rates are inclusive of , all taxes and duties (Exise duty @12.50% & CST @ 2% against Form 'C'), labour cess, contractor profit and overhead charges all complete as per direction of Engineer-in-charge. | [9 empty] | 43796 | #REF! | #REF! | #REF! | #REF! | #REF!
HDPE pipe of materials grade PE100- PN10 (dia in mm)
| 90mm dia Pipe |  |  |  |  | 100 | M | P/M | 437.96 | 43796 |  | 0.65
| 75mm dia Pipe |  |  |  |  | 0 | M | P/M | 306.31 | 0
| 63mm dia Pipe |  |  |  |  | 0 | M | P/M | 218.62 | 0
HDPE pipe of materials grade PE100- PN8 (dia in mm)
| 50mm dia Pipe |  |  |  |  | 0 | M | P/M | 116.25 | 0
| 40mm dia Pipe |  |  |  |  | 0 | M | P/M | 76.53 | 0
| Providing all materials labours tools, fittings, specials and tackles for fitting, jointing and connecting HDPE pipes. | [14 empty] | 115.1
| 5% of the cost of HDPE Pipe | [8 empty] | 2189.8 | [5 empty] | 144.1 | 25.1955
6 | Providing and fixing brass gate valve with C.I. wheel of approved quality (screwed end).
| 80mm dia Pipe |  |  |  |  | 0 | Nos. | Each | 2227.6 | 0
| 65mm dia Pipe |  |  |  |  | 0 | Nos. | Each | 1490.7 | 0
| 50mm dia Pipe |  |  |  |  | 0 | Nos. | Each | 878.2 | 0
| 40mm dia Pipe |  |  |  |  | 0 | Nos. | Each | 707.3 | 0
7 18.33 | Constructing masonry Chamber 60x60x75 cm inside, in brick work in cement mortar 1:4 (1 cement : 4 coarse sand) for sluice valve,with C.I. surface box 100mm top diameter, 160 mm bottom diameter and 180 mm deep ( inside) with chained lid and RCC top slab 1:2:4 mix (1 cement : 2 coarse sand : 4 graded stone aggregate 20mm nominal size) , necessary excavation, foundation concrete 1:5:10(1 cement : 5 fine sand : 10 graded stone aggregate 40 mm nominalsize) and inside plastering with cement mortar 1:3 (1 cement : 3coarse sand) 12 mm thick, finished with a floating coat of neat cement complete as per standard specifications & direction of E/I. |  |  |  |  | 0 | Nos. | Each | 7210.6 | 0
| Work for additional depth | [5 empty] | M3 | P/M3 | 5017.9 | 0
Brick work (1:4) in foundation
| 2 | 1.1 | 0.25 | 0.35 | 0.1925
| 2 | 0.6 | 0.25 | 0.35 | 0.105
[5 empty] | 0.2975 | 0
Plaster (1:3)
| 8 | 1.1 |  | 0.35 | 3.08 | 0 | M2 | P/M2 | 164.3 | 0
| Carriage 10% of item 7 | [8 empty] | 0
8 11.72 | Providing designation of 100A Brick flat Soling joints filled with local sand including cost of watering, taxes & royalty all complete as per specification & direction of E/I.
|  | 0 | 0.45 | 0.45 |  | 0 | M2 | P/M2 | 283.3 | 0
[9 empty] | TOTAL | 75449.8555
[9 empty] | p/km | 754.4986
[9 empty] | Say | 75450
| JE |  | Assistant Engineer |  |  |  |  | Executive Engineer
P.H.Division, Begusarai

## 6B
Sub Est. No. 06 B
ANALYSIS OF 100 METER WATER SUPPLY DISTRIBUTION SYSTEM FOR 75 MM DIA HDPE PIPELINE. | [10 empty] | 2
S.N. | Particulars |  |  |  |  | Quantity |  | Unit | Rate | Amount
1A 2.8 | Earthwork in excavation over areas (exceeding 30 cm in depth 1.5 in width as well as 10 sqm on plan) including disposal of excavated earth lead upto 50m and lift upto 1.5m, disposal earth to be levelled and neatly dressed. | [6 empty] | P/M3 | 360.7 | 12498.255
| 90mm dia Pipe | 0 | 0.3 | 1.1 | = | 0
| 75mm dia Pipe | 100 | 0.3 | 1.1 | = | 33
| 63mm dia Pipe | 0 | 0.3 | 1.1 | = | 0
| 50mm dia Pipe | 0 | 0.3 | 1.1 | = | 0
| 40mm dia Pipe | 0 | 0.3 | 1.1 | = | 0
|  | 100 |  |  |  | 33 | M3
| Add 5% extra for fittings = |  |  |  |  | 1.65 | M3
[6 empty] | 34.65 | M3
1B 2.26 | Filling available excavated earth (excluding rock) in trenches, plinth, sides of foundations etc. in layers not exceeding 20cm in depth, consolidating each deposited layer by ramming and watering, lead up to 50 m and lift upto 1.5 m. |  |  |  |  | 33.957 | M3 | P/M3 | 123.9 | 4207.2723
2 15.2.1 | Demolishing cement concrete manually/ by mechanical means including disposal of material within 50 metres lead as per direction of Engineer - in - charge. | [5 empty] | M3 | P/M3 | 970.9 | 1310.715
1:3:6 or richer mix
| 1 | 30 | 0.3 | 0.15 | = | 1.35
1.35
3 4.1.3 | Providing and laying in position cement concrete of specified grade excluding the cost of centering and shuttering all work upto plinth
| 1:2:4 (1 cement: 2 coarse sand : 4 graded stone aggregate 20mm nominal size) |  |  |  |  | 1.35 | M3 | P/M3 | 3998.1 | 5397.435
4 | Carriage of materials
| (a) Coarse sand (44 Km pucca +1 KM Kacha Carriage) |  |  |  |  | 0.621 | M3 | P/M3 | 1160.62 | 720.745
| (b) Stone Chips(195 Km pucca + 5KM Kacha Carriage) |  |  |  |  | 1.242 | M3 | P/M3 | 4291.17 | 5329.6331
5 | Providing and laying High Density Polyethyene pipe (HDPE pipe) of 20 mm to 225 mm OD and pressure 6.0 Kg/cm2 and 10 Kg/cm2 sutable for water supply which is available in all standard, like ISI-4984/1995 and various grades like PE-80, PE-100 including required specials. Rates are inclusive of , all taxes and duties (Exise duty @12.50% & CST @ 2% against Form 'C'), labour cess, contractor profit and overhead charges all complete as per direction of Engineer-in-charge. | [9 empty] | 30631 | #REF! | #REF! | #REF! | #REF! | #REF!
HDPE pipe of materials grade PE100- PN10 (dia in mm)
| 90mm dia Pipe |  |  |  |  | 0 | M | P/M | 437.96 | 0 |  | 0.65
| 75mm dia Pipe |  |  |  |  | 100 | M | P/M | 306.31 | 30631
| 63mm dia Pipe |  |  |  |  | 0 | M | P/M | 218.62 | 0
HDPE pipe of materials grade PE100- PN8 (dia in mm)
| 50mm dia Pipe |  |  |  |  | 0 | M | P/M | 116.25 | 0
| 40mm dia Pipe |  |  |  |  | 0 | M | P/M | 76.53 | 0
| Providing all materials labours tools, fittings, specials and tackles for fitting, jointing and connecting HDPE pipes. | [14 empty] | 115.1
| 5% of the cost of HDPE Pipe | [8 empty] | 1531.55 | [5 empty] | 144.1 | 25.1955
6 | Providing and fixing brass gate valve with C.I. wheel of approved quality (screwed end).
| 80mm dia Pipe |  |  |  |  | 0 | Nos. | Each | 2227.6 | 0
| 65mm dia Pipe |  |  |  |  | 0 | Nos. | Each | 1490.7 | 0
| 50mm dia Pipe |  |  |  |  | 0 | Nos. | Each | 878.2 | 0
| 40mm dia Pipe |  |  |  |  | 0 | Nos. | Each | 707.3 | 0
7 18.33 | Constructing masonry Chamber 60x60x75 cm inside, in brick work in cement mortar 1:4 (1 cement : 4 coarse sand) for sluice valve,with C.I. surface box 100mm top diameter, 160 mm bottom diameter and 180 mm deep ( inside) with chained lid and RCC top slab 1:2:4 mix (1 cement : 2 coarse sand : 4 graded stone aggregate 20mm nominal size) , necessary excavation, foundation concrete 1:5:10(1 cement : 5 fine sand : 10 graded stone aggregate 40 mm nominalsize) and inside plastering with cement mortar 1:3 (1 cement : 3coarse sand) 12 mm thick, finished with a floating coat of neat cement complete as per standard specifications & direction of E/I. |  |  |  |  | 0 | Nos. | Each | 7210.6 | 0
| Work for additional depth | [5 empty] | M3 | P/M3 | 5017.9 | 0
Brick work (1:4) in foundation
| 2 | 1.1 | 0.25 | 0.35 | 0.1925
| 2 | 0.6 | 0.25 | 0.35 | 0.105
[5 empty] | 0.2975 | 0
Plaster (1:3)
| 8 | 1.1 |  | 0.35 | 3.08 | 0 | M2 | P/M2 | 164.3 | 0
| Carriage 10% of item 7 | [8 empty] | 0
8 11.72 | Providing designation of 100A Brick flat Soling joints filled with local sand including cost of watering, taxes & royalty all complete as per specification & direction of E/I.
|  | 0 | 0.45 | 0.45 |  | 0 | M2 | P/M2 | 283.3 | 0
[9 empty] | TOTAL | 61626.6055
[9 empty] | Say | 61627
[9 empty] | Rate per meter | 616.27
| JE |  | Assistant Engineer |  |  |  |  | Executive Engineer
P.H.Division, Begusarai

## 6C
Sub Est. No. 06 C
ANALYSIS OF 100 METER WATER SUPPLY DISTRIBUTION SYSTEM FOR 63 MM DIA HDPE PIPELINE. | [10 empty] | 2
S.N. | Particulars |  |  |  |  | Quantity |  | Unit | Rate | Amount
1A 2.8 | Earthwork in excavation over areas (exceeding 30 cm in depth 1.5 in width as well as 10 sqm on plan) including disposal of excavated earth lead upto 50m and lift upto 1.5m, disposal earth to be levelled and neatly dressed. | [6 empty] | P/M3 | 360.7 | 12498.255
| 90mm dia Pipe | 0 | 0.3 | 1.1 | = | 0
| 75mm dia Pipe | 0 | 0.3 | 1.1 | = | 0
| 63mm dia Pipe | 100 | 0.3 | 1.1 | = | 33
| 50mm dia Pipe | 0 | 0.3 | 1.1 | = | 0
| 40mm dia Pipe | 0 | 0.3 | 1.1 | = | 0
|  | 100 |  |  |  | 33 | M3
| Add 5% extra for fittings = |  |  |  |  | 1.65 | M3
[6 empty] | 34.65 | M3
1B 2.26 | Filling available excavated earth (excluding rock) in trenches, plinth, sides of foundations etc. in layers not exceeding 20cm in depth, consolidating each deposited layer by ramming and watering, lead up to 50 m and lift upto 1.5 m. |  |  |  |  | 33.957 | M3 | P/M3 | 123.9 | 4207.2723
2 15.2.1 | Demolishing cement concrete manually/ by mechanical means including disposal of material within 50 metres lead as per direction of Engineer - in - charge. | [5 empty] | M3 | P/M3 | 970.9 | 1310.715
1:3:6 or richer mix
| 1 | 30 | 0.3 | 0.15 | = | 1.35
1.35
3 4.1.3 | Providing and laying in position cement concrete of specified grade excluding the cost of centering and shuttering all work upto plinth
| 1:2:4 (1 cement: 2 coarse sand : 4 graded stone aggregate 20mm nominal size) |  |  |  |  | 1.35 | M3 | P/M3 | 3998.1 | 5397.435
4 | Carriage of materials
| (a) Coarse sand (44 Km pucca +1 KM Kacha Carriage) |  |  |  |  | 0.621 | M3 | P/M3 | 1160.62 | 720.745
| (b) Stone Chips(195 Km pucca + 5KM Kacha Carriage) |  |  |  |  | 1.242 | M3 | P/M3 | 4291.17 | 5329.6331
5 | Providing and laying High Density Polyethyene pipe (HDPE pipe) of 20 mm to 225 mm OD and pressure 6.0 Kg/cm2 and 10 Kg/cm2 sutable for water supply which is available in all standard, like ISI-4984/1995 and various grades like PE-80, PE-100 including required specials. Rates are inclusive of , all taxes and duties (Exise duty @12.50% & CST @ 2% against Form 'C'), labour cess, contractor profit and overhead charges all complete as per direction of Engineer-in-charge. | [9 empty] | 21862 | #REF! | #REF! | #REF! | #REF! | #REF!
HDPE pipe of materials grade PE100- PN10 (dia in mm)
| 90mm dia Pipe |  |  |  |  | 0 | M | P/M | 437.96 | 0 |  | 0.65
| 75mm dia Pipe |  |  |  |  | 0 | M | P/M | 306.31 | 0
| 63mm dia Pipe |  |  |  |  | 100 | M | P/M | 218.62 | 21862
HDPE pipe of materials grade PE100- PN8 (dia in mm)
| 50mm dia Pipe |  |  |  |  | 0 | M | P/M | 116.25 | 0
| 40mm dia Pipe |  |  |  |  | 0 | M | P/M | 76.53 | 0
| Providing all materials labours tools, fittings, specials and tackles for fitting, jointing and connecting HDPE pipes. | [14 empty] | 115.1
| 5% of the cost of HDPE Pipe | [8 empty] | 1093.1 | [5 empty] | 144.1 | 25.1955
6 | Providing and fixing brass gate valve with C.I. wheel of approved quality (screwed end).
| 80mm dia Pipe |  |  |  |  | 0 | Nos. | Each | 2227.6 | 0
| 65mm dia Pipe |  |  |  |  | 0 | Nos. | Each | 1490.7 | 0
| 50mm dia Pipe |  |  |  |  | 0 | Nos. | Each | 878.2 | 0
| 40mm dia Pipe |  |  |  |  | 0 | Nos. | Each | 707.3 | 0
7 18.33 | Constructing masonry Chamber 60x60x75 cm inside, in brick work in cement mortar 1:4 (1 cement : 4 coarse sand) for sluice valve,with C.I. surface box 100mm top diameter, 160 mm bottom diameter and 180 mm deep ( inside) with chained lid and RCC top slab 1:2:4 mix (1 cement : 2 coarse sand : 4 graded stone aggregate 20mm nominal size) , necessary excavation, foundation concrete 1:5:10(1 cement : 5 fine sand : 10 graded stone aggregate 40 mm nominalsize) and inside plastering with cement mortar 1:3 (1 cement : 3coarse sand) 12 mm thick, finished with a floating coat of neat cement complete as per standard specifications & direction of E/I. |  |  |  |  | 0 | Nos. | Each | 7210.6 | 0
| Work for additional depth | [5 empty] | M3 | P/M3 | 5017.9 | 0
Brick work (1:4) in foundation
| 2 | 1.1 | 0.25 | 0.35 | 0.1925
| 2 | 0.6 | 0.25 | 0.35 | 0.105
[5 empty] | 0.2975 | 0
Plaster (1:3)
| 8 | 1.1 |  | 0.35 | 3.08 | 0 | M2 | P/M2 | 164.3 | 0
| Carriage 10% of item 7 | [8 empty] | 0
8 11.72 | Providing designation of 100A Brick flat Soling joints filled with local sand including cost of watering, taxes & royalty all complete as per specification & direction of E/I.
|  | 0 | 0.45 | 0.45 |  | 0 | M2 | P/M2 | 283.3 | 0
[9 empty] | TOTAL | 52419.1555
[9 empty] | Say | 52420
[9 empty] | Rate per Meter | 524.2
| JE |  | Assistant Engineer |  |  |  |  | Executive Engineer
P.H.Division, Begusarai

## 6D
Sub Est. No. 06 D
ANALYSIS OF 100 METER WATER SUPPLY DISTRIBUTION SYSTEM FOR 50 MM DIA HDPE PIPELINE. | [10 empty] | 2
S.N. | Particulars |  |  |  |  | Quantity |  | Unit | Rate | Amount
1A 2.8 | Earthwork in excavation over areas (exceeding 30 cm in depth 1.5 in width as well as 10 sqm on plan) including disposal of excavated earth lead upto 50m and lift upto 1.5m, disposal earth to be levelled and neatly dressed. | [6 empty] | P/M3 | 360.7 | 12498.255
| 90mm dia Pipe | 0 | 0.3 | 1.1 | = | 0
| 75mm dia Pipe | 0 | 0.3 | 1.1 | = | 0
| 63mm dia Pipe | 0 | 0.3 | 1.1 | = | 0
| 50mm dia Pipe | 100 | 0.3 | 1.1 | = | 33
| 40mm dia Pipe | 0 | 0.3 | 1.1 | = | 0
|  | 100 |  |  |  | 33 | M3
| Add 5% extra for fittings = |  |  |  |  | 1.65 | M3
[6 empty] | 34.65 | M3
1B 2.26 | Filling available excavated earth (excluding rock) in trenches, plinth, sides of foundations etc. in layers not exceeding 20cm in depth, consolidating each deposited layer by ramming and watering, lead up to 50 m and lift upto 1.5 m. |  |  |  |  | 33.957 | M3 | P/M3 | 123.9 | 4207.2723
2 15.2.1 | Demolishing cement concrete manually/ by mechanical means including disposal of material within 50 metres lead as per direction of Engineer - in - charge. | [5 empty] | M3 | P/M3 | 970.9 | 1310.715
1:3:6 or richer mix
| 1 | 30 | 0.3 | 0.15 | = | 1.35
1.35
3 4.1.3 | Providing and laying in position cement concrete of specified grade excluding the cost of centering and shuttering all work upto plinth
| 1:2:4 (1 cement: 2 coarse sand : 4 graded stone aggregate 20mm nominal size) |  |  |  |  | 1.35 | M3 | P/M3 | 3998.1 | 5397.435
4 | Carriage of materials
| (a) Coarse sand (44 Km pucca +1 KM Kacha Carriage) |  |  |  |  | 0.621 | M3 | P/M3 | 1160.62 | 720.745
| (b) Stone Chips(195 Km pucca + 5KM Kacha Carriage) |  |  |  |  | 1.242 | M3 | P/M3 | 4291.17 | 5329.6331
5 | Providing and laying High Density Polyethyene pipe (HDPE pipe) of 20 mm to 225 mm OD and pressure 6.0 Kg/cm2 and 10 Kg/cm2 sutable for water supply which is available in all standard, like ISI-4984/1995 and various grades like PE-80, PE-100 including required specials. Rates are inclusive of , all taxes and duties (Exise duty @12.50% & CST @ 2% against Form 'C'), labour cess, contractor profit and overhead charges all complete as per direction of Engineer-in-charge. | [9 empty] | 11625 | #REF! | #REF! | #REF! | #REF! | #REF!
HDPE pipe of materials grade PE100- PN10 (dia in mm)
| 90mm dia Pipe |  |  |  |  | 0 | M | P/M | 437.96 | 0 |  | 0.65
| 75mm dia Pipe |  |  |  |  | 0 | M | P/M | 306.31 | 0
| 63mm dia Pipe |  |  |  |  | 0 | M | P/M | 218.62 | 0
HDPE pipe of materials grade PE100- PN8 (dia in mm)
| 50mm dia Pipe |  |  |  |  | 100 | M | P/M | 116.25 | 11625
| 40mm dia Pipe |  |  |  |  | 0 | M | P/M | 76.53 | 0
| Providing all materials labours tools, fittings, specials and tackles for fitting, jointing and connecting HDPE pipes. | [14 empty] | 115.1
| 5% of the cost of HDPE Pipe | [8 empty] | 581.25 | [5 empty] | 144.1 | 25.1955
6 | Providing and fixing brass gate valve with C.I. wheel of approved quality (screwed end).
| 80mm dia Pipe |  |  |  |  | 0 | Nos. | Each | 2227.6 | 0
| 65mm dia Pipe |  |  |  |  | 0 | Nos. | Each | 1490.7 | 0
| 50mm dia Pipe |  |  |  |  | 0 | Nos. | Each | 878.2 | 0
| 40mm dia Pipe |  |  |  |  | 0 | Nos. | Each | 707.3 | 0
7 18.33 | Constructing masonry Chamber 60x60x75 cm inside, in brick work in cement mortar 1:4 (1 cement : 4 coarse sand) for sluice valve,with C.I. surface box 100mm top diameter, 160 mm bottom diameter and 180 mm deep ( inside) with chained lid and RCC top slab 1:2:4 mix (1 cement : 2 coarse sand : 4 graded stone aggregate 20mm nominal size) , necessary excavation, foundation concrete 1:5:10(1 cement : 5 fine sand : 10 graded stone aggregate 40 mm nominalsize) and inside plastering with cement mortar 1:3 (1 cement : 3coarse sand) 12 mm thick, finished with a floating coat of neat cement complete as per standard specifications & direction of E/I. |  |  |  |  | 0 | Nos. | Each | 7210.6 | 0
| Work for additional depth | [5 empty] | M3 | P/M3 | 5017.9 | 0
Brick work (1:4) in foundation
| 2 | 1.1 | 0.25 | 0.35 | 0.1925
| 2 | 0.6 | 0.25 | 0.35 | 0.105
[5 empty] | 0.2975 | 0
Plaster (1:3)
| 8 | 1.1 |  | 0.35 | 3.08 | 0 | M2 | P/M2 | 164.3 | 0
| Carriage 10% of item 7 | [8 empty] | 0
8 11.72 | Providing designation of 100A Brick flat Soling joints filled with local sand including cost of watering, taxes & royalty all complete as per specification & direction of E/I.
|  | 0 | 0.45 | 0.45 |  | 0 | M2 | P/M2 | 283.3 | 0
[9 empty] | TOTAL | 41670.3055
[9 empty] | Say | 41671
[9 empty] | Rate per meter | 416.71
| JE |  | Assistant Engineer |  |  |  |  | Executive Engineer
P.H.Division, Begusarai

## 6E
Sub Est. No. 06 E
ANALYSIS OF 100 METER WATER SUPPLY DISTRIBUTION SYSTEM FOR 40 MM DIA HDPE PIPELINE. | [10 empty] | 2
S.N. | Particulars |  |  |  |  | Quantity |  | Unit | Rate | Amount
1A 2.8 | Earthwork in excavation over areas (exceeding 30 cm in depth 1.5 in width as well as 10 sqm on plan) including disposal of excavated earth lead upto 50m and lift upto 1.5m, disposal earth to be levelled and neatly dressed. | [6 empty] | P/M3 | 360.7 | 12498.255
| 90mm dia Pipe | 0 | 0.3 | 1.1 | = | 0
| 75mm dia Pipe | 0 | 0.3 | 1.1 | = | 0
| 63mm dia Pipe | 0 | 0.3 | 1.1 | = | 0
| 50mm dia Pipe | 0 | 0.3 | 1.1 | = | 0
| 40mm dia Pipe | 100 | 0.3 | 1.1 | = | 33
|  | 100 |  |  |  | 33 | M3
| Add 5% extra for fittings = |  |  |  |  | 1.65 | M3
[6 empty] | 34.65 | M3
1B 2.26 | Filling available excavated earth (excluding rock) in trenches, plinth, sides of foundations etc. in layers not exceeding 20cm in depth, consolidating each deposited layer by ramming and watering, lead up to 50 m and lift upto 1.5 m. |  |  |  |  | 33.957 | M3 | P/M3 | 123.9 | 4207.2723
2 15.2.1 | Demolishing cement concrete manually/ by mechanical means including disposal of material within 50 metres lead as per direction of Engineer - in - charge. | [5 empty] | M3 | P/M3 | 970.9 | 1310.715
1:3:6 or richer mix
| 1 | 30 | 0.3 | 0.15 | = | 1.35
1.35
3 4.1.3 | Providing and laying in position cement concrete of specified grade excluding the cost of centering and shuttering all work upto plinth
| 1:2:4 (1 cement: 2 coarse sand : 4 graded stone aggregate 20mm nominal size) |  |  |  |  | 1.35 | M3 | P/M3 | 3998.1 | 5397.435
4 | Carriage of materials
| (a) Coarse sand (44 Km pucca +1 KM Kacha Carriage) |  |  |  |  | 0.621 | M3 | P/M3 | 1160.62 | 720.745
| (b) Stone Chips(195 Km pucca + 5KM Kacha Carriage) |  |  |  |  | 1.242 | M3 | P/M3 | 4291.17 | 5329.6331
5 | Providing and laying High Density Polyethyene pipe (HDPE pipe) of 20 mm to 225 mm OD and pressure 6.0 Kg/cm2 and 10 Kg/cm2 sutable for water supply which is available in all standard, like ISI-4984/1995 and various grades like PE-80, PE-100 including required specials. Rates are inclusive of , all taxes and duties (Exise duty @12.50% & CST @ 2% against Form 'C'), labour cess, contractor profit and overhead charges all complete as per direction of Engineer-in-charge. | [9 empty] | 7653 | #REF! | #REF! | #REF! | #REF! | #REF!
HDPE pipe of materials grade PE100- PN10 (dia in mm)
| 90mm dia Pipe |  |  |  |  | 0 | M | P/M | 437.96 | 0 |  | 0.65
| 75mm dia Pipe |  |  |  |  | 0 | M | P/M | 306.31 | 0
| 63mm dia Pipe |  |  |  |  | 0 | M | P/M | 218.62 | 0
HDPE pipe of materials grade PE100- PN8 (dia in mm)
| 50mm dia Pipe |  |  |  |  | 0 | M | P/M | 116.25 | 0
| 40mm dia Pipe |  |  |  |  | 100 | M | P/M | 76.53 | 7653
| Providing all materials labours tools, fittings, specials and tackles for fitting, jointing and connecting HDPE pipes. | [14 empty] | 115.1
| 5% of the cost of HDPE Pipe | [8 empty] | 382.65 | [5 empty] | 144.1 | 25.1955
6 | Providing and fixing brass gate valve with C.I. wheel of approved quality (screwed end).
| 80mm dia Pipe |  |  |  |  | 0 | Nos. | Each | 2227.6 | 0
| 65mm dia Pipe |  |  |  |  | 0 | Nos. | Each | 1490.7 | 0
| 50mm dia Pipe |  |  |  |  | 0 | Nos. | Each | 878.2 | 0
| 40mm dia Pipe |  |  |  |  | 0 | Nos. | Each | 707.3 | 0
7 18.33 | Constructing masonry Chamber 60x60x75 cm inside, in brick work in cement mortar 1:4 (1 cement : 4 coarse sand) for sluice valve,with C.I. surface box 100mm top diameter, 160 mm bottom diameter and 180 mm deep ( inside) with chained lid and RCC top slab 1:2:4 mix (1 cement : 2 coarse sand : 4 graded stone aggregate 20mm nominal size) , necessary excavation, foundation concrete 1:5:10(1 cement : 5 fine sand : 10 graded stone aggregate 40 mm nominalsize) and inside plastering with cement mortar 1:3 (1 cement : 3coarse sand) 12 mm thick, finished with a floating coat of neat cement complete as per standard specifications & direction of E/I. |  |  |  |  | 0 | Nos. | Each | 7210.6 | 0
| Work for additional depth | [5 empty] | M3 | P/M3 | 5017.9 | 0
Brick work (1:4) in foundation
| 2 | 1.1 | 0.25 | 0.35 | 0.1925
| 2 | 0.6 | 0.25 | 0.35 | 0.105
[5 empty] | 0.2975 | 0
Plaster (1:3)
| 8 | 1.1 |  | 0.35 | 3.08 | 0 | M2 | P/M2 | 164.3 | 0
| Carriage 10% of item 7 | [8 empty] | 0
8 11.72 | Providing designation of 100A Brick flat Soling joints filled with local sand including cost of watering, taxes & royalty all complete as per specification & direction of E/I.
|  | 0 | 0.45 | 0.45 |  | 0 | M2 | P/M2 | 283.3 | 0
[9 empty] | TOTAL | 37499.7055
[9 empty] | Say | 37500
[9 empty] | Rate per meter | 375
| JE |  | Assistant Engineer |  |  |  |  | Executive Engineer
P.H.Division,Begusarai

## 7. RISER & dILIVERY
Sub Estimate no. - 07
Name of work :- Estimate for replacing damaged Riser & Delivery pipe 8 meter staging with G.I pipe and providing gate valve all complete as per direction of engineer in charge.
S.N. | Particulars | Quantity |  | Unit | Rate | Amount
6A/ 18.12 | Providing and fixing G.I.Pipes complete with G.I. Fittings including trenching and refilling etc.
18.12.6 | 50mm dia G.I.Pipe from T/well to PVC Tank | 14 | M | P/M | 572.6 | 8016.4 | 611.3975
18.12.8 | 80mm dia G.I.Pipe from PVC Tank to Distribution main | 14 | M | P/M | 818.2 | 11454.8
18.12.7 | 65mm dia G.I.Pipe for wash out | 12 | M | P/M | 667.7 | 8012.4
7A/ 18.31.1.1 | P/F C.I sluice Valve (with Cap) complete with bolts,nuts,rubber insertions etc
6B/ | Providing and fixing brass gate valve with C.I. wheel of approved quality (screwed end).
| 80mm dia Pipe | 1 | Nos. | Each | 2227.6 | 2227.6
| 50mm dia Pipe | 2 | Nos. | Each | 878.2 | 1756.4
10A | Supplying all materials labours & fixing 50mm dia. G.I pipe for using as filling station etc. All as per direction of E/I
| 50mm dia. Pipe from distribution main | 3.5 | M | P/M | 572.6 | 2004.1
10B | Providing and fixing G.I fittings
| 80mmx80mmx50mm dia Tee | 1 | No | Each | 225 | 225
| 50mm dia bend | 3 | No | Each | 175 | 525
| Providing and fixing gun metal gate valve with C.I. wheel of approved quality (screwed end) :50mm nominal dia. | 1 | N | Each | 811.4 | 811.4
| Sub Total Of Part (II) |  |  |  |  | 0
| Grand Total |  |  |  |  | 35033.1
Executive Engineer
Begusarai

## 8. WATER TANK
Sub Estimate no. - 08
Estimate for supply & installation of water storage tank.
S.N. | Particulars | Quantity |  | Unit | Rate | Amount
1A/ 18.48 | Providing and placing on terrace (at all floor levels) polyethylene water storage tank, ISI : 12701 marked, with cover and suitable locking arrangement and making necessary holes for inlet, outlet and overflow pipes but without fittings and the base support for tank. | 5000 | Ltrs. | P/Ltr. | 9.7 | 48500 | 1 | 5000 | 5000
1B | Providing and fixing MS clamp consisting of 32mm X 5mm thick two no. rings spaced suitably distance apart. |  |  |  | LS | 3000
2 | Providing and fixing PTMT extension nipple for water tank pipe, fittings of approved quality and colour.
| 50mm dia | 2 | Nos. | each | 300 | 600
| 63mm dia | 1 | No. | each | 350 | 350
| 80 mm dia | 1 | No. | each | 550 | 550
| Grand Total |  |  |  |  | 53000
Executive Engineer
Begusarai

## 9. Clorinator
Sub Estimate no.- 9
Electronically Regulated Doser Type Chlorinator
Sl. No. | Particulars | Quantity |  | Unit | Rate (In Rs.) | Amount (In Rs.)
1 | Providing cost of electronically regulated Doser type chlorinator using sodium Hypo Chlorite (NaOCl ) and installation including all cost and necessary fittings and connections as required and carriage cost etc. all complete as per direction of E/I.
|  | 1 | No. | Each | 23515 | 23515
TOTAL : - | [5 empty] | 23515
Executive Engineer P.H. Division, Begusarai

## 10. Staging
Sub Est. No. 7
8 M HIGH STEEL STRUCTURE STAGING FOR 10000 LITER PVC TANK / RCC STAGING
S.N. | Particulars | [5 empty] | Quantity |  | Unit | Rate | Amount
1 10.3 | Structural steel work riveted or bolted in built up sections, trusess and framed work, including cutting,hoisting,fixing in position and applying a priming coat of approved primer all complete
| for 8M high staging with ladder of ISA65x65x6 and 16mm dia MS bar as trade @ 400mm c/c and GI enclosure to house electric switch panel & treatment unit (where required) of suitably designed MS section of angle, channel, etc. as per drawing attached. | [5 empty] | 4240 | Kg | P/Kg | 104 | 440960
2 2.8.1 | Earth work in excavation in foundation trenches or drains(not exceeding 1.5 m in width or 10 sqm on plan) including ressing of sides and ramming of bottoms, lift upto 1.5 m . including getting out the excavated soil and disposal of surplus excavated soil as directed, within a lead of 50 m. All Kinds of soil
base of footing
| 4 | 1.95 | 1.95 | 1.35 | = | 20.5335
Under Tie beam
| 2 | 2.3 | 0.25 | 0.275 | = | 0.31625
| 2 | 1.3 | 0.25 | 0.275 | = | 0.17875
[6 empty] | 21.0285 | 21.0285 | M3 | P/M3 | 360.7 | 7584.9799
3- 2.28 | Supplying and filling in plinth with local sand and under floors including watering, ramming consolidating and dressing complete.
base of footing
| 4 | 1.95 | 1.95 | 0.1 | = | 1.521
Under Tie beam
| 2 | 3.95 | 0.25 | 0.1 | = | 0.1975
| 2 | 2.95 | 0.25 | 0.1 | = | 0.1475
Floor
| 1 | 4 | 3 | 0.1 | = | 1.2
[6 empty] | 3.066 | 3.066 | M3 | P/M3 | 287.3 | 880.8618
4- 11.72 | Providing designation of 100A Brick flat Soling joints filled with local sand including cost of watering, taxes & royalty all complete as per specification & direction of E/I.
base of footing
| 4 | 1.95 | 1.95 |  | = | 15.21
Under Tie beam
| 2 | 3.95 | 0.25 |  | = | 1.975
| 2 | 2.95 | 0.25 |  | = | 1.475
Floor
| 1 | 4 | 3 |  | = | 12
[6 empty] | 30.66 | 30.66 | M2 | P/M2 | 283.3 | 8685.978
5 4.1.2 | Providing and laying in position cement concrete of specified grade exluding the cost of centring and shuttering-all work upto plinth level.
1:1.5:3(1 Cement :1.5 coarse sand:3 graded stone aggregate 20 mm nominal size)
base of footing
| 4 | 1.95 | 1.95 | 0.075 | = | 1.1407
Floor
| 1 | 4 | 3 | 0.1 | = | 1.2
[6 empty] | 2.3407 | 2.3407 | M3 | P/M3 | 4420.8 | 10347.9876
6 5.1.2 | Providing and laying in position specified grade of reinforced cement concrete excluding the cost of entring,shuttering,finishing and reinforcement-All work puto plinth level
1:1:5:3(1 cement: 1.5 coarse sand:3 graded stone aggregate 20 mm nominal size)
Tie beam
| 2 | 3.8 | 0.25 | 0.25 | = | 0.475
| 2 | 2.8 | 0.25 | 0.25 | = | 0.35
base of footing
| 4 | 1.8 | 1.8 | 0.3 | = | 3.888
| 4 | 0.6 | 0.6 | 0.15 | = | 0.216
Column below GL
| 4 | 0.45 | 0.45 | 0.65 | = | 0.5265
Column above GL
| 4 | 0.45 | 0.45 | 0.15 | = | 0.1215
[6 empty] | 5.577 | 5.577 | M3 | P/M3 | 4688.3 | 26146.6491
7- 5.9.1 | Centring and shuttering including strutting,propping etc. and removal of form for.
| 4 | 3.8 | 0.25 |  | = | 3.8
| 4 | 2.8 | 0.25 |  | = | 2.8
| 16 | 1.8 | 0.3 |  | = | 8.64
| 16 | 0.6 | 0.15 |  | = | 1.44
| 16 | 0.45 | 0.65 |  | = | 4.68
| 16 | 0.45 | 0.15 |  | = | 1.08
[6 empty] | 22.44 | 22.44 | M2 | P/M2 | 211.6 | 4748.304
8- 5.22 | Reinforcement for R.C.C. work including straightening, cutting, bending, placing in position and binding all complete.
8 mm to 16 mm tor steel
| Total Reinforcement. @1.25% of Vol. Of Concrete (Kg/cuM) |  |  |  |  | = | 446.24 | Kg. | P/Kg. | 94.5 | 42169.68
9 2.26 | Filling available excavated earth (excluding rock) in trenches, plinth, sides of oundations etc. in layers not exceeding 20 cm in depth: consolidating each deposited layer by ramming and watering lead (50% of E/W in excavation) | [5 empty] | 10.5143 | M3 | P/M3 | 123.9 | 1302.7156
10 13.26 | Neat cement punning
| 1 | 4 | 3 |  | = | 12 | 12 | M2 | P/M2 | 40.5 | 486
11- 10.7.1 | Providing and fixing 1mm thick M.S. sheet door with frame of 40x40x6mm angle iron and 3mm M.S. gusset plates at the junctions and corners, all necessary fittings complete, including applying a priming coat of approved steel primer.
Using flats 30x6 mm for diagonal braces and central cross piece.
Door
| 1 | 0.9 | 2.1 |  | = | 1.89
Window
| 1 | 1.2 | 0.9 |  | = | 1.08
|  |  |  | Total | = | 2.97 | 2.97 | M3 | P/M3 | 3653 | 10849.41
12- 12.1.4 | Providing corrugated G.S. sheet roofing fixed with G.I.J. or hooks, bolts and nuts 8 mm diameter with bitumen and G. I. limpet washers or with G.I. limpet washers filled with white lead and including a coat of approved steel primer and two coats of approved paint on over lapping of sheets complete (upto a pitch of 60°) excluding the cost or purlins, rafters and trusses.
0.8mm thick with zinc coating not less than 275 gm/mz
Roof
| 1 | 4.5 | 3.5 |  | = | 15.75
Wall
| 1 | 16 | 3 |  | = | 48
63.75
Deduct for door & window
| 1 | 0.9 | 2.1 |  | = | 1.89
| 1 | 1.2 | 0.9 |  | = | 1.08
2.97
| Net Qty |  |  |  | = | 60.78 | 60.78 | M2 | M2 | 1501.3 | 91249.014
13 10.19 | Providing and fixing anchor bolt of 20 mm dia and 0.60 Mtr length (bolt, washer & double nut) embedded in R.C.C pedestal all complete as per direction of Engineer in charge. @4x4x1.60kg | [5 empty] | 25.6 | Kg | P/kg | 82.7 | 2117.12
14- 13.82.1 | Painting with ready mixed paint of approved brand and manufacture in all shades to give an even shade:
New steel work (two or more coats)
Frame work
| 0.5 | 16 | 8 |  | = | 64
| 0.5 | 5 | 4 |  | = | 10
Roof sheet
| 2 | 4.5 | 3.5 |  | = | 31.5
Top sheet
| 2 | 5 | 4 |  | = | 40
GI sheet wall
| 2 | 16 | 3 |  | = | 96
[6 empty] | 241.5 | 241.5 | M2 | M2 | 83.5 | 20165.25
15 | Carriage of the following materials from quarry to work site including loading, unloading and staking at work site as per specification & direction of E/I.
| (a) Bricks | [5 empty] | 990 | Nos. | %0 nos. | 927.887 | 918.6081
| (b) Coarse sand | [5 empty] | 3.44 | M3 | P/M3 | 2050.9262 | 7055.1861
| (c) Stone Chips | [5 empty] | 6.695 | M3 | P/M3 | 3021.011 | 20225.6686
| (d) Local Sand | [5 empty] | 3.53 | M3 | P/M3 | 277.2046 | 978.5322
[10 empty] | TOTAL | 696871.9452
[10 empty] | say | 696900
| Junior Engineer |  |  |  |  | Assistant engineer |  |  |  |  | Executive Engineer
Begusarai

## 11. PAINTING
Sub Est. No. 11
PAINTING OF 8 M HIGH STEEL STRUCTURE STAGING
S.N. | Particulars |  |  |  |  | Quantity |  | Unit | Rate | Amount
14- 13.82.1 | Painting with ready mixed paint of approved brand and manufacture in all shades to give an even shade:
New steel work (two or more coats)
Frame work
| 0.5 | 16 | 8 | = | 64
| 0.5 | 5 | 4 | = | 10
Roof sheet
| 2 | 4.5 | 3.5 | = | 31.5
Top sheet
| 2 | 5 | 4 | = | 40
GI sheet wall
| 2 | 16 | 3 | = | 96
[5 empty] | 241.5 | 241.5 | M2 | M2 | 83.5 | 20165.25
[9 empty] | TOTAL | 20165.25
[9 empty] | say | 20200
Executive Engineer
P.H. Division, Begusarai

## 12. ROOM for S.Staging
Sub Est. No. 12
Name of the work :- Providing GI enclosure to house electric switch panel for steel structure staging all complete.
S.N. | Particulars | [5 empty] | Quantity |  | Unit | Rate | Amount
11- 10.7.1 | Providing and fixing 1mm thick M.S. sheet door with frame of 40x40x6mm angle iron and 3mm M.S. gusset plates at the junctions and corners, all necessary fittings complete, including applying a priming coat of approved steel primer.
Using flats 30x6 mm for diagonal braces and central cross piece.
Door
| 1 | 0.9 | 2.1 |  | = | 1.89
Window
| 1 | 1.2 | 0.9 |  | = | 1.08
|  |  |  | Total | = | 2.97 | 2.97 | M3 | P/M3 | 3653 | 10849.41
12- 12.1.4 | Providing corrugated G.S. sheet roofing fixed with G.I.J. or hooks, bolts and nuts 8 mm diameter with bitumen and G. I. limpet washers or with G.I. limpet washers filled with white lead and including a coat of approved steel primer and two coats of approved paint on over lapping of sheets complete (upto a pitch of 60°) excluding the cost or purlins, rafters and trusses.
0.8mm thick with zinc coating not less than 275 gm/mz
Roof
| 1 | 4.5 | 3.5 |  | = | 15.75
Wall
| 1 | 16 | 3 |  | = | 48
63.75
Deduct for door & window
| 1 | 0.9 | 2.1 |  | = | 1.89
| 1 | 1.2 | 0.9 |  | = | 1.08
2.97
| Net Qty |  |  |  | = | 60.78 | 60.78 | M2 | M2 | 1501.3 | 91249.014
13 10.19 | Providing and fixing anchor bolt of 20 mm dia and 0.60 Mtr length (bolt, washer & double nut) embedded in R.C.C pedestal all complete as per direction of Engineer in charge. @4x4x1.60kg | [5 empty] | 25.6 | Kg | P/kg | 82.7 | 2117.12
[10 empty] | TOTAL | 104215.544
[10 empty] | say | 104200
Executive Engineer P.H. Division, Begusarai

## 13. Floor of Staging
Sub Est. No. 13
Name of the work :- Construction of floor for staging etc. all complete
S.N. | Particulars | [5 empty] | Quantity |  | Unit | Rate | Amount
3- 2.28 | Supplying and filling in plinth with local sand and under floors including watering, ramming consolidating and dressing complete.
Floor
| 1 | 4 | 3 | 0.1 | = | 1.2
[6 empty] | 1.2 | 1.2 | M3 | P/M3 | 287.3 | 344.76
4- 11.72 | Providing designation of 100A Brick flat Soling joints filled with local sand including cost of watering, taxes & royalty all complete as per specification & direction of E/I.
Floor
| 1 | 4 | 3 |  | = | 12
[6 empty] | 12 | 12 | M2 | P/M2 | 283.3 | 3399.6
5 4.1.2 | Providing and laying in position cement concrete of specified grade exluding the cost of centring and shuttering-all work upto plinth level.
1:1.5:3(1 Cement :1.5 coarse sand:3 graded stone aggregate 20 mm nominal size)
base of footing
| 4 | 1.95 | 1.95 | 0.075 | = | 0
Floor
| 1 | 4 | 3 | 0.1 | = | 1.2
[6 empty] | 1.2 | 1.2 | M3 | P/M3 | 4420.8 | 5304.96
9- 6.1.14A +6.3A | Brick work with bricks of class designation 100A in foundation and plinth in : Cement mortar 1:6 (1 Cement : 6 Sand) Extra for brick work in super structure above plinth
| 2 | 4.25 | 0.25 | 0.5 | = | 0
| 2 | 3.25 | 0.25 | 0.5 | = | 0
| Net Quantity |  |  |  |  | 0 | 0 | M3 | P/M3 | 4490.6 | 0
10/ 2.28 | Supplying and Filling in plinth with local sand and under floors including, watering, ramming consolidating and dressing complete. | [5 empty] | 6.9062 | M3 | P/M3 | 287.3 | 1984.1656 | 6.9062 |  | 18.4925
15 | Carriage of the following materials from quarry to work site including loading, unloading and staking at work site as per specification & direction of E/I.
| (a) Bricks ( 7 Km. Pucca & 1 Km. Kaccha lead) | [5 empty] | 396 | Nos. | %0 nos. | 873.2 | 345.7872 |  | 2094.8814
| (b) Coarse sand (44 Km pucca & 1 km kaccha Carriage) | [5 empty] | 0.552 | M3 | P/M3 | 2094.8814 | 1156.3745 |  | 2999.8414
| (c) Stone Chips (195 Km pucca & 5 km unsurafced Carriage) | [5 empty] | 1.104 | M3 | P/M3 | 2999.8414 | 3311.8249 |  | 328.9166
| (d) Local Sand ( 2 Km. lead & 1km Kachaa lead) | [5 empty] | 8.1062 | M3 | P/M3 | 328.9166 | 2666.2802
| TOTAL | [9 empty] | 18513.7525
| Rate per sqm. | [9 empty] | 1542.8127
Executive Engineer P.H. Division, Begusarai

## 14. Ladder
(Sub Estimate - 14)
Name of work :- Providing ladder in staging including all accessories etc. all complete.
1 10.32.1 | Particulars | Quantity |  | Unit | Rate | Amount
| Ladder of ISA 65x65x6 and 16mm dia MS bar as trade @ 400mm c/c including all accessories for weight 50kg. complete as per standard specifications & direction of E/I. | 120 | Kg | P/Kg | 104 | 12480 | 290 kg
16mm bar
[7 empty] | width | 0.6 | 0.6
[7 empty] | Nos. | 8000/400 +1 | 21
[9 empty] | 1.6 kg/m | 20.16 | kg
Executive Engineer P.H. Division, Begusarai
ISA 65x65x6
[7 empty] | @5.93kg/m |  | 8m+8m
[9 empty] | 16 | 94.88 | kg
[10 empty] | 115.04 | Kg
[9 empty] | Say | 120.792 | Kg

## 15. HC_Hdpe
Sub Est. No. 15
Estimate for the work - House service connection
SUB-ESTIMATE
S.No. | Description |  |  |  | Qty | Unit | Rate | Amount
1A | Providing and fixing MDPE (PE 80 GradeCompound) pipes PN-12.5 (12.5kg/Sqcm) as per ISO 4427 and specification for waterapplication rates are inclusive of , taxes and duties (Exise duty @12.50% &CST @2% against Form 'C'), labour cess, contractor profit and overhead charges all complete asper direction of Engineer-in-charge.complete.
| MDPE Pipe 20mm dia nominal bore |  |  |  | 6 | PM | 27.42 | 164.52
1B | Providing and fixing G.I. pipes complete with G.I. fittings and clamps, i/c cutting and making good the walls etc.Internal work - Exposed on wall
18.10.1 | 15 mm dia nominal bore |  |  |  | 1.1 | PM | 227.7 | 250.47
1C | Providing and faying cement concreate in kerbs, steps and the like at or near ground level excluding the cost of centring, shuttering and finishing.
4.4.1 | 1:2:4 (1 Cement :2 coarse sand :4 grade stone aggregate 20 mm nominal size)
Providing SWR pipe as support with concrete work to the standing GI Pipe
| 22/28 x 0.10m x .10m x 1.0M= |  |  |  | 0.009 | P/M3 | 3998.1 | 35.9829
12.78.2 | Providing & fixing of SWR Pipe of 110mm dia= |  |  |  | 1 | PM | 257.5 | 257.5
2 | Earth work in excavation in foundation trenches or drains(not exceeding 1.5 m in width or 10 sqm on plan) including dressing of sides and amming of bottoms, lift upto 1.5 m . including getting out the excavated soil and disposal of surplus excavated soil as directed, within a lead of 50 m. All kinds of soil
2.8.1 | 6 | 0.3 | 0.6 | 1.08 | 1.08 | CuM | 360.7 | 389.556
3 2.26 | Filling available excavated earth (excluding rock) in trenches, plinth, sides of foundations etc. in layers not exceeding 20 cm in depth: consolidating each deposited layer by ramming and watering lead |  |  |  | 1.06 | CuM | 123.9 | 131.334
4 | Providing and fixing brass ferrule with CI mouth cover incuding boring and tapping the main:
18.20.1 | 15mm nominal bore |  |  |  | 1 | Each | 301.6 | 301.6
(a) | Providing and fixing P.P. Clamp service Saddle (Brass threaded) |  |  |  | 1 | Each | 400 | 400
(b) | Providing and fixing female Adopter for adjoining the ferrule to MDPE pipe |  |  |  | 1 | Each | 75 | 75
(c) | Providing and fixing female elbow Adopter for adjoining the MDPE pipe to GI Pipe |  |  |  | 1 | Each | 50 | 50
5 | Providing and fixing CP brass bib cock of approved quality conforming to IS :8931
18.49 | 15 mm nominal bore |  |  |  | 1 | Each | 434.2 | 434.2
| Total | [6 empty] | 2490.1629
| Say | [6 empty] | 2490
For total no of Household | [6 empty] | 150 | 373500
Executive Engineer P.H. Division, Begusarai

## Retrofitting (hidden)
(Sub Estimate - 14)
Name of work :- Providing Retrofiting to stand post for existing house service connection.
1C | Providing and faying cement concrete in kerbs, steps and the like at or near ground level excluding the cost of centring, shuttering and finishing.
4.4.1 | 1:2:4 (1 Cement :2 coarse sand :4 grade stone aggregate 20 mm nominal size)
Providing SWR pipe as support with concrete work to the standing GI Pipe
| 22/28 x 0.10m x .10m x 1.0M= | 0.009 | P/M3 | 3998.1 | 35.9829
12.78.2 | Providing & fixing of SWR Pipe of 110mm dia= | 1 | PM | 257.5 | 257.5
|  |  |  | Total | 293.4829
Executive Engineer
P.H Division, Hajipur

## IRP (8) (hidden)
Sub Estimate no.- 9A
Estimate for Iron Treatment Plant (Included GST @ 18%)
S.N. | Particulars | Quantity |  | Unit | Rate (In Rs.) | Amount (In Rs.)
1 | Design, supply, erection, installation, testing and commissioning of Iron removal plant based on aeration/ filteration/ activated carbon treatemnt units or any other suitable treatmnet process of ISO 9001 certified reputed make housed in MS/FRP vessel suitable for required flow rate with iron concentration upto 10 ppm in raw water to deliver treated water quality confirming to IS 10500( latest revision) including all necessary civil works, accessories,taxes and duties etc. all complete as per directions of Engineer-in-Charge.
| 8 KLPH Capacity | 1 | No. | Each | 489605 | 489605
TOTAL : - | [5 empty] | 489605
[5 empty] | Say | 489605
Executive Engineer P.H. Division, Hajipur

## IRP (16) (hidden)
Sub Estimate no.- 9B
Estimate for Iron Treatment Plant (Included GST @ 18%)
S.N. | Particulars | Quantity |  | Unit | Rate (In Rs.) | Amount (In Rs.)
1 | Design, supply, erection, installation, testing and commissioning of Iron removal plant based on aeration/ filteration/ activated carbon treatemnt units or any other suitable treatmnet process of ISO 9001 certified reputed make housed in MS/FRP vessel suitable for required flow rate with iron concentration upto 10 ppm in raw water to deliver treated water quality confirming to IS 10500( latest revision) including all necessary civil works, accessories,taxes and duties etc. all complete as per directions of Engineer-in-Charge.
| 16 KLPH Capacity | 1 | No. | Each | 600880 | 600880
TOTAL : - | [5 empty] | 600880
[5 empty] | Say | 600880
Executive Engineer P.H. Division, Hajipur

## IRP 12 (hidden)
Sub Estimate no.- 9B
Estimate for Iron Treatment Plant (Included GST @ 18%)
S.N. | Particulars | Quantity |  | Unit | Rate (In Rs.) | Amount (In Rs.)
1 | Design, supply, erection, installation, testing and commissioning of Iron removal plant based on aeration/ filteration/ activated carbon treatemnt units or any other suitable treatmnet process of ISO 9001 certified reputed make housed in MS/FRP vessel suitable for required flow rate with iron concentration upto 10 ppm in raw water to deliver treated water quality confirming to IS 10500( latest revision) including all necessary civil works, accessories,taxes and duties etc. all complete as per directions of Engineer-in-Charge.
| 12 KLPH Capacity | 1 | No. | Each | 545245 | 545245
TOTAL : - | [5 empty] | 545245
[5 empty] | Say | 545245
Executive Engineer P.H. Division, Hajipur

## Pit (hidden)
SUB ESTIMATE NO -6
Detailed Estimate for construction of chamber for waste water disposal 1.00Mx 2.00M x 1.50M deep (with fly proof galvanized M.S. wire covering)
1 |  | Earth work in excavation
| 2.8 | 1.50m x 2.50m x 1.00M = | 3.75 | M3 | P/M3 | 360.7 | 1352.625
2 | 2.28 | Supplying & filling in plinth with local sand under floors including watering, ramming consolidating and dressing complete.
|  | 1.50m x 2.50m x 0.10M = | 0.375 | M3 | P/M3 | 287.3 | 107.7375
3 | 11.72 | Providing designation 100 A one brick flat soling joints filled with local sand including cost of watering, taxes, royalty all complete as per building specification and direction of E/l.
|  | 1.50m x 2.50m = | 3.75 | M2 | P/M2 | 283.3 | 1062.375
4 | (SOR 4.1.4) | Providing & laying in position cement concrete of specified grade excluding the cost of centring & shuttering etc. all work up to plinth level.
1:2:4 (1 cement : 2 coarse sand : 4 graded stone aggregate 20 mm nominal size)
|  | 1.50m x 2.50m x 0.08M = | 0.3 | M3 | P/M3 | 3879.4 | 1163.82
5 | (SOR 6.1.14A) | Brick work with bricks of class designation 100A in foundation and plinth in
Cement mortar 1:4 (1 cement : 4 coarse sand)
|  | L. W. = 2 x 2.50 x 0.25 x 1.5 = | 1.875
|  | S. W. = 2 x 1.00 x 0.25 x 1.5 = | 0.375
|  |  | 2.25 | M3 | P/M3 | 4819.9 | 10844.775
6 | (SOR 13.17.1) | 12 mm cement plaster 1:3 (1 cement: 3 coarse sand) finished with a floating coat of near cement
In side
|  | L. W. = 2 x 2.00 x 1.5 = | 6
|  | S. W. = 2 x 1.00 x 1.5 = | 3
|  | Bottom = 2.0 x 1.0 = | 2
|  |  | 11 | M2 | P/M2 | 203.6 | 2239.6
7 | (SOR 13.11.2 & 13.26) | Providing 12mm cement plaster (1:4)
out side with neat cement punning
|  | L. W. = 2 x 2.5 x 0.75 = | 3.75 |  |  | 152.9
|  | S. W. = 2 x 1.50 x 0.75 = | 2.25 |  |  | 40.5
|  |  | 6 | M2 | P/M2 | 193.4 | 1160.4
8 | (SOR 9.51.2) | Providing and fixing fly proof galvanized M.S. wire gauze to windows and clerestory window using galvanized M.S. wire gage with average width of aperture 1.4 mm in both directions with wire of dia.0.63 mm.
with mild steel U beading
|  | 2.5m x 1.5m = | 3.75 | M2 | P/M2 | 639.9 | 2399.625
10 |  | Carriage of materials.
|  | (a) Bricks ( 7 Km. Pucca & 1 Km. Kachha lead) | 1037 | No. | P/%0 | 1429.6 | 1482.4952
|  | (b) Coarse Sand (100 Km. lead) | 1.09 | M3 | P/M3 | 1015.1 | 1106.459
|  | (c) Stone Chips (150 Km. lead) | 0.27 | M3 | P/M3 | 1690.7 | 456.489
|  | (d) Local Sand ( 2 Km. Pucca & 1 Km. Kachha lead) | 0.43 | M3 | P/M3 | 407.1 | 175.053
|  | Total |  |  |  |  | 23551.4537
|  | Say |  |  |  |  | 23551
Executive Engineer P.H. Division, Hajipur

## 16. Rep of HC
SUB-ESTIMATE - 16
Estimate for the work - Reparing of House service connection
S.No. | Description |  |  |  | Qty | Unit | Rate | Amount
1A Rate as per cost index @15.06%) | Providing and fixing MDPE (PE 80 GradeCompound) pipes PN-12.5 (12.5kg/Sqcm) as per ISO 4427 and specification for waterapplication rates are inclusive of all taxes and duties, labour cess, contractor profit and overhead charges all complete asper direction of Engineer-in-charge.complete.
| MDPE Pipe 20mm dia nominal bore (WP indexed at 15.06% over 2018 rates) |  |  |  | 3 | PM | 27.42 | 82.26
1B | Providing and fixing G.I. pipes complete with G.I. fittings and clamps, i/c cutting and making good the walls etc.Internal work - Exposed on wall
18.10.1 | 15 mm dia nominal bore |  |  |  | 0 | PM | 227.7 | 0
1C | Providing and laying cement concreate in kerbs, steps and the like at or near ground level excluding the cost of centring, shuttering and finishing.
4.4.1 | 1:2:4 (1 Cement :2 coarse sand :4 grade stone aggregate 20 mm nominal size)
Providing SWR pipe as support with concrete work to the standing GI Pipe
| 22/28 x 0.10m x .10m x 1.0M= |  |  |  | 0.009 | P/M3 | 3998.1 | 35.9829
12.78.2 | Providing & fixing of SWR Pipe of 110mm dia= |  |  |  | 1 | PM | 257.5 | 257.5
2 | Earth work in excavation in foundation trenches or drains(not exceeding 1.5 m in width or 10 sqm on plan) including dressing of sides and amming of bottoms, lift upto 1.5 m . including getting out the excavated soil and disposal of surplus excavated soil as directed, within a lead of 50 m. All kinds of soil
2.8.1 | 3 | 0.3 | 0.6 | 0.54 | 0.54 | CuM | 360.7 | 194.778
3 2.26 | Filling available excavated earth (excluding rock) in trenches, plinth, sides of foundations etc. in layers not exceeding 20 cm in depth: consolidating each deposited layer by ramming and watering lead |  |  |  | 0.5292 | CuM | 123.9 | 65.5679
4 | Providing and fixing brass ferrule with CI mouth cover incuding boring and tapping the main:
18.20.1 | 15mm nominal bore |  |  |  | 0 | Each | 301.6 | 0
(a) Rate as per cost index @15.06%) | Providing and fixing P.P. Clamp service Saddle (Brass threaded) (WP indexed at 15.06% over 2018 rates) |  |  |  | 0 | Each | 400 | 0
(b) Rate as per cost index @15.06%) | Providing and fixing female Adopter for adjoining the ferrule to MDPE pipe (WP indexed at 15.06% over 2018 rates) |  |  |  | 1 | Each | 75 | 75 | 1.15
(c) Rate as per cost index @15.06%) | Providing and fixing female elbow Adopter for adjoining the MDPE pipe to GI Pipe (WP indexed at 15.06% over 2018 rates) |  |  |  | 1 | Each | 50 | 50
| Total | [6 empty] | 761.0888
| Say | [6 empty] | 761
Junior Engineer |  |  | Assistant Engineer |  |  | Executive Engineer
Begusarai

## 16a._rep hc
Sub- Estimate No. 16A
Repairing of House Connection in case leakage at Ferrule
S.No. | Description |  |  |  | Qty | Unit | Rate | Amount
1 | Earth work in excavation in foundation trenches or drains(not exceeding 1.5 m in width or 10 sqm on plan) including dressing of sides and amming of bottoms, lift upto 1.5 m . including getting out the excavated soil and disposal of surplus excavated soil as directed, within a lead of 50 m. All kinds of soil
2.8.1 | 1 | 1 | 1 | 1 | 1 | CuM | 360.7 | 360.7
2.8.1 | 6 | 0.3 | 0.6 | 1.08 | 0 | CuM | 360.7 | 0
2 2.26 | Filling available excavated earth (excluding rock) in trenches, plinth, sides of foundations etc. in layers not exceeding 20 cm in depth: consolidating each deposited layer by ramming and watering lead |  |  |  | 0.98 | CuM | 123.9 | 121.422
3 | Providing and fixing MDPE (PE 80 GradeCompound) pipes PN-12.5 (12.5kg/Sqcm) as per ISO 4427 and specification for waterapplication rates are inclusive of , taxes and duties (Exise duty @12.50% &CST @2% against Form 'C'), labour cess, contractor profit and overhead charges all complete asper direction of Engineer-in-charge.complete.
| MDPE Pipe 20mm dia nominal bore |  |  |  | 6 | PM | 27.42 | 0
7 | Providing and fixing brass ferrule with CI mouth cover incuding boring and tapping the main:
18.20.1 | 15mm nominal bore |  |  |  | 1 | Each | 301.6 | 301.6
8 | Providing and fixing P.P. Clamp service Saddle (Brass threaded) |  |  |  | 1 | Each | 400 | 400
9 | Providing and fixing female Adopter for adjoining the ferrule to MDPE pipe |  |  |  | 1 | Each | 75 | 75
10 | Providing and fixing female elbow Adopter for adjoining the MDPE pipe to GI Pipe |  |  |  | 1 | Each | 50 | 50
11 | Providing and fixing PTMT bib cock of approved quality and colour:
18.54.1 | 15 mm nominal bore |  |  |  | 1 | Each | 109.8 | 109.8
1418.522
| Total | [6 empty] | 1418.522
[7 empty] | Say | 1419
| Junior Engineer |  | Assistant Engineer |  |  |  | Executive Engineer
Begusarai

## 16b_rep_min hc
Sub- Estimate No.16B
Repairing of House Connection
S.No. | Description |  | Qty | Unit | Rate | Amount
Repairing of House Connection in case of only MDPE damage
1 | Providing and fixing MDPE (PE 80 Grade Compound) pipes PN-12.5 (12.5kg/Sqcm) as per ISO 4427 and specification for waterapplication rates are inclusive of , taxes and duties (Exise duty @12.50% &CST @2% against Form 'C'), labour cess, contractor profit and overhead charges all complete asper direction of Engineer-in-charge.complete.
| MDPE Pipe 20mm dia. nominal bore |  | 3 | PM | 27.42 | 82.26
2 | Providing and fixing female elbow Adopter for adjoining the MDPE pipe to GI Pipe |  | 2 | Each | 50 | 100
4 | Providing and fixing PTMT bib cock of approved quality and colour:
18.54.1 | 15 mm nominal bore |  | 0 | Each | 109.8 | 0
182.26
| Total |  |  |  |  | 182.26
| Say |  |  |  |  | 182
| Junior Engineer | Assistant Engineer |  |  | Executive Engineer
Begusarai

## 17. New Bib Cock
SUB-ESTIMATE - 17
Estimate for the work - New Bib Cock
S.No. | Description |  | Qty | Unit | Rate | Amount
1 (18.54) | Providing and fixing PTMT bib cock of approved quality and colour. |  | 1 | Each | 109.8 | 109.8
| Total |  |  |  |  | 109.8
| Say |  |  |  |  | 110
Junior Engineer |  | Assistant Engineer |  | Executive Engineer
Begusarai

## 18. Repairing of Motor
Sub Estimate - 18
Repairing of 3 HP Motor
Sl. No. | Particulars | Quantity |  | Unit | Rate | Amount
1 | 2 | 3 |  | 4 | 5 | 6
1 | Providing all labours, tools and tackles at site for opening all electrical connections of 3 HP sub motor and dismentalling of delivery line& taken out submersible motor pump with column pipe from Tube Well. Analysis Mechanic for 1 day = 1 No @ 391.00 = Rs 391.00 Unskilled Helper for 1 day 2 No @ 306.00 = Rs 612.00 Total = 1003.00 Add CP & OH @ 15% = Rs 150.45 Gross Total = Rs 1153.45 Add 12% GST = Rs 138.41 Gross Total including 12% = Rs 1291.86 Say = Rs 1292.00 | 1 | Job | P/Job | 1292 | 1292
2 | Complete opening of 3 HP Sub motor part by part, cutting its burnt wire & taking out from slots, cleaning the stator slots all complete in workshop. | 1 | Job | P/Job | 300 | 300
3 | Cost for supply of PVC insulated copper winding wire of size 0.8mm dia make - Finolex Base Cost (List Price) exclusive GST = 5.75 Add CP & OH @ 15% = 0.86 Gross Total = 6.61 Add 12% GST = 0.79 Gross Total including 12% = 7.40 Say = 7.50 | 500 | mtr | P/mtr | 7.5 | 3750
4 | Cost for making,supplying and fitting of lower & upper bronze bush of size ID 20mm OD 28mm Length 25mm. Analysis Weight of bronze rod of size OD 28mm X Length 25mm density 8780 Kg/m3 = 3.14 X 28 X 28 X 25 X 8780/10^9 =0.14 Kg Cost @ Rs 850 per Kg = Rs 119.00 Cost for cutting, finishing and machining work for making bush as per size @ 40% of a = Rs 47.60 Total = Rs. 166.60 Add CP & OH @ 15% = Rs 24.99 Gross Total = Rs 191.59 Add 12% GST = Rs 22.99 Net Total including GST 12% = Rs 214.58 Say = Rs 215.00 | 4 | No | Each | 215 | 860
5 | Supply and fitting of thrust plate with counter thrust complete set | 1 | No | Each | 800 | 800
6 | Cost for making all arrangement tools & skilled workmanship for making coil of copper wire as per required size and rewinding of stator | 18 | No | Each | 30 | 540
7 | Cost for insulating material and jointing materials such asPVC paper sleede, cotton tap, PVC tap, soldering wire, flux & rubber compound etc. as required at the time of rewinding | 1 | Job | P/Job | 200 | 200
8 | Cost of Transportation charges of 3 HP sub motor including loading, all complete and carrying from pump house to firm workshop and back to pump house after rewinding | 1 | Job | P/Job | 500 | 500
9 | Providing all labours, tools and tackles at site for lowering of 3 HP sub motor pump with column pipe into the tube well, doing all electric connection, refitting nut-bolt & refitting delivery line & testing on load. Analysis Mechanic for 1 day = 1 No @ 391.00 = Rs 391.00 Unskilled Helper for 1 day 2 No @ 306.00 = Rs 612.00 Total = 1003.00 Add CP & OH @ 15% = Rs 150.45 Gross Total = Rs 1153.45 Add 12% GST = Rs 138.41 Gross Total including 12% = Rs 1291.86 Say = Rs 1292.00 | 1 | Job | P/Job | 1292 | 1292
10 | Deduct : Cost of scrap materials burnt copper wire | 1.5 | Kg | P/Kg | 436 | -654
8880
[5 empty] | Say = | 8880
Junior Engineer Assistant Engineer |  |  |  |  | Executive Engineer
Begusarai

## 18b. Repairing of 5hp
Sub- Estimate No.18b
Estimate for repairing and rewinding of 5 HP Sub Motor(single/Three phase) with Provision of all materials tools & labour etc.
Sr. No. | Particulars | [6 empty] | Quantity |  | Unit | Rate | Amount
1 | Providing all aboun, tools and tackles at uite for opening all electrical connections of 3 HP Sub Motor and diamentling of delevery line & taken out submersible motor Pump with column pipe from Tube Well | [6 empty] | 1 | Job | P/Job | 1887.587 | 1887.587
Analysis
| (i) Mechanic for 1 days | 1 | No. | @ | 473 | = | 473
| (ii) Unskilled Helper for 1 days | 3 | No. | @ | 306 | = | 918
|  |  |  | Total |  |  | 1391
| Add: CP & OH @15% |  |  |  |  | = | 208.65
| Grass Total | [5 empty] | 1599.65
| Add GST @ 18% |  |  |  |  | = | 287.937
| Net including 18% GST | [5 empty] | 1887.587
2 | Complete opening of 3 HP Sub Motor Part by part, cutting its bumt wire & taking out from slots, cleaning the stator slots all complete in workshop. | [6 empty] | 1 | Job | P/Job | 750 | 750
3 | Repairing of slots by weiding with Cl electrodes and facing and polishing all complete. | [6 empty] | 1 | Slot | P/Slot | 40 | 40
4 | Cost for supply of PVC insulated copper winding wire of Size 0.9 mm make -Finolex
| Base Cost (list price( exclusive) GST |  |  |  |  | = | 7.25 | 500 | m | P/m | 9.8383 | 4919.125
| Add: CP & OH @15% |  |  |  |  | = | 1.0875
| Gross Total |  |  |  |  | = | 8.3375
| Add GST @ 18% | [5 empty] | 1.5008
| Net including 18% GST | [5 empty] | 9.8383
5 | Cost for making, supplying and fitting of Lower & upper bronze bush of size | [6 empty] | 4 | Nos. | each | 758.9701 | 3035.8804
| ID | 20 mm | OD | 28mm | length | 25mm
Analysis
Weight of bronze rod of OD 37mm x length 50mm x density 8780 kg/m3
| = π/4 x 37 x 37 x50 x 8780/m3 |  |  |  |  | = | 0.47
| Cost | @ | 850 | per kg |  | = | 399.5
| cost for cutting, finishing and machining work for make bush as per size @ 40 % |  |  |  |  | = | 159.8
[5 empty] | Total | = | 559.3
| Add CP & O.H @ 15% |  |  |  |  | = | 83.895
|  |  |  | Gross Total |  | = | 643.195
| Add GST @ 18% |  |  |  |  | = | 115.7751
| Net including 18% GST | [5 empty] | 758.9701
6 | Supply & fitting of Thrust Plate with counter thrust complete set | [6 empty] | 1 | Nos. | each | 1000 | 1000
7 | Cost for making all arrangement tools & skilled workmanship for making coil of copper wire as per required size and rewinding of stator. | [6 empty] | 18 | Nos. | each | 40 | 720
8 | Cost for insulating materials and jointing materials Such as PVC paper. sleeve, cotton tap, PVC tap, soldering wire, flux & rubber compound etc. as required at the time of rewinding. | [6 empty] | 1 | Job | P/Job | 500 | 500
9 | Cost for transportation charge of 3 HP Sub Motor including loading unloading all complete and carrying from pump house to firm workshop and back to pump house after rewinding. | [6 empty] | 1 | Job | P/Job | 1000 | 1000
10 | Providing all labours, tools and tackles at site for lowering of 3 HP Submersible motor pump with column pipe into the Tubwell, doing all electric connection, re-fitting nut bolt & refitting deleviry line & testing on load
Analysis
| (i) Mechanic for 1 days | 1 | No. | @ | 473 | = | 473 | 1 | Job | P/Job | 1887.587 | 1887.587
| (ii) Unskilled Helper for 1 days | 3 | No. | @ | 306 | = | 918
[5 empty] | Total |  | 1391
| Add: CP & OH @15% |  |  |  |  | = | 208.65
| Grass Total | [5 empty] | 1599.65
| Add GST @ 18% |  |  |  |  | = | 287.937
| Net including 18% GST | [5 empty] | 1887.587
[11 empty] | Total | 15740.1794
[11 empty] | Say | 15740
| Junior Engineer |  |  | Assistant Engineer |  |  |  |  | Executive Engineer
P.H. Division, Begusarai

## 19. Repairing of Starter
Sub Estimate - 19
Repairing Of Starter
Sl. No. | Particulars | Quantity |  | Unit | Rate | Amount
1 | 2 | 3 |  | 4 | 5 | 6
1 | Providing all labours, tools & tackles for repairing of 3 HP starter with supply, changing and fitting magnet coil 1 No, 1 No over load relay unit (8.9-13.5) Amp, 2 No push button, Voltmeter - 1 No, Ameter - 1 No and changing all iternal wiring with suitable PVC wire and strip as required | 1 | Job | P/Job | 1500 | 1500
[5 empty] | Total Rs. | 1500
Junior Engineer Assistant Engineer |  |  |  |  | Executive Engineer
P.H. Division, Begusarai

## 20. Repairing of Stabilizer
Sub Estimate - 20
Repairing Of Stabilizer
Sl. No. | Particulars | Quantity |  | Unit | Rate | Amount
1 | 2 | 3 |  | 4 | 5 | 6
1 | Repairing of 7.5 KVA automatic voltage stabilizer with 12 % GST including CP & OH | 1 | Job | P/Job | 3000 | 3000
[5 empty] | Total Rs. | 3000
Junior Engineer Assistant Engineer |  |  |  |  | Executive Engineer
P.H. Division, Begusarai

## 21. Service Cable
Sub Est. No. 21
Estimate for supply service cable from nearest source up-to pumping station.
Sl. No. | Particulars | Quantity |  | Unit | Rate | Amount
1 | 2 | 3 |  | 4 | 5 | 6 |  | 1.1506
1 | Supplying & fitting 2.5 mm2 copper service cable from power point from nearest source up-to pumping station. | 50 | mtrs | P/Mt | 130 | 6500 | 45500 | 52352.3
[5 empty] | Total Rs. | 6500 | 2803 | 3225.1318
| Junior Engineer Assistant Engineer |  |  |  | Executive Engineer
P.H. Division, Begusarai

## RCC STRUCTURE (hidden)
Sub Est. No-05
Construction of additional column & wall around the foundation of existing RCC structure in Ward No 05 of Panchayat Jurawanpur Karari | [11 empty] | 3
S.N. | Particulars | [5 empty] | Quantity (in Nos) | Unit |  | Rate | Amount
8 | Filling available excavated eath (excluding rock) in
2.26 | trenches, plinth, sides of bundations etc. in layers not | [5 empty] | 12 | M3 | P/M3 | 123.9 | 1486.8
9 | 12mm thick Cement.Plastering. (1:4)
13.26 | Tie beam | 4 | 4.55 | 0.25 |  | 4.55
|  | 2 | 3.55 | 0.25 |  | 1.775
| Side wall | 4 | 4.1 | 2 |  | 32.8
|  | 2 | 4.5 | 2 |  | 18
| Column | 20 | 0.25 | 2 |  | 10
[6 empty] | 67.125 | 67.125 | M2 | P/M2 | 193.4 | 12981.975
9-6.1.14A +6.3A | Brick work with bricks of class designation 100A in foundation and plinth in : Cement mortar 1:6 (1 Cement : 6 Sand) Extra for brick work in super structure above plinth
| 2 | 4.55 | 0.25 | 2 | = | 4.55
| 1 | 3.55 | 0.25 | 2 | = | 1.775
| Net Quantity |  |  |  |  | 6.325 | 6.325 | M3 | P/M3 | 4490.6 | 28403.045
10/ 2.28 | Supplying and Filling in plinth with local sand and under floors including, watering, ramming consolidating and dressing complete. | [5 empty] | 18.4925 | M3 | P/M3 | 287.3 | 5312.8953 |  | 18.4925
11 | Painting on primer water proofing paint of approved brand and manufacture in all shades to give an even shade New surface wall (two or more coats) | [5 empty] | 41.7 | M2 | P/M3 | 99.3 | 4140.81
12 | Carriage of the following materials from quarry to work site
[7 empty] | 2.183 | M2 | P/M3 | 856.3 | 1869.3029
| (b) Coarse sand (100 Km pucca Carriage) | [5 empty] | 1.052 | M2 | P/M3 | 1713.82 | 1802.9386
| (c) Stone Chips (150 Km pucca Carriage) | [5 empty] | 1.896 | M2 | P/M3 | 2473.39 | 4689.5474
| (d) Local Sand (3 Km, lead) | [5 empty] | 2.976 | M2 | P/M3 | 262.05 | 779.8608
| Bricks (7 Km. Pucca & 1 Km. Kachha lead) | [5 empty] | 3125 | Nos. | %0 nos. | 606.1 | 1894.0625
[10 empty] | Total | 63361.2375
[10 empty] | Say | 63400
Junior Engineer, |  |  |  | Assistant Engineer |  |  |  |  | Executive Engineer
P.H.Division, Hajipur

## Rep Rising & Delivery Pipe (hidden)
Sub Estimate - 11
Name of work :- Estimate for replacing damaged riser & delivery pipe 8 meter staging with CPVC pipe and providing gun metel gate valve all complete as per direction of engineer in charge.
Sl. No. | Particulars | Quantity |  | Unit | Rate | Amount
1 | 2 | 3 |  | 4 | 5 | 6
1 | Providing and fixing Chlorinated Polyvinyl Chloride (CPVC) pipes, having thermal stability for hot & cold water supply, including all CPVC plain & brass threaded fittings, including fixing the pipe clamps at 1.0 mtr spacing. This includes jointing of pipes & fittings with one step CPVC solvent cement and testing of joints complete as per direction of Engineer In Charge.
18.7.6 | Riser pipe 50 mm dia nominal bore | 2 | Mtr | P/M | 791 | 1582
18.9.7 | Delivery pipe 80 mm dia nominal bore | 2 | Mtr | P/M | 1889 | 3778
[5 empty] | Total Rs. | 5360
Junior Engineer Assistant Engineer |  |  |  |  | Executive Engineer
P.H.Division, Hajipur

## 22.Tank Cleaning
Sub Estimate - 22
Name of Work :- Cleaning of one 5000 Ltr capacity overhead pvc tank with bleaching powder, scrubing of surface with coconut brush including marking the date of cleaning with stencil and paint all complete as per the direction of Engineer In Charge.
Sl. No. | Particulars | Quantity |  | Unit | Rate | Amount
1 | 2 | 3 |  | 4 | 5 | 6
1 (14.75A) | Cleaning of terrace/loft water storage tank (inside surface area) upto 2000 ltr capacity at all heights with coconut brushes duster etc, removal of silt, rubbing from the tank and cleaning the tank with fresh water disinfecting with bleaching powder @ 0.5 gm per ltr capacity of tank, including marking the date of cleaning on the side of tank body with the help of stencil and paint and disposing the malba, all complete as per direction of Engineer In Charge. | 5000 | Ltr | P/Ltr | 0.1 | 500
[5 empty] | Total Rs. | 500
Junior Engineer Assistant Engineer |  |  |  |  | Executive Engineer
P.H. Division, Begusarai

## 23Analysis leakage repair 90 mm
Sub Estimate :- 23A
ANALYSIS OF LEAKAGE REPAIRING IN 90 MM DIAMETER HDPE PIPE (For pipe laid at 0.5 to 1.0m)
SL NO | Particulars |  | Quantity |  | Units | Rate | Amounts
1. (2.28) | Earthwork in excavation over areas (exceeding 30 cm in depth 1.5 in width as well as 10 sqm on plan) including disposal of excavated earth lead upto 50m and lift upto 1.5m, disposal earth to be levelled and neatly dressed.
| 90 mm dia Pipe | 3x0.3x1.0x1= | 0.9 | M3
|  |  | 0.9 | M3
|  | Add 5% extra for fittings = | 0.045 | M3
|  | Total= | 0.945 | M3 | P/M3 | 360.7 | 340.8615
2 | Filling available excavated earth (excluding rock) in trenches, plinth, sides of foundations etc. in layers not exceeding 20cm in depth, consolidating each deposited layer by ramming and watering, lead up to 50 m and lift upto 1.5 m.
|  |  | 0.9261 | M3 | P/M3 | 123.9 | 114.7438
3 | Providing material for leakage repairing
D- jointers
| 90 mm dia Pipe |  | 3 | Nos | Each | 606 | 1818
4 | Providing Labour for leakage repairing
0L27 | Plumber |  | 1 | Nos | Each | 391 | 391
0L70 | Semi Skilled Labour |  | 1 | Nos | Each | 318 | 318
0L05 | Helper |  | 2 | Nos | Each | 306 | 612
|  | Grand Total for 03 Leakages without PCC cutting in One day = |  |  |  |  | 3594.6053
|  | For 01 Leakage without PCC cutting = |  |  |  |  | 1198
1 15.2.1 | Demolishing cement concrete manually/by mechanical means including disposal of material within 50 metres lead as per direction of Engineer - in - charge.( in 10% length)
| 1:3:6 or richer mix | 3x0.3x1.0x0.15= | 0.135 | M3 | P/M3 | 970.9 | 131.0715
5(a) 4.1.3 | Providing and laying in position cement concrete of specified grade excluding the cost of centering and shuttering all work upto plinth level.
| 1:2:4 (1 cement: 2 coarse sand : 4 graded stone aggregate 40mm nominal size) |  | 0.135 | M3 | P/M3 | 3998.1 | 539.7435
5(b) | Carriage of the following materials from quarry to work site including loading, unloading and staking at work site as per specification & direction of E/I.
| Coarse Sand (100 Km pucca Carriage) |  | 0.06075 | M3 | P/M3 | 2094.88 | 127.264
| Stone chips (150 Km pucca Carriage) |  | 0.1215 | M3 | P/M3 | 2999.84 | 364.4806
|  |  | Total for PCC Cutting & Restoration |  |  |  | 1162.5595
|  | Grand Total for 03 Leakages with PCC cutting in One day |  |  |  |  | 4757.1648
|  |  | For 01 Leakage with PCC cutting |  |  |  | 1586
| Junior Engineer |  | Assistant Engineer |  |  | Executive Engineer
P.H. Division, Begusarai

## Analysis leakage repair 75mm
Sub Estimate :- 23B
ANALYSIS OF LEAKAGE REPAIRING IN 75 MM DIAMETER HDPE PIPE (For pipe laid at 0.5 to 1.0m)
SL NO | Particulars |  | Quantity |  | Units | Rate | Amounts
1. (2.28) | Earthwork in excavation over areas (exceeding 30 cm in depth 1.5 in width as well as 10 sqm on plan) including disposal of excavated earth lead upto 50m and lift upto 1.5m, disposal earth to be levelled and neatly dressed.
| 75 mm dia Pipe | 3x0.3x1.0x1= | 0.9 | M3
|  |  | 0.9 | M3
|  | Add 5% extra for fittings = | 0.045 | M3
|  | Total= | 0.945 | M3 | P/M3 | 360.7 | 340.8615
2 | Filling available excavated earth (excluding rock) in trenches, plinth, sides of foundations etc. in layers not exceeding 20cm in depth, consolidating each deposited layer by ramming and watering, lead up to 50 m and lift upto 1.5 m.
|  |  | 0.9261 | M3 | P/M3 | 123.9 | 114.7438
3 | Providing material for leakage repairing
D- jointers
| 75 mm dia Pipe |  | 3 | Nos | Each | 588 | 1764
4 | Providing Labour for leakage repairing
0L27 | Plumber |  | 1 | Nos | Each | 391 | 391
0L70 | Semi Skilled Labour |  | 1 | Nos | Each | 318 | 318
0L05 | Helper |  | 2 | Nos | Each | 306 | 612
|  | Grand Total for 03 Leakages without PCC cutting in One day = |  |  |  |  | 3540.6053
|  | For 01 Leakage without PCC cutting = |  |  |  |  | 1180
1 15.2.1 | Demolishing cement concrete manually/by mechanical means including disposal of material within 50 metres lead as per direction of Engineer - in - charge.( in 10% length)
| 1:3:6 or richer mix | 3x0.3x1.0x0.15= | 0.135 | M3 | P/M3 | 970.9 | 131.0715
5(a) 4.1.3 | Providing and laying in position cement concrete of specified grade excluding the cost of centering and shuttering all work upto plinth level.
| 1:2:4 (1 cement: 2 coarse sand : 4 graded stone aggregate 40mm nominal size) |  | 0.135 | M3 | P/M3 | 3998.1 | 539.7435
5(b) | Carriage of the following materials from quarry to work site including loading, unloading and staking at work site as per specification & direction of E/I.
| Coarse Sand (100 Km pucca Carriage) |  | 0.06075 | M3 | P/M3 | 2094.88 | 127.264
| Stone chips (150 Km pucca Carriage) |  | 0.1215 | M3 | P/M3 | 2999.84 | 364.4806
|  |  | Total for PCC Cutting & Restoration |  |  |  | 1162.5595
|  | Grand Total for 03 Leakages with PCC cutting in One day |  |  |  |  | 4703.1648
|  |  | For 01 Leakage with PCC cutting |  |  |  | 1568
| Junior Engineer |  | Assistant Engineer |  |  | Executive Engineer
P.H. Division, Begusarai

## Analysis leakage repair 63 mm
Sub Estimate :- 23C
ANALYSIS OF LEAKAGE REPAIRING IN 63 MM DIAMETER HDPE PIPE (For pipe laid at 0.5 to 1.0m)
SL NO | Particulars |  | Quantity |  | Units | Rate | Amounts
1. (2.28) | Earthwork in excavation over areas (exceeding 30 cm in depth 1.5 in width as well as 10 sqm on plan) including disposal of excavated earth lead upto 50m and lift upto 1.5m, disposal earth to be levelled and neatly dressed.
| 63 mm dia Pipe | 3x0.3x1.0x1= | 0.9 | M3
|  |  | 0.9 | M3
|  | Add 5% extra for fittings = | 0.045 | M3
|  | Total= | 0.945 | M3 | P/M3 | 360.7 | 340.8615
2 | Filling available excavated earth (excluding rock) in trenches, plinth, sides of foundations etc. in layers not exceeding 20cm in depth, consolidating each deposited layer by ramming and watering, lead up to 50 m and lift upto 1.5 m.
|  |  | 0.9261 | M3 | P/M3 | 123.9 | 114.7438
3 | Providing material for leakage repairing
D- jointers
| 63 mm dia Pipe |  | 3 | Nos | Each | 535 | 1605
4 | Providing Labour for leakage repairing
0L27 | Plumber |  | 1 | Nos | Each | 391 | 391
0L70 | Semi Skilled Labour |  | 1 | Nos | Each | 318 | 318
0L05 | Helper |  | 2 | Nos | Each | 306 | 612
|  | Grand Total for 03 Leakages without PCC cutting in One day = |  |  |  |  | 3381.6053
|  | For 01 Leakage without PCC cutting = |  |  |  |  | 1127
1 15.2.1 | Demolishing cement concrete manually/by mechanical means including disposal of material within 50 metres lead as per direction of Engineer - in - charge.( in 10% length)
| 1:3:6 or richer mix | 3x0.3x1.0x0.15= | 0.135 | M3 | P/M3 | 970.9 | 131.0715
5(a) 4.1.3 | Providing and laying in position cement concrete of specified grade excluding the cost of centering and shuttering all work upto plinth level.
| 1:2:4 (1 cement: 2 coarse sand : 4 graded stone aggregate 40mm nominal size) |  | 0.135 | M3 | P/M3 | 3998.1 | 539.7435
5(b) | Carriage of the following materials from quarry to work site including loading, unloading and staking at work site as per specification & direction of E/I.
| Coarse Sand (100 Km pucca Carriage) |  | 0.06075 | M3 | P/M3 | 2094.88 | 127.264
| Stone chips (150 Km pucca Carriage) |  | 0.1215 | M3 | P/M3 | 2999.84 | 364.4806
|  |  | Total for PCC Cutting & Restoration |  |  |  | 1162.5595
|  | Grand Total for 03 Leakages with PCC cutting in One day |  |  |  |  | 4544.1648
|  |  | For 01 Leakage with PCC cutting |  |  |  | 1515
| Junior Engineer |  | Assistant Engineer |  |  | Executive Engineer
P.H. Division, Begusarai

## Analysis leakage repair 50mm
Sub Estimate :- 23D
ANALYSIS OF LEAKAGE REPAIRING IN 50 MM DIAMETER HDPE PIPE (For pipe laid at 0.5 to 1.0m)
SL NO | Particulars |  | Quantity |  | Units | Rate | Amounts
1. (2.28) | Earthwork in excavation over areas (exceeding 30 cm in depth 1.5 in width as well as 10 sqm on plan) including disposal of excavated earth lead upto 50m and lift upto 1.5m, disposal earth to be levelled and neatly dressed.
| 50 mm dia Pipe | 3x0.3x1.0x1= | 0.9 | M3
|  |  | 0.9 | M3
|  | Add 5% extra for fittings = | 0.045 | M3
|  | Total= | 0.945 | M3 | P/M3 | 360.7 | 340.8615
2 | Filling available excavated earth (excluding rock) in trenches, plinth, sides of foundations etc. in layers not exceeding 20cm in depth, consolidating each deposited layer by ramming and watering, lead up to 50 m and lift upto 1.5 m.
|  |  | 0.9261 | M3 | P/M3 | 123.9 | 114.7438
3 | Providing material for leakage repairing
D- jointers
| 50 mm dia Pipe |  | 3 | Nos | Each | 504 | 1512
4 | Providing Labour for leakage repairing
0L27 | Plumber |  | 1 | Nos | Each | 391 | 391
0L70 | Semi Skilled Labour |  | 1 | Nos | Each | 318 | 318
0L05 | Helper |  | 2 | Nos | Each | 306 | 612
|  | Grand Total for 03 Leakages without PCC cutting in One day = |  |  |  |  | 3288.6053
|  | For 01 Leakage without PCC cutting = |  |  |  |  | 1096
1 15.2.1 | Demolishing cement concrete manually/by mechanical means including disposal of material within 50 metres lead as per direction of Engineer - in - charge.( in 10% length)
| 1:3:6 or richer mix | 3x0.3x1.0x0.15= | 0.135 | M3 | P/M3 | 970.9 | 131.0715
5(a) 4.1.3 | Providing and laying in position cement concrete of specified grade excluding the cost of centering and shuttering all work upto plinth level.
| 1:2:4 (1 cement: 2 coarse sand : 4 graded stone aggregate 40mm nominal size) |  | 0.135 | M3 | P/M3 | 3998.1 | 539.7435
5(b) | Carriage of the following materials from quarry to work site including loading, unloading and staking at work site as per specification & direction of E/I.
| Coarse Sand (100 Km pucca Carriage) |  | 0.06075 | M3 | P/M3 | 2094.88 | 127.264
| Stone chips (150 Km pucca Carriage) |  | 0.1215 | M3 | P/M3 | 2999.84 | 364.4806
|  |  | Total for PCC Cutting & Restoration |  |  |  | 1162.5595
|  | Grand Total for 03 Leakages with PCC cutting in One day |  |  |  |  | 4451.1648
|  |  | For 01 Leakage with PCC cutting |  |  |  | 1484
| Junior Engineer |  | Assistant Engineer |  |  | Executive Engineer
P.H. Division, Begusarai

## Analysis leakage repair 40mm
Sub Estimate :-23E
ANALYSIS OF LEAKAGE REPAIRING IN 40 MM DIAMETER HDPE PIPE (For pipe laid at 0.5 to 1.0m)
SL NO | Particulars |  | Quantity |  | Units | Rate | Amounts
1. (2.28) | Earthwork in excavation over areas (exceeding 30 cm in depth 1.5 in width as well as 10 sqm on plan) including disposal of excavated earth lead upto 50m and lift upto 1.5m, disposal earth to be levelled and neatly dressed.
| 50 mm dia Pipe | 3x0.3x1.0x1= | 0.9 | M3
|  |  | 0.9 | M3
|  | Add 5% extra for fittings = | 0.045 | M3
|  | Total= | 0.945 | M3 | P/M3 | 360.7 | 340.8615
2 | Filling available excavated earth (excluding rock) in trenches, plinth, sides of foundations etc. in layers not exceeding 20cm in depth, consolidating each deposited layer by ramming and watering, lead up to 50 m and lift upto 1.5 m.
|  |  | 0.9261 | M3 | P/M3 | 123.9 | 114.7438
3 | Providing material for leakage repairing
D- jointers
| 50 mm dia Pipe |  | 3 | Nos | Each | 478 | 1434
4 | Providing Labour for leakage repairing
0L27 | Plumber |  | 1 | Nos | Each | 391 | 391
0L70 | Semi Skilled Labour |  | 1 | Nos | Each | 318 | 318
0L05 | Helper |  | 2 | Nos | Each | 306 | 612
|  | Grand Total for 03 Leakages without PCC cutting in One day = |  |  |  |  | 3210.6053
|  | For 01 Leakage without PCC cutting = |  |  |  |  | 1070
1 15.2.1 | Demolishing cement concrete manually/by mechanical means including disposal of material within 50 metres lead as per direction of Engineer - in - charge.( in 10% length)
| 1:3:6 or richer mix | 3x0.3x1.0x0.15= | 0.135 | M3 | P/M3 | 970.9 | 131.0715
5(a) 4.1.3 | Providing and laying in position cement concrete of specified grade excluding the cost of centering and shuttering all work upto plinth level.
| 1:2:4 (1 cement: 2 coarse sand : 4 graded stone aggregate 40mm nominal size) |  | 0.135 | M3 | P/M3 | 3998.1 | 539.7435
5(b) | Carriage of the following materials from quarry to work site including loading, unloading and staking at work site as per specification & direction of E/I.
| Coarse Sand (100 Km pucca Carriage) |  | 0.06075 | M3 | P/M3 | 2094.88 | 127.264
| Stone chips (150 Km pucca Carriage) |  | 0.1215 | M3 | P/M3 | 2999.84 | 364.4806
|  |  | Total for PCC Cutting & Restoration |  |  |  | 1162.5595
|  | Grand Total for 03 Leakages with PCC cutting in One day |  |  |  |  | 4373.1648
|  |  | For 01 Leakage with PCC cutting |  |  |  | 1458
| Junior Engineer |  | Assistant Engineer |  |  | Executive Engineer
P.H. Division, Begusarai

## elec (hidden)
Sub Estimate No.- 8B
energy Charges for 5 year
PUBLIC HEALTH DIVISION, HAJIPUR.
S.N. | Description |  | Quantity | Rate | Unit | Amount
1 | Cost of Energy charges
| HP of pump =3HP |  | 3
| 3 | HP | = | 2.238 | KKW
| Opreating Hour Average running |  |  | 8 | Hours/Day
| Unit Expenditure per year=HP*0.746*8*365*1.1 |  |  | 7253.8056 | Unit
| Energy Charges @ |  |  | 2.6 | per Unit | 18859.8946
| Fixed charges (3HPx100x365/30) |  | 3 | 100 | Per HP per month | 3650
| duty charges @ 6% of energy charges |  |  |  |  | 1131.5937
| Total |  |  |  |  | 23641.4882
23641.4882
| Therefore Annual Maintenance for one Year |  |  |  |  | 23641.4882
| Therefore Maintenance for five Year |  |  |  |  | 118207.4412
| Say |  |  |  |  | 118207
Executive Engineer
P.H. Division, Hajipur

## popforcast (hidden)
Population Forcast
1 | Block | #REF! | Scheme | 6B (MUSLIM TOLA) | 150
| Panchayat | #REF!
The Population of three decades are as under
Population
|  |  | 1991 | 2001 | 2011 | 2018
|  |  | 401.3158 | 532.8947 | 657.8947 | 750
|  |  | 401.3158 | 532.8947 | 657.8947 | 750
DESIGN OF POPULATION
The Population Forecast by
1- | Calculation by Arithmetic Increase Method
S.N. | Year | Population | Increase in Population = X
1 | 1991 | 401.3158
131.5789
2 | 2001 | 532.8947
125
3 | 2011 | 657.8947
| Total |  | 256.5789
| Average increase per decade = X = |  | 128.2895
| The future population are computed by using | [5 empty] | Value of
|  | PN | = | Population in forecast year |  | in 2022 | N = | 0.7 | 657.8947 | 89.8026 | 747.6974
| PN = PO+ (N x X ) | Po | = | Population in Last Census |  | in 2037 | N = | 2.2 | 657.8947 | 282.2368 | 940.1316
|  | N | = | No. of next decade |  | in 2052 | N = | 3.7 | 657.8947 | 474.6711 | 1132.5658
|  | X | = | Average increase per decade
| Population in base Year | in 2022 | = | 747.6974
| Population in intermediate Year | in 2037 | = | 940.1316
| Population in ultimate Year | in 2052 | = | 1132.5658
2- | Calculation by Geometric Mean Method
S.N. | Year | Population | Increase in Population = X | Percentage increase in Population = R
1 | 1991 | 401.3158
|  |  | 131.5789 | 0.32787
2 | 2001 | 532.8947 |  |  | 0.27732
|  |  | 125 | 0.23457
3 | 2011 | 657.8947
The Geometric Growth rate = R = 2√ (a) x (b)
|  | = | 27.7322 | % Per Decade
|  | PN | = | Population in forecast year |  | in 2022 | N = | 0.7 | 657.8947 | 1.2773 | 1.1869 | 780.8483
| PN = PO (1 + R/100)N | Po | = | Population in Last Census |  | in 2037 | N = | 2.2 | 657.8947 | 1.2773 | 1.7134 | 1127.2424
|  | N | = | No. of next decade |  | in 2052 | N = | 3.7 | 657.8947 | 1.2773 | 2.4735 | 1627.301
|  | R | = | Percentage increase in Population
| Population in base Year | in 2022 | = | 780.8483
| Population in intermediate Year | in 2037 | = | 1127.2424
| Population in ultimate Year | in 2052 | = | 1627.301
3- | Calculation by Incremental Increase Method
S.N. | Year | Population | Increase = X | Incremental Increase = Y
1 | 1991 | 401.3158
131.5789
2 | 2001 | 532.8947
|  |  | 125 | -6.5789
3 | 2011 | 657.8947
|  |  | 256.5789 | -6.5789 |  |  |  |  | Po | N * X | N(N+1) *Y/2 | PN = PO + N*X + N (N+1) Y / 2
|  | PN | = | Population in forecast year |  | in 2022 | N = | 0.7 | 657.8947 | 89.8026 | -3.9145 | 743.7829
| PN = PO + N*X + N (N+1) Y / 2 | Po | = | Population in Last Census |  | in 2037 | N = | 2.2 | 657.8947 | 282.2368 | -23.1579 | 916.9737
|  | X | = | 128.2895 |  | in 2052 | N = | 3.7 | 657.8947 | 474.6711 | -57.2039 | 1075.3618
|  | Y | = | -6.5789
| Population in base Year | in 2022 | = | 743.7829
| Population in intermediate Year | in 2037 | = | 916.9737
| Population in ultimate Year | in 2052 | = | 1075.3618
4 | Calculation by Decadal Increase Method
| Year | Population | Increase in Population | Decadal Increase
| 1991 | 401.3158 |  | in %
| 2001 | 532.8947 | 131.5789 | 32.7869
| 2011 | 657.8947 | 125 | 23.4568
| Total Increase: |  | 256.5789
Hence average increase per decade |  |  | 128 | 28.1218 | 2.8122 | % Increase
|  |  |  | %per year | % Increase
| Population in base Year | (Population 2011 + (Average increase per decade x 0.6)) |  |  | 734.6947 | 10.4533
| Population in intermediate Year | (Population 2011 + (Average increase per decade x 2.1)) |  |  | 926.6947 | 29.0063
| Population in ultimate Year | (Population 2011 + (Average increase per decade x 3.6)) |  |  | 1118.6947 | 41.1909
AVERAGE OF ALL METHODS
S.N. | Methods of Forecast |  | Expected Population in
|  | Base Year | Intermediate Year | Ultimate Year | Percentage of Increase from 2011
|  | in 2022 | in 2037 | in 2052
1 | Arithmetic Increase Method | 747.6974 | 940.1316 | 1132.5658 | 72.15 | 20.0417
2 | Geometric Mean Method | 780.8483 | 1127.2424 | 1627.301 | 147.3498 | 40.9305
3 | Incremental Increase Method | 743.7829 | 916.9737 | 1075.3618 | 63.455 | 17.6264
4 | Decadal Increase Method | 734.6947 | 926.6947 | 1118.6947 | 70.0416 | 19.456
| Average of all methods | 751.7558 | 977.7606 | 1238.4809 | 88.2491 | 24.5136
AVERAGE OF THREE METHODS
S.N. | Methods of Forecast |  | Expected Population in
|  | Base Year | Intermediate Year | Ultimate Year | Percentage of Increase from 2011
|  | in 2022 | in 2037 | in 2052
1 | Arithmetic Increase Method | 747.6974 | 940.1316 | 1132.5658 | 72.15 | 20.0417
2 | Geometric Mean Method | 780.8483 | 1127.2424 | 1627.301 | 147.3498 | 40.9305
3 | Incremental Increase Method | 743.7829 | 916.9737 | 1075.3618 | 63.455 | 17.6264
| Average of three methods | 757.4429 | 994.7825 | 1278.4096 | 94.3183 | 26.1995
Population of the Village is increasing rapidally. The Average Population Growth rate of 22.35 % per decade comes through Average of three methods which is very near to Average Growth rate of Bihar (22.49), is adapted here for Population Forecasting.
Sl. | Year |  | Population
1 | Initial Year | in 2022 | 757.4429
2 | Prospective Year | in 2037 | 994.7825
3 | Ultimate Year | in 2052 | 1278.4096
POPULATION ADOPTED FOR DESIGN |  |  |  | Percentage of increase
1 | Population in Census Year | in 2011 | 657.8947 | From 2011
2 | Population in Base Year | in 2022 | 757.4429 | 15.1313 | % Increased | 99.5481 | 2.5219 | 3
3 | Population in Intermediate Year | in 2037 | 994.7825 | 51.2069 | % Increased | 336.8878 | 2.4384 | 2
4 | Population in Ultimate Year | in 2052 | 1278.4096 | 94.3183 | % Increased | 620.5148 | 2.62 | 3
As per norms the population is to be fed through house connection @70 lpcd including 15% Uaccounted flow of water. Demand of water for initial, intermediate and ultimate stages are as under:
| Year | Population |  |  | Demand
@81 LPCD in MLD
| in 2011 | 657.8947 |  |  | 0.053289 | 53289.4737
| in 2022 | 757.4429 |  |  | 0.061353 | 61352.8724
| in 2037 | 994.7825 |  |  | 0.080577 | 80577.3856
| in 2052 | 1278.4096 |  |  | 0.10355 | 103551.1741
Executive Engineer P.H. Division, Hajipur

## 23Analysis leakage repair 9 (2)
Sub Estimate :- 24A
ANALYSIS OF LEAKAGE REPAIRING IN 90 MM DIAMETER HDPE PIPE (For pipe laid at 0.0 to 0.5m)
SL NO | Particulars |  | Quantity |  | Units | Rate | Amounts
1. (2.28) | Earthwork in excavation over areas (exceeding 30 cm in depth 1.5 in width as well as 10 sqm on plan) including disposal of excavated earth lead upto 50m and lift upto 1.5m, disposal earth to be levelled and neatly dressed.
| 90 mm dia Pipe | 3x0.3x1.0x0.5= | 0.45 | M3
|  |  | 0.45 | M3
|  | Add 5% extra for fittings = | 0.0225 | M3
|  | Total= | 0.4725 | M3 | P/M3 | 360.7 | 170.4307
2 | Filling available excavated earth (excluding rock) in trenches, plinth, sides of foundations etc. in layers not exceeding 20cm in depth, consolidating each deposited layer by ramming and watering, lead up to 50 m and lift upto 1.5 m.
|  |  | 0.46305 | M3 | P/M3 | 123.9 | 57.3719
3 | Providing material for leakage repairing
D- jointers
| 90 mm dia Pipe |  | 3 | Nos | Each | 606 | 1818
4 | Providing Labour for leakage repairing
0L27 | Plumber |  | 1 | Nos | Each | 391 | 391
0L70 | Semi Skilled Labour |  | 1 | Nos | Each | 318 | 318
0L05 | Helper |  | 2 | Nos | Each | 306 | 612
|  | Grand Total for 03 Leakages without PCC cutting in One day = |  |  |  |  | 3366.8026
|  | For 01 Leakage without PCC cutting = |  |  |  |  | 1122
1 15.2.1 | Demolishing cement concrete manually/by mechanical means including disposal of material within 50 metres lead as per direction of Engineer - in - charge.( in 10% length)
| 1:3:6 or richer mix | 3x0.3x1.0x0.15= | 0.135 | M3 | P/M3 | 970.9 | 131.0715
5(a) 4.1.3 | Providing and laying in position cement concrete of specified grade excluding the cost of centering and shuttering all work upto plinth level.
| 1:2:4 (1 cement: 2 coarse sand : 4 graded stone aggregate 40mm nominal size) |  | 0.135 | M3 | P/M3 | 3998.1 | 539.7435
5(b) | Carriage of the following materials from quarry to work site including loading, unloading and staking at work site as per specification & direction of E/I.
| Coarse Sand (100 Km pucca Carriage) |  | 0.06075 | M3 | P/M3 | 2094.88 | 127.264
| Stone chips (150 Km pucca Carriage) |  | 0.1215 | M3 | P/M3 | 2999.84 | 364.4806
|  |  | Total for PCC Cutting & Restoration |  |  |  | 1162.5595
|  | Grand Total for 03 Leakages with PCC cutting in One day |  |  |  |  | 4529.3622
|  |  | For 01 Leakage with PCC cutting |  |  |  | 1510
| Junior Engineer |  | Assistant Engineer |  |  | Executive Engineer
P.H. Division, Begusarai

## Analysis leakage repair 75m (2)
Sub Estimate :- 24B
ANALYSIS OF LEAKAGE REPAIRING IN 75 MM DIAMETER HDPE PIPE (For pipe laid at 0.0 to 0.5 m)
SL NO | Particulars |  | Quantity |  | Units | Rate | Amounts
1. (2.28) | Earthwork in excavation over areas (exceeding 30 cm in depth 1.5 in width as well as 10 sqm on plan) including disposal of excavated earth lead upto 50m and lift upto 1.5m, disposal earth to be levelled and neatly dressed.
| 75 mm dia Pipe | 3x0.3x1.0x0.5= | 0.45 | M3
|  |  | 0.45 | M3
|  | Add 5% extra for fittings = | 0.0225 | M3
|  | Total= | 0.4725 | M3 | P/M3 | 360.7 | 170.4307
2 | Filling available excavated earth (excluding rock) in trenches, plinth, sides of foundations etc. in layers not exceeding 20cm in depth, consolidating each deposited layer by ramming and watering, lead up to 50 m and lift upto 1.5 m.
|  |  | 0.46305 | M3 | P/M3 | 123.9 | 57.3719
3 | Providing material for leakage repairing
D- jointers
| 75 mm dia Pipe |  | 3 | Nos | Each | 588 | 1764
4 | Providing Labour for leakage repairing
0L27 | Plumber |  | 1 | Nos | Each | 391 | 391
0L70 | Semi Skilled Labour |  | 1 | Nos | Each | 318 | 318
0L05 | Helper |  | 2 | Nos | Each | 306 | 612
|  | Grand Total for 03 Leakages without PCC cutting in One day = |  |  |  |  | 3312.8026
|  | For 01 Leakage without PCC cutting = |  |  |  |  | 1104
1 15.2.1 | Demolishing cement concrete manually/by mechanical means including disposal of material within 50 metres lead as per direction of Engineer - in - charge.( in 10% length)
| 1:3:6 or richer mix | 3x0.3x1.0x0.15= | 0.135 | M3 | P/M3 | 970.9 | 131.0715
5(a) 4.1.3 | Providing and laying in position cement concrete of specified grade excluding the cost of centering and shuttering all work upto plinth level.
| 1:2:4 (1 cement: 2 coarse sand : 4 graded stone aggregate 40mm nominal size) |  | 0.135 | M3 | P/M3 | 3998.1 | 539.7435
5(b) | Carriage of the following materials from quarry to work site including loading, unloading and staking at work site as per specification & direction of E/I.
| Coarse Sand (100 Km pucca Carriage) |  | 0.06075 | M3 | P/M3 | 2094.88 | 127.264
| Stone chips (150 Km pucca Carriage) |  | 0.1215 | M3 | P/M3 | 2999.84 | 364.4806
|  |  | Total for PCC Cutting & Restoration |  |  |  | 1162.5595
|  | Grand Total for 03 Leakages with PCC cutting in One day |  |  |  |  | 4475.3622
|  |  | For 01 Leakage with PCC cutting |  |  |  | 1492
| Junior Engineer |  | Assistant Engineer |  |  | Executive Engineer
P.H. Division, Begusarai

## Analysis leakage repair 63 (2)
Sub Estimate :- 23C
ANALYSIS OF LEAKAGE REPAIRING IN 63 MM DIAMETER HDPE PIPE (For pipe laid at 0.0 to 0.5m)
SL NO | Particulars |  | Quantity |  | Units | Rate | Amounts
1. (2.28) | Earthwork in excavation over areas (exceeding 30 cm in depth 1.5 in width as well as 10 sqm on plan) including disposal of excavated earth lead upto 50m and lift upto 1.5m, disposal earth to be levelled and neatly dressed.
| 63 mm dia Pipe | 3x0.3x1.0x0.5= | 0.45 | M3
|  |  | 0.45 | M3
|  | Add 5% extra for fittings = | 0.0225 | M3
|  | Total= | 0.4725 | M3 | P/M3 | 360.7 | 170.4307
2 | Filling available excavated earth (excluding rock) in trenches, plinth, sides of foundations etc. in layers not exceeding 20cm in depth, consolidating each deposited layer by ramming and watering, lead up to 50 m and lift upto 1.5 m.
|  |  | 0.46305 | M3 | P/M3 | 123.9 | 57.3719
3 | Providing material for leakage repairing
D- jointers
| 63 mm dia Pipe |  | 3 | Nos | Each | 535 | 1605
4 | Providing Labour for leakage repairing
0L27 | Plumber |  | 1 | Nos | Each | 391 | 391
0L70 | Semi Skilled Labour |  | 1 | Nos | Each | 318 | 318
0L05 | Helper |  | 2 | Nos | Each | 306 | 612
|  | Grand Total for 03 Leakages without PCC cutting in One day = |  |  |  |  | 3153.8026
|  | For 01 Leakage without PCC cutting = |  |  |  |  | 1051
1 15.2.1 | Demolishing cement concrete manually/by mechanical means including disposal of material within 50 metres lead as per direction of Engineer - in - charge.( in 10% length)
| 1:3:6 or richer mix | 3x0.3x1.0x0.15= | 0.135 | M3 | P/M3 | 970.9 | 131.0715
5(a) 4.1.3 | Providing and laying in position cement concrete of specified grade excluding the cost of centering and shuttering all work upto plinth level.
| 1:2:4 (1 cement: 2 coarse sand : 4 graded stone aggregate 40mm nominal size) |  | 0.135 | M3 | P/M3 | 3998.1 | 539.7435
5(b) | Carriage of the following materials from quarry to work site including loading, unloading and staking at work site as per specification & direction of E/I.
| Coarse Sand (100 Km pucca Carriage) |  | 0.06075 | M3 | P/M3 | 2094.88 | 127.264
| Stone chips (150 Km pucca Carriage) |  | 0.1215 | M3 | P/M3 | 2999.84 | 364.4806
|  |  | Total for PCC Cutting & Restoration |  |  |  | 1162.5595
|  | Grand Total for 03 Leakages with PCC cutting in One day |  |  |  |  | 4316.3622
|  |  | For 01 Leakage with PCC cutting |  |  |  | 1439
| Junior Engineer |  | Assistant Engineer |  |  | Executive Engineer
P.H. Division, Begusarai

## Analysis leakage repair 50m (2)
Sub Estimate :- 23D
ANALYSIS OF LEAKAGE REPAIRING IN 50 MM DIAMETER HDPE PIPE (For pipe laid at 0.0 to 0.5m)
SL NO | Particulars |  | Quantity |  | Units | Rate | Amounts
1. (2.28) | Earthwork in excavation over areas (exceeding 30 cm in depth 1.5 in width as well as 10 sqm on plan) including disposal of excavated earth lead upto 50m and lift upto 1.5m, disposal earth to be levelled and neatly dressed.
| 50 mm dia Pipe | 3x0.3x1.0x0.5= | 0.45 | M3
|  |  | 0.45 | M3
|  | Add 5% extra for fittings = | 0.0225 | M3
|  | Total= | 0.4725 | M3 | P/M3 | 360.7 | 170.4307
2 | Filling available excavated earth (excluding rock) in trenches, plinth, sides of foundations etc. in layers not exceeding 20cm in depth, consolidating each deposited layer by ramming and watering, lead up to 50 m and lift upto 1.5 m.
|  |  | 0.46305 | M3 | P/M3 | 123.9 | 57.3719
3 | Providing material for leakage repairing
D- jointers
| 50 mm dia Pipe |  | 3 | Nos | Each | 504 | 1512
4 | Providing Labour for leakage repairing
0L27 | Plumber |  | 1 | Nos | Each | 391 | 391
0L70 | Semi Skilled Labour |  | 1 | Nos | Each | 318 | 318
0L05 | Helper |  | 2 | Nos | Each | 306 | 612
|  | Grand Total for 03 Leakages without PCC cutting in One day = |  |  |  |  | 3060.8026
|  | For 01 Leakage without PCC cutting = |  |  |  |  | 1020
1 15.2.1 | Demolishing cement concrete manually/by mechanical means including disposal of material within 50 metres lead as per direction of Engineer - in - charge.( in 10% length)
| 1:3:6 or richer mix | 3x0.3x1.0x0.15= | 0.135 | M3 | P/M3 | 970.9 | 131.0715
5(a) 4.1.3 | Providing and laying in position cement concrete of specified grade excluding the cost of centering and shuttering all work upto plinth level.
| 1:2:4 (1 cement: 2 coarse sand : 4 graded stone aggregate 40mm nominal size) |  | 0.135 | M3 | P/M3 | 3998.1 | 539.7435
5(b) | Carriage of the following materials from quarry to work site including loading, unloading and staking at work site as per specification & direction of E/I.
| Coarse Sand (100 Km pucca Carriage) |  | 0.06075 | M3 | P/M3 | 2094.88 | 127.264
| Stone chips (150 Km pucca Carriage) |  | 0.1215 | M3 | P/M3 | 2999.84 | 364.4806
|  |  | Total for PCC Cutting & Restoration |  |  |  | 1162.5595
|  | Grand Total for 03 Leakages with PCC cutting in One day |  |  |  |  | 4223.3622
|  |  | For 01 Leakage with PCC cutting |  |  |  | 1408
| Junior Engineer |  | Assistant Engineer |  |  | Executive Engineer
P.H. Division, Begusarai

## Analysis leakage repair 40m (2)
Sub Estimate :-23E
ANALYSIS OF LEAKAGE REPAIRING IN 40 MM DIAMETER HDPE PIPE (For pipe laid at 0.0 to 0.5m)
SL NO | Particulars |  | Quantity |  | Units | Rate | Amounts
1. (2.28) | Earthwork in excavation over areas (exceeding 30 cm in depth 1.5 in width as well as 10 sqm on plan) including disposal of excavated earth lead upto 50m and lift upto 1.5m, disposal earth to be levelled and neatly dressed.
| 50 mm dia Pipe | 3x0.3x1.0x0.5= | 0.45 | M3
|  |  | 0.45 | M3
|  | Add 5% extra for fittings = | 0.0225 | M3
|  | Total= | 0.4725 | M3 | P/M3 | 360.7 | 170.4307
2 | Filling available excavated earth (excluding rock) in trenches, plinth, sides of foundations etc. in layers not exceeding 20cm in depth, consolidating each deposited layer by ramming and watering, lead up to 50 m and lift upto 1.5 m.
|  |  | 0.46305 | M3 | P/M3 | 123.9 | 57.3719
3 | Providing material for leakage repairing
D- jointers
| 50 mm dia Pipe |  | 3 | Nos | Each | 478 | 1434
4 | Providing Labour for leakage repairing
0L27 | Plumber |  | 1 | Nos | Each | 391 | 391
0L70 | Semi Skilled Labour |  | 1 | Nos | Each | 318 | 318
0L05 | Helper |  | 2 | Nos | Each | 306 | 612
|  | Grand Total for 03 Leakages without PCC cutting in One day = |  |  |  |  | 2982.8026
|  | For 01 Leakage without PCC cutting = |  |  |  |  | 994
1 15.2.1 | Demolishing cement concrete manually/by mechanical means including disposal of material within 50 metres lead as per direction of Engineer - in - charge.( in 10% length)
| 1:3:6 or richer mix | 3x0.3x1.0x0.15= | 0.135 | M3 | P/M3 | 970.9 | 131.0715
5(a) 4.1.3 | Providing and laying in position cement concrete of specified grade excluding the cost of centering and shuttering all work upto plinth level.
| 1:2:4 (1 cement: 2 coarse sand : 4 graded stone aggregate 40mm nominal size) |  | 0.135 | M3 | P/M3 | 3998.1 | 539.7435
5(b) | Carriage of the following materials from quarry to work site including loading, unloading and staking at work site as per specification & direction of E/I.
| Coarse Sand (100 Km pucca Carriage) |  | 0.06075 | M3 | P/M3 | 2094.88 | 127.264
| Stone chips (150 Km pucca Carriage) |  | 0.1215 | M3 | P/M3 | 2999.84 | 364.4806
|  |  | Total for PCC Cutting & Restoration |  |  |  | 1162.5595
|  | Grand Total for 03 Leakages with PCC cutting in One day |  |  |  |  | 4145.3622
|  |  | For 01 Leakage with PCC cutting |  |  |  | 1382
| Junior Engineer |  | Assistant Engineer |  |  | Executive Engineer
P.H. Division, Begusarai

## 26.rep_riser
SUB ESTIMATE NO - 26
Repairing of riser and delivery pipe with CPVC pipe and providing gun metal Gate valve.
S.No. | Description | Qty |  | Unit | Rate | Amount
1 | Providing and fixing Chlorinated Polyvinyl Chloride (CPVC) pipes, having thermal stability for hot & cold water supply, including all CPVC plain & brass threaded fittings, including fixing the pipe with clamps at 1.00 m spacing. This includes jointing of pipes & fittings with one step CPVC solvent cement and testing of joints complete as per direction of Engineer in Charge.
18.7.6 | Riser Pipe 50mm dia nominal bore | 1 | M | PM | 791 | 791
18.9.7 | Delivery Pipe 80mm dia nominal bore | 1 | M | PM | 1889.5 | 1889.5
Replacement of Gun metal Gate valve. (50 mm dia.)
S.No. | Description | Qty |  | Unit | Rate | Amount
1 . Chattisgarh SOR | Providing and fixing G. I. Union in G.I. Pipe line i/c cutting threading testing etc. complete (Old work) confirming to IS1879
6.23 | 50mm dia | 1 | No. | each | 677 | 677
2. Chattisgarh SOR | Providing and fixing G. I. socket in G.I. Pipe line i/c cutting threading testing etc. complete (Old work) confirming to IS 1879
6.25 | 50mm dia | 1 | No. | each | 140 | 140
3 BCD SOR | Providing and fixing gun metal gate valve with C.I. wheel of approved quality (screwed end) :
18.17.4 | 50 mm nominal bore |  |  |  |  | 925.2715
| Total |  |  |  |  | 1742.2715
[5 empty] | Say | 1742
Replacement of Gun metal Gate valve. (80 mm dia.)
1. Chattisgarh SOR | Providing and fixing G. I. Union in G.I. Pipe line i/c cutting threading testing etc. complete (Old work) confirming to IS1879
6.23 | 80mm dia | 1 | No. | each | 1641 | 1641
2. Chattisgarh SOR | Providing and fixing G. I. socket in G.I. Pipe line i/c cutting threading testing etc. complete (Old work) confirming to IS 1879
6.25 | 80mm dia. | 1 | No. | each | 272 | 272
3 BCD SOR | Providing and fixing gun metal gate valve with C.I. wheel of approved quality (screwed end) :
18.17.4 | 80 mm nominal bore | 1 | No. | each | 2227.6 | 2346.9994
[5 empty] | Total | 4259.9994
[5 empty] | Say | 4260
| Junior Engineer Assistant Engineer |  |  | Executive Engineer
P.H. Division, Begusarai

## 27 dev_TW
Sub Estimate- 27
Development of 150mm x 100mm dia H/Y Tube well
S.No. | Description | Qty. |  | Unit | Rate | Amount
1 | Providing all materials, tools and tackles at site for opening all electrical connections of 3 HP Sub Motor and dismantling of delivery line & taken out submersible motor Pump with column pipe from Tube Well. | 1 | Job | P/Job | 1887.587 | 1887.587
2 24.12 | Development of tube well in accordance with IS : 2800 (part I) and IS: 11189, to establish maximum rate of usable water yield without sand content (beyond permissible limit), with required capacity air compressor, running the compressor for required time till well is fully develo ped, measuring yield of well by "V" notch method or any other approved method, measuring static level & draw down etc. by step draw down method, collecting water sampl & getting tested in approved laboratory, i/c disinfection of tubewell, all complete,including hire & labour charges of air compressor, tools & accessories etc., all as per requirement and direction of Engineer-in-charge. | 8 | Hrs. | P/H | 916.8 | 7334.4
3 | Transportation and erection of developing equipments & all other required tools and M/C by and suitable mechanical means including all cost of loading, unloading, placing at work site and back after completion of work as per S/D of E/I. | 1 | No. | Each | 5000 | 5000
4 | Providing all labours, tools and tackles at site for lowering of 3 HP Submersible motor pump with column pipe into the Tubwell, doing all electric connection, re-fitting nut bolt & refitting deleviry line & testing on load | 1 | Job | P/Job | 1887.587 | 1887.587
|  | TOTAL |  |  |  | 16109.574
[5 empty] | Say | 16110
|  | Assistant Engineer |  | Executive Engineer
P.H. Division, Begusarai

## 28 rep_rcc sta
Sub Est. No. 28
Repair of RCC Staging 4.0M x 3.0M x 8.0M High
S.N. | Particulars | [5 empty] | Quantity |  | Unit | Rate | Amount
1A 2.8.1 | Earth work in excavation in foundation trenches or drains(not exceeding 1.5 m in width or 10 sqm on plan) including dressing of sides and ramming of bottoms, lift upto 1.5 m . including getting out the excavated soil and disposal of surplus excavated soil as directed, within a lead of 50 m. All Kinds of soil
In foundation
| 4 | 1.95 | 1.95 | 1.35 | = | 20.5335
| 2 | 2.3 | 0.25 | 0.25 | = | 0.2875
| 2 | 1.3 | 0.25 | 0.25 | = | 0.1625
| 1 | 1 | 1 | 0.575 | = | 0.575
| 1 | 1.2 | 0.9 | 0.275 | = | 0.297
[6 empty] | 21.8555 |  | M | P/M | 360.7 | 0
1B 2.26 | Filling available excavated earth (excluding rock) in trenches, plinth, sides of foundations etc. in layers not exceeding 20 cm in depth: consolidating each deposited layer by ramming and watering lead | [6 empty] | M | P/M | 123.9 | 0
2- 2.28 | Providing clean coarse sand filling in foundation trenches or in plinth including ramming & watering as per specification & direction of E/I including cost of materials taxes & royalty.
Steps
| 1 | 1.2 | 0.9 | 0.1 | = | 0.108
In Foundation of column
| 4 | 1.95 | 1.95 | 0.1 | = | 1.521
In Ladder fixing block at GL
| 1 | 1 | 1 | 0.1 | = | 0.1
Under Tie beam at G.L.
| 2 | 3.95 | 0.25 | 0.1 | = | 0.1975
| 2 | 2.95 | 0.25 | 0.1 | = | 0.1475
In Plinth
| 1 | 4 | 3 | 0.28 | = | 3.36
[6 empty] | 5.434 |  | M3 | P/M3 | 287.3 | 0
3- 11.72 | Providing designation of 100A Brick flat Soling joints filled with local sand including cost of watering, taxes & royalty all complete as per specification & direction of E/I.
Steps
| 1 | 1.2 | 0.9 |  | = | 1.08
In Foundation of column
| 4 | 1.95 | 1.95 |  | = | 15.21
In Ladder fixing block at GL
| 1 | 1 | 1 |  | = | 1
Under Tie beam at G.L.
| 2 | 3.95 | 0.25 |  | = | 1.975
| 2 | 2.95 | 0.25 |  | = | 1.475
In Plinth
| 1 | 4 | 3 |  | = | 12
[6 empty] | 32.74 |  | M2 | P/M2 | 283.3 | 0
4- 4.1.3 | Providing and laying in position cement concrete of specified grade excluding the cost of centering and shuttering all work up to plinth
1:2:4 (1 cement: 2 coarse sand : 4 graded stone aggregate 40mm nominal size) (M15)
Steps
| 1 | 1.2 | 0.9 | 0.1 | = | 0.108
In Foundation of column
| 4 | 1.95 | 1.95 | 0.075 | = | 1.1407
In Ladder fixing block at GL
| 1 | 1 | 1 | 0.4 | = | 0.4
Under Tie beam at G.L.
| 2 | 3.95 | 0.25 | 0.1 | = | 0.1975
| 2 | 2.95 | 0.25 | 0.1 | = | 0.1475
In Plinth
| 1 | 4 | 3 | 0.1 | = | 1.2
[6 empty] | 3.1938 |  | M3 | P/M3 | 3998.1 | 0
4 A- 5.1.2 | Providing and laying in position reinforced cement concrete of specified grade excluding the cost of centring and shuttering all work up to plinth
1:1.5:3 (1 cement: 1.5 coarse sand : 3 graded stone aggregate 20mm nominal size)
| No | Length | Width | Height (av.) | Sub Qty.
In foundation
| 4 | 1.8 | 1.8 | 0.3 | = | 3.888
| 4 | 0.45 | 0.45 | 0.15 | = | 0.1215
| 4 | 0.3 | 0.3 | 0.65 | = | 0.234
| In Tie beam at G.L. |  |  |  | =
| 2 | 3.95 | 0.25 | 0.35 | = | 0.69125
| 2 | 2.95 | 0.25 | 0.35 | = | 0.51625
[6 empty] | 5.451 |  | M3 | P/M3 | 4688.3 | 0
4 B- 5.9.5 | Centring and shuttering including struting, propping etc. and removal of form for:
Lintels, beams, plinth beams etc.
In foundation
| 16 | 1.8 | 0.3 |  | = | 8.64
| 16 | 0.45 | 0.15 |  | = | 1.08
| 16 | 0.3 | 0.65 |  | = | 3.12
In Tie beam at G.L.
| 4 | 3.95 | 0.35 |  | = | 5.53
| 4 | 2.95 | 0.35 |  | = | 4.13
[6 empty] | 22.5 |  | M2 | P/M2 | 404.7 | 0
5- 6.1.14A | Providing designation 100A brick work in C.M. (1:6) in foundation & plinth with approved quality of clean coarse sand of F.M. 2 to 2.5 including providing 10 mm thick mortar joints, cost of screening materials, racking out joints to 15 mm depth curing taxes & reality all complete as per specification & direction of E/I.
Brick work with bricks of class designation 100A in plinth in :
Cement mortar 1:6 (1 Cement : 6 Sand)
| No | Length | Width | Height (av.) | Sub Qty.
Long Wall
| 2 | 3.95 | 0.25 | 0.15 | = | 0.29625
Short Wall
| 2 | 2.95 | 0.25 | 0.15 | = | 0.22125
In steps
| 1 | 1.2 | 0.9 | 0.15 | = | 0.162
| 1 | 1.2 | 0.6 | 0.15 | = | 0.108
| 1 | 1.2 | 0.3 | 0.15 | = | 0.054
[6 empty] | 0.8415 |  | M3 | P/M3 | 4819.9 | 0
6 A- 5.1.2 | Providing and laying in position Reinforced cement concrete of specified grade excluding the cost of centering and shuttering all work up to plinth
1:1.5:3 (1 cement: 1.5 coarse sand : 3 graded stone aggregate 20mm nominal size)
In Column up to PL
| 4 | 0.3 | 0.3 | 0.45 | = | 0.162
In band at plinth
| 2 | 3.95 | 0.25 | 0.075 | = | 0.14813
| 2 | 2.95 | 0.25 | 0.075 | = | 0.11063
[6 empty] | 0.42075 |  | M3 | P/M3 | 4688.3 | 0
6B 4.12 | Extra for providing and mixing water prooding material in cement concrete work in the proportion recommended by the manufacturers. (In band at Plinth) | [6 empty] | Kg. | per 50 kg cement | 57.16 | 0
6 C- 5.9.5 | Centering and shuttering including strutting, propping etc. and removal of form for:
Lintels, beams, plinth beams etc.
In Column up to PL
| 16 | 0.3 | 0.45 |  | = | 2.16
In band at plinth
| 4 | 3.95 | 0.075 |  | = | 1.185
| 4 | 2.95 | 0.075 |  | = | 0.885
[6 empty] | 4.23 |  | M2 | P/M2 | 404.7 | 0
7 A- 5.2.2 | Reinforced cement concrete work in wall (any thickness), inclusing attached pilasters, buttresses, plinth and string courses, fillets, coloumns, plinth and string courses, pillars, piers, abutments, posts and struts etc. up to five floor level excluding the cots of centring, shuttering, finishing and reinforcement.
1:1.5:3 (1 cement: 1.5 coarse sand : 3 graded stone aggregate 20mm nominal size)
| No | Length | Width | Height (av.) | Sub Qty.
In band at Lintels level
| 2 | 1.5 | 0.25 | 0.1 | = | 0.075
In beam B1, B2
| 2 | 4.5 | 0.25 | 0.2 | = | 0.45
| 2 | 3 | 0.25 | 0.2 | = | 0.3
In beam B3, B4
| 2 | 4.5 | 0.25 | 0.3 | = | 0.675
| 2 | 3 | 0.25 | 0.3 | = | 0.45
In beam B5, B6
| 2 | 5 | 0.25 | 0.25 | = | 0.625
| 2 | 3 | 0.25 | 0.25 | = | 0.375
In Column from PL to Roof level
| 4 | 0.3 | 0.3 | 8 | = | 2.88
For parapet post
| 8 | 0.125 | 0.125 | 0.85 | = | 0.10625
[6 empty] | 5.9363 |  | M3 | P/M3 | 5670 | 0
7 B- 5.9.5 | Centering and shuttering including strutting, propping etc. and removal of form for:
Lintels, beams, plinth beams etc.
In Column up to Roof level
| 16 | 0.3 | 8 |  | = | 38.4
In beams
| 4 | 4 | 0.2 |  | = | 3.2
| 4 | 3 | 0.2 |  | = | 2.4
| 6 | 4.5 | 0.3 |  | = | 8.1
| 6 | 3.5 | 0.3 |  | = | 6.3
| 6 | 5 | 0.25 |  | = | 7.5
| 6 | 3.5 | 0.25 |  | = | 5.25
In band at lintel
| 4 | 1.5 | 0.1 |  | = | 0.6
For parapet post
| 32 | 0.125 | 0.85 |  | = | 3.4
[6 empty] | 75.15 |  | M2 | P/M2 | 404.7 | 0
8 A- 5.3 | Reinforced cement concrete work in beams,suspended floors, roofs having slope upto 15, landings,balconiec, shelves, chajjas, lintels, bands, plain window sills, staircases and spiral stair cases upto floor five level excludingthe cost of centring, shuttering, finishing and reinforement with 1:2:4 (1 cement:2 coarse sand:4 graded stone aggregate 20 mm nominal size).
| No | Length | Width | Height (av.) | Sub Qty.
Chajja
| 2 | 1.1 | 0.45 | 0.063 | = | 0.06237
In shelves
| 4 | 1.05 | 0.45 | 0.063 | = | 0.11907
[6 empty] | 0.18144 |  | M3 | P/M3 | 5335.9 | 0
8 B- 5.9.3 | Centering and shuttering including strutting, propping etc. and removal of form for:
Chajja
| 2 | 1.1 | 0.45 |  | = | 0.99
| 2 | 1.1 | 0.5 |  | = | 1.1
| 4 | 0.45 | 0.063 |  | = | 0.1134
[6 empty] | 2.2034 |  | M2 | P/M2 | 437.5 | 0
9- 6.1.14B + 6.3B | Brick work with bricks of class designation 100A in foundation and plinth in :
Cement mortar 1:6 (1 Cement : 6 Sand)
Extra for brick work in superstructure above plinth upto V floor
| 2 | 3.95 | 0.25 | 2.7 | = | 5.3325
| 2 | 2.95 | 0.25 | 2.7 | = | 3.9825
In shelves
| 2 | 0.2 | 0.125 | 2.1 | = | 0.105
| Deduction |  |  |  |  | 9.42
For door
| 1 | 0.9 | 0.25 | 2.1 | = | 0.4725
For window
| 1 | 0.9 | 0.25 | 1.2 | = | 0.27 |  |  |  | 4540.3
| Total deduction |  |  |  |  | 0.7425 |  |  |  | 803.2
| Net Quantity |  |  |  |  | 8.6775 |  | M3 | P/M3 | 5343.5 | 0
10 A- 5.2.2 | Providing R.C.C. M-200 with nominal mix of (1:1.5:3) in roof slab
| No | Length | Width | Height (av.) | Sub Qty.
Roof Slab
| 1 | 5 | 3.5 | 0.15 | = | 2.625
| 1 | 4.7 | 3.7 | 0.1 | = | 1.739
Landing
| 3 | 0.6 | 0.6 | 0.15 | = | 0.162
[6 empty] | 4.526 |  | M3 | P/M3 | 5670 | 0
10 B- 5.9.3 | Centring and shuttering including struting, propping etc. and removal of form for:
In Roof slab
| No | Length | Width | Height (av.) | Sub Qty.
| 1 | 4.5 | 3 |  | = | 13.5
| 1 | 4.2 | 3.2 |  | = | 13.44
| 2 | 5 | 0.15 |  | = | 1.5
| 2 | 3.5 | 0.15 |  | = | 1.05
| 2 | 4.7 | 0.1 |  | = | 0.94
| 2 | 3.7 | 0.1 |  | = | 0.74
| 3 | 0.6 | 0.6 |  | = | 1.08
| 3 | 0.6 | 0.15 |  | = | 0.27
| 6 | 0.6 | 0.15 |  | = | 0.54
[6 empty] | 33.06 |  | M2 | P/M2 | 437.5 | 0
11- 5.22.7A | Reinforcement for RCC work including stragihtening, cutting, bending & placing in position and binding all complete.
6 mm to 16 mm tor steel
| Total Reinforcement. @1.60% of Vol. Of Concrete (Kg/cuM) |  |  |  |  | = |  | Kg. | P/Kg. | 94.5 | 0
12-A 10.5.1 | Providing and fixing 1mm thick M.S. sheet door with frame of 40x40x6mm angle iron and 3mm M.S. gusset plates at the junctions and corners, all necessary fittings complete, including applying a priming coat of approved steel primer.
| Door D | 1 | 0.9 | 2.1 | = | 1.89
| Window | 1 | 0.9 | 1.2 | = | 1.08
[6 empty] | 2.97 | 2.97 | M3 | P/M3 | 3653 | 10849.41
12-B 9.48.1 | Providing and fixing the M.S. grill of required pattern in frames of windows etc. with M.S. flat. Square or round bars etc. all complete
fixed to steel windows by welding.
| No | Length | Width | Height (av.) | Sub Qty.
For windows
| 1 | 1.2 | x | 0.9 | = | 1.08 | M2
[5 empty] | @ | 25 | Kg/M2
[6 empty] | 27 | 27 | Kg. | P/Kg. | 144.5 | 3901.5
13- 5.18.3 | Providing precast cement concrete jali 1:2:4 reinforced with 1.6mm mild steel wire including roughening cleaning, fixing and finishing in cement mortar 1:3 etc. all complete excluding plastering of the jambs sills & soffits.
25mm thick
| No | Length | Width | Height (av.) | Sub Qty.
| 2 | 0.45 |  | 0.45 | = | 0.405 |  | M2 | P/M2 | 835.8 | 0
14-A 13.24.2 | Providing 6 mm thick cement plaster to ceiling of mix 1:4
| No | Length | Width | Height (av.) | Sub Qty.
| 1 | 4.5 | 3 |  | = | 13.5
| 1 | 4.2 | 3.2 |  | = | 13.44
| 2 | 5 | 0.15 |  | = | 0.75
| 2 | 3.5 | 0.15 |  | = | 0.525
| 2 | 4.7 | 0.1 |  | = | 0.47
| 2 | 3.7 | 0.1 |  | = | 0.37
| 3 | 0.6 | 0.6 |  | = | 0.36
| 9 | 0.6 | 0.15 |  | = | 0.09
[6 empty] | 29.505 | 29.505 | M2 | P/M2 | 125.6 | 3705.828
14-B 13.11.4 | 12mm Cment plaster in coarse sand
1:6 (1cement : 6 Coarse Sand)
| No | Length | Width | Height (av.) | Sub Qty.
In side
| 2 | 4 |  | 2.68 | = | 21.44
| 2 | 3 |  | 2.68 | = | 16.08
| 2 | 2.1 |  | 0.25 | = | 1.05
| 2 | 1.2 |  | 0.25 | = | 0.6
| 3 | 0.9 |  | 0.25 | = | 0.675
Outside
| 2 | 4.5 |  | 3 | = | 27
| 2 | 3.5 |  | 3 | = | 21
Chajja
| 2 | 1.1 |  | 0.45 | = | 0.99
| 1 | 1.1 |  | 0.5 | = | 0.55
| 2 | 0.45 |  | 0.063 | = | 0.0567
In Column
| 16 | 0.3 |  | 5 | = | 24
| In beams |  |  |  | =
| 4 | 4 |  | 0.2 | = | 3.2
| 4 | 4 |  | 0.25 | = | 4
| 4 | 3 |  | 0.2 | = | 2.4
| 4 | 3 |  | 0.25 | = | 3
| 6 | 4.5 |  | 0.25 | = | 6.75
| 6 | 3 |  | 0.25 | = | 4.5
In steps
| 1 | 0.9 |  | 0.15 | = | 0.135
| 1 | 0.6 |  | 0.15 | = | 0.09
| 1 | 0.3 |  | 0.15 | = | 0.045
137.5617
Deduction
Door & Winsow
| 1 | 0.9 |  | 2.1 | = | 1.89
| 1 | 0.9 |  | 1.2 | = | 1.08
2.97
|  |  |  | Net Plaster |  | 134.5917 | 134.5917 | M2 | P/M2 | 141.5 | 19044.7255
14C- 13.11.4 + 13.26 | Providing 12mm cement plaster (1:6) including providing 1.5mm neat cement punning
| No | Length | Width | Height (av.) | Sub Qty.
In Dado
| 2 | 4 |  | 0.22 | = | 1.76
| 2 | 3 |  | 0.22 | = | 1.32
In floors
| 1 | 4 |  | 3 | = | 12
In steps
| 1 | 0.9 |  | 0.15 | = | 0.135
| 1 | 0.6 |  | 0.15 | = | 0.09
| 1 | 0.3 |  | 0.15 | = | 0.045
Outside plinth
| 2 | 4.5 |  | 0.45 | = | 4.05 |  |  |  | 141.5
| 2 | 3.5 |  | 0.45 | = | 3.15 |  |  |  | 40.5
[6 empty] | 22.55 | 22.55 | M2 | P/M2 | 182 | 4104.1
16- 13.79.1 | Finishing walls with water proofing cement paint of approved brand and manufacture and of required shade to give an even shade
| New work ( three or more coats) | [5 empty] | 164.0967 | M2 | M2 | 81.2 | 13324.652
17- 13.81.3 + 13.82.1 | Applying priming coat & painting with ready mixed paint of approved brand and manufacture in all sheds to give an even shade
with ready mixed zinc chromate yellow primer of app. Brand on new steel work (two or more coats)
In Door
| 1 | 2.25 | 0.9 | 2.1 | = | 4.2525
In windows
| 1 | 2.25 | 0.9 | 1.2 | = | 2.43 |  |  |  | 34.6
| In Grill |  |  |  |  | 1.08 |  |  |  | 83.5
[6 empty] | 7.7625 | 7.7625 | M2 | M2 | 118.1 | 916.7513
21 10.2 | Structural steel work riveted or bolted in built up sections, trusess and framed work, including cutting,hoisting,fixing in position and applying a priming coat of approved ateef primer all complete..
Providing MS ladder 50mm x 50mm x 6mm.
| 24M + 23 x 0.50M=35.5M @ 4.502kg/M= | [6 empty] | Kg. | P/Kg. | 95.4 | 0
22 | Providing railing at the top with 25mm GI pipe. | [5 empty] | 51 | Mtr | P/Mtr | 269.2 | 13729.2
23 | Providing necesary arrangement for proper fixation of P.V.C. Tank for lateral stability against wind pressure force. | [8 empty] | LS | 2000
24 | Carriage of the following materials from quarry to work site including loading, unloading and staking at work site as per specification & direction of E/I.
| Bricks (7 Km. Pucca & 1 Km. Kachha lead) | [6 empty] | Nos. | %0 nos. | 873.2 | 0
| Coarse Sand (100 Km. lead) | [6 empty] | M3 | P/M3 | 2094.88 | 0
| Stone chips (150Km. Pucca lead) | [6 empty] | M3 | P/M3 | 2999.84 | 0
| Local Sand (2 Km. Pucca + 1 Km. Kachha lead) | [6 empty] | M3 | P/M3 | 328.92 | 0
71576.1668
[10 empty] | Say | 71600
| Junior Engineer |  |  |  |  | AE |  |  |  | Executive Engineer
P.H. Division, Begusarai

## 29 rep_road res
Sub Est. No. 29
Road Restoration in place of Damaged portion of existing pipeline network
S.N. | Particulars |  |  |  |  | Quantity |  | Unit | Rate | Amount
1 15.2.1 | Demolishing cement concrete manually/by mechanical means including disposal of material within 50 metres lead as per direction of Engineer - in - charge.( in 10% length)
| 1:3:6 or richer mix | [10 empty] | (a) Bricks ( 7 Km. Pucca & 1 Km. Kaccha lead) | 990 | Nos. | %0 nos. | 873.2
| Existing Pipe Line | 100 | 0.3 | 0.15 | = | 4.5 | [5 empty] | (b) Coarse sand (100 Km pucca Carriage) | 3.44 | M3 | P/M3 | 2094.88
[7 empty] | M3 | P/M3 | 970.9 | 0 |  | (c) Stone Chips (150 Km pucca Carriage) | 6.695 | M3 | P/M3 | 2999.84
5(a) 4.1.3 | Providing and laying in position cement concrete of specified grade excluding the cost of centering and shuttering all work upto plinth level. |  |  |  |  | 4.5 | M3 | P/M3 | 3998.1 | 17991.45 |  | (d) Local Sand ( 3 Km. lead) | 3.53 | M3 | P/M3 | 328.92
1:2:4 (1 cement: 2 coarse sand : 4 graded stone aggregate 40mm nominal size)
5(b) | Carriage of the following materials from quarry to work site including loading, unloading and staking at work site as per specification & direction of E/I.
| Coarse Sand (100 Km pucca Carriage) |  |  |  |  | 2.025 | M3 | P/M3 | 2094.88 | 4242.132
| Stone chips (150 Km pucca Carriage) |  |  |  |  | 4.05 | M3 | P/M3 | 2999.84 | 12149.352
| Sub-Total | [8 empty] | 34382.934
| Total | [8 empty] | 34382.934
| Say Rs. | [8 empty] | 34383 | 382.0333
[9 empty] | per meter | 343.83
| Junior Engineer |  |  |  | Assistant Engineer |  |  | Executive Engineer
P.H. Division, Begusarai

## 31attendent room 01
Sub Est. No.- 31
ESTIMATE FOR THE REPAIRING OF SWITCH CUM ATTENDANT ROOM 6.00 M X 4.00 M X 3.50 M (High) with TOILET
S.N. Code No. | Particulars | [5 empty] | Quantity |  | Unit | Rate | Amount
1- 2.8.1 | Earthwork in excavation over areas (exceeding 30 cm in depth 1.5m in depth 1.5 in width as well as 10 sqm on plan) including disposal of excavated earth lead upto 50m and lift upto 1.5m, disposal earth to be leveled and neatly dressed.
| No | Length | Width | Height (av.) | Sub Qty.
Piller
| 6 | 1.8 | 1.8 | 1.8 |  | 34.992
Long Wall
| 2 | 5 | 1.2 | 1.375 | = | 16.5
Short Wall
| 2 | 3 | 1.2 | 1.375 | = | 9.9
Long Wall of Toilet
| 1 | 1.8 | 0.8 | 1.375 | = | 1.98
Short Wall of Toilet
| 2 | 1.2 | 0.8 | 1.375 | = | 2.64
[6 empty] | 66.012 | 66.012 | M3 | P/M3 |  | 0
1B 2.26 | Filling available excavated earth (excluding rock) in trenches, plinth,sides of foundations etc. in layers not exceeding 20 cm in depth: consolidating each deposited layer by ramming and watering lead | [5 empty] | 31.0256 | M3 | P/M3 |  | 0
2- 2.28 | Supplying and filling in plinth with local sand and under floors including watering, ramming consolidating and dressing complete.
| No | Length | Width | Height (av.) | Sub Qty.
Piller
| 6 | 1.8 | 1.8 | 0.15 |  | 2.916
Long Wall of Switch Cum Pump Attendant Room
| 2 | 5 | 1.2 | 0.15 | = | 1.8
Short Wall of Switch Cum Pump Attendant Room
| 2 | 3 | 1.2 | 0.15 | = | 1.08
Long Wall of Toilet
| 1 | 1.5 | 0.8 | 0.15 | = | 0.18
Short Wall of Toilet
| 2 | 1 | 0.8 | 0.15 | = | 0.24
In Plinth of pump house
| 1 | 5 | 3 | 0.4 | = | 6
In Plinth of Toilet
| 1 | 1.8 | 1.2 | 0.4 | = | 0.864
[6 empty] | 13.08 | 13.08 | M3 | P/M3 |  | 0
3- 11.72 | Providing designation of 100A Brick on edge Soling joints filled with local sand including cost of watering, taxes & royalty all complete as per specification & direction of E/I.
| No | Length | Width | Height (av.) | Sub Qty.
Piller
| 6 | 1.8 | 1.8 |  |  | 19.44
Long Wall of P/H
| 2 | 5 | 1.2 |  | = | 12
Short Wall of P/H
| 2 | 3 | 1.2 |  | = | 7.2
Long Wall of a Toilet
| 1 | 1.5 | 0.8 |  | = | 1.2
Short Wall of Toilet
| 2 | 1 | 0.8 |  | = | 1.6
In Plinth of pump house
| 1 | 5 | 3 |  | = | 15
In Plinth of Toilet
| 1 | 1.8 | 1.2 |  | = | 2.16
[6 empty] | 58.6 | 58.6 | M2 | P/M2 |  | 0
4- 4.1.4 | Providing and laying in position cement concrete of specified grade excluding the cost of centering and shuttering all work upto plinth
1:2:4 (1 cement: 2 coarse sand : 4 graded stone aggregate 40mm nominal size)
| No | Length | Width | Height (av.) | Sub Qty.
Piller
| 6 | 1.8 | 1.8 | 0.3 |  | 5.832
Long Wall of P/H
| 2 | 5 | 1.2 | 0.1 | = | 1.2
Short Wall of P/H
| 2 | 3 | 1.2 | 0.1 | = | 0.72
Long Wall of a Toilet
| 1 | 1.5 | 0.8 | 0.1 | = | 0.12
Short Wall of Toilet
| 2 | 1 | 0.8 | 0.1 | = | 0.16
In Plinth of pump house
| 1 | 5 | 3 | 0.1 | = | 1.5
In Plinth of Toilet
| 1 | 1.8 | 1.2 | 0.1 | = | 0.216
1 13.74 | Removing white or color wash by scraping and sand preparing the surface smooth including necessary repair of scratches etc. all complete.
| No | Length | Width | Height (av.) | Sub Qty.
Room(ceiling)
| 1 | 6 | 4 |  | = | 24
| 1 | 1.8 | 1.2 |  | = | 2.16
Outside projection
| 2 | 6.3 | 0.3 |  | = | 3.78
| 2 | 4.3 | 0.3 |  | = | 2.58
Chajja
| 2 | 1.2 | 0.6 |  | = | 1.44
| 2 | 0.9 | 0.6 |  | = | 1.08
35.04
In side
| 2 | 6 |  | 3.5 | = | 42
| 2 | 4 |  | 3.5 | = | 28
| 2 | 1.8 |  | 3.5 | = | 12.6
| 2 | 1.2 |  | 3.5 | = | 8.4
Outside
| 2 | 6 |  | 3.5 | = | 42
| 2 | 4 |  | 3.5 | = | 28
| 3 | 1.8 |  | 3.5 | = | 18.9
| Deduction |  |  |  |  | 179.9
Door
| 1 | 0.9 |  | 2.1 | = | 1.89
| 1 | 0.75 |  | 2.1 | = | 1.575
Windows
| 1 | 1.2 |  | 1.2 | = | 1.44
| 1 | 0.5 |  | 0.6 | = | 0.3
Steps
| 2 | 1.05 |  | 0.6 | = | 1.26
|  | Net Deduction |  |  |  | 6.465
|  | Net Surface |  |  |  | 208.475 | 208.475 | M2 | P/M2 | 7.7 | 1605.2575
04- 13.11.4 | Cement plaster in coarse sand
1:6 (1cement : 6 Coarse Sand
| No | Length | Width | Height (av.) | Sub Qty.
In side
| 2 | 6 |  | 3.5 | = | 42
| 2 | 4 |  | 3.5 | = | 28
| 2 | 1.8 |  | 3.5 | = | 12.6
| 2 | 1.2 |  | 3.5 | = | 8.4
Outside
| 2 | 6 |  | 3.5 | = | 42
| 2 | 4 |  | 3.5 | = | 28
| 3 | 1.8 |  | 3.5 | = | 18.9
| Deduction |  |  |  |  | 179.9
( i ) | Door
| 1 | 0.9 |  | 2.1 | = | 1.89
| 1 | 0.75 |  | 2.1 | = | 1.575
( ii ) | Windows
| 1 | 1.2 |  | 1.2 | = | 1.44
| 1 | 0.5 |  | 0.6 | = | 0.3
(iii) | Steps
| 2 | 1.05 |  | 0.6 | = | 1.26
|  |  | Net Deduction |  |  | 6.465
|  |  | Net Plaster |  |  | 173.435
| 50% of total area: |  |  |  |  | 86.7175 | 86.7175 | M2 | P/M2 | 141.5 | 12270.5263
07- 13.79.2 | Finishing walls with water proofing cement paint of approved brand and manufacture and of required shade to give an even shade
| Old work (one or more coats) | [5 empty] | 208.475 | M2 | M2 | 61.1 | 12737.8225
8 | Providing lighting arrangement both inside & outside the attendent room including fitting & fixing two nos., tube lights inside the pump house ad one no. of Vapor Halogen light outside with all necessary electrical power wiring with suitable PVC sheathed copper conductor of ISI mar as per direction of E/I. | [5 empty] | 1 | No. | Each | 5000 | 5000
| Total | [9 empty] | 31613.6063
| Junior Engineer |  |  | Assistant Engineer |  |  | Executive Engineer
P.H. Division, Begusarai

## Compound_wall 02
Sub Est. No:-32
REPAIR & PAINTING OF 1.5M (High) COMPOUND WALL
S.N. Code No. | Particulars | [5 empty] | Quantity |  | Unit | Rate | Amount
| Taking length of compound wall |  |  |  |  | 29 | M
| Taking height of compound wall |  |  |  |  | 1.5 | M
6 | Brick work with bricks of class designation 100A in foundation and plinth in :
6.1.14A | Cement mortar 1:6 (1 Cement : 6 Sand) | [12 empty] | 8.6
| No | Length | Width | Height (av.) |  | Sub Qty. | [7 empty] | 8.6
| 1 | 8.5 | 0.375 | 0.165 | = | 0.52594 | [7 empty] | 7.6
| 1 | 8.5 | 0.375 | 0.165 | = | 0.52594 | [7 empty] | 3.6
| 1 | 12 | 0.375 | 0.165 | = | 0.7425
1.7944
| 25% work to be done for repairing | [5 empty] | 0.44859 | M3 | P/M3 | 4819.9 | 2162.177
7 | Brick work with bricks of class designation 100A in foundation and plinth in :
6.1.14A + 6.3A | Cement mortar 1:6 (1 Cement : 6 Sand)
| Extra for brick work in superstructure above plinth upto V floor | [12 empty] | 0.449
| No | Length | Width | Height (av.) |  | Sub Qty. | [7 empty] | 2.264
Pillar | 11 | 0.25 | 0.25 | 1.5 | = | 1.0312 | [5 empty] | 195.75 | 0.003 | 0.58725
Wall | 1 | 29 | 0.125 | 1.5 | = | 5.4375 | [7 empty] | 3.3002
[6 empty] | 6.4688 | [8 empty] | 2.713 | 3.3913
| 35% work to be done for repairing | [5 empty] | 2.2641 | M3 | P/M3 | 842.2 | 1906.7934 |  |  |  |  | 2.9068
8- | Cement plaster in coarse sand | [11 empty] | 0.449
13.11.4 | 1:6 (1cement : 6 Coarse Sand | [11 empty] | 2.264
| No | Length | Width | Height (av.) |  | Sub Qty. | [6 empty] | 2.713 | 500 | 1356.5
Wall | 2 | 29 |  | 1.5 | = | 87
25% extra for crown |  |  |  |  | = | 108.75 | [7 empty] | 2.9
[6 empty] | 195.75 | 195.75 | M2 | P/M2 | 141.5 | 27698.625 |  |  | 0.587
9 | Finishing walls with water proofing cement paint of approved brand and manufacture and of required shade to give an even shade | [12 empty] | 3.487
13.79.2 | Old work (one or more coats) | [5 empty] | 195.75 | M2 | M2 | 61.1 | 11960.325
Supplying and filling in compound wall by local sand in low land incluinding watering, etc all complete.
11 | Carriage of the following materials from quarry to work site including loading, unloading and staking at work site as per specification & direction of E/I.
| (a) Bricks ( 7 Km. Pucca & 1 Km. Kaccha lead) | [5 empty] | 2150 | Nos. | %0 nos. | 963.04 | 2070.536
| (b) Coarse sand (44 Km pucca & 1 km kaccha Carriage) | [5 empty] | 4 | M3 | P/M3 | 1120.6 | 4482.4
| Total Rate for 29M long compound wall = | [9 empty] | 50280.8565
| So Rate per M of compound wall = | [9 empty] | 1733.8226
| Total cost of 29M long compound wall = | [7 empty] | 50280.8565
| Junior Engineer |  |  | Assistant Engineer |  |  | Executive Engineer
P.H. Division, Begusarai

## campus development 04
Sub Est. No. - 33
CAMPUS DEVELOPMENT
S.N. | Particulars |  |  |  |  | Quantity |  |  | Unit | Rate | Amount
1 2.28(i) | Supplying and filling in compound wall by local sand in low land incluinding watering, etc all complete. | [5 empty] | 33.6 | M3 | P/M3 | 287.3 | 9653.28
earth filling in campus
|  | 10 | 8 | 0.6 | = | 48
| Deduct | 4 | 6 | 0.6 | = | 14.4
|  | total |  |  |  | 33.6
2 11.72 (i) | Brick flat soaling inside campus | [5 empty] | 56 | M2 | P/M2 | 283 | 15848
|  | 10 | 8 | 0 | = | 80
| Deduct | 4 | 6 | 0 | = | 24
|  | total |  |  |  | 56
3 | Carriage of the following material from qurry to work site incluiding loading and unloading
| (a) Bricks ( 7 Km. Pucca & 1 Km. Kaccha lead) | [5 empty] | 1960 | Nos. | %0 nos. | 1077.2 | 2111.312
| (b) Local sand ( 7 Km. Pucca & 1 Km. Kaccha lead) | [5 empty] | 33.6 | M3 | P/M3 | 278.08 | 9343.488
[9 empty] | Total |  | 27302.8
| Junior Engineer |  |  | Assistant Engineer |  |  |  |  | Executive Engineer
P.H. Division, Begusarai

## 2HP 08
Sub Est. No-34
Model estimate for supply, installation & commissioning of single phase 2 H.P submersible motor pump set with all accessories including extension of L.T. line from nearest source up-to pumping station.
Sl. No. | Particulars |  | Quantity |  | Unit | Rate | Amount
1 | 2 |  | 3 |  | 4 | 5 | 6
[A] | Supply Installation, commissioning and testing of single phase 2 H.P. submersible pump set having discharging capacity 3 lps at a total head of 45 meter(approx) of KSB/ Kirloskar or equivalent make with all accessories & fittings etc including loading unloading and transportation of the pump set to the work site with all required labour, materials, tools and tackles installation, testing & commissioning as per standards specifications and direction of E/I. |  | 1 | job | Each | 88500 | Rs.88500.00
| (i) 50 mm dia x 3 mtrs long medium class G.I column pipe both end threaded and one end socketed- 6(six)nos |  | 1 | No
(ii) 1x3x2.5 mm² flat copper conductor submersible cable -40 (forty) mtrs.
(iii) 50 mm dia union socket- 1(one) no.
(iv) 65 mm dia x 250 mm long G.I. nipple- 1 (one) no.
(v) 50 mm dia G.I Elbow—1(One) no.
(vi) 50 mm dia M.S. clamps—2(Two) Pairs.
(vii) 50 mmx 250 mm long G.I nipple- 1(One) no.
(viii) Tube well cap for 125 mm dia T/Well – 1(one) no.
(ix) 50 mm dia x 65 mm dia reducer socket –1(one) no.
[B] | Supply Installation, commissioning and testing of floor mounted outdoor type L.T feeder pillar single phase starter controll pannel operated on 220 V, 3 phase , 50 c/s for 2 HP Submersible pump set made of MS sheet (minimum 2 mm thick) duly spray power coated painting with following accessories made of M.S sheet ( minimum 2mm thick) duly spray powder coated painting with following accessories |  | 1 | No
(i) 90-220 V range single phase 7.5 KVA automatic voltage stabilizer make- Sen & Pandit/ Vertex/ISI marked If any. 1 No.
(ii) Suitable single phase starter control panel for above motor of BCH /L&Tmake – 1(one) no.
[C] | Supplying & fitting 2.5 mm2 copper service cable from power point from nearest source up-to pumping station.. |  | 20 | mtrs
[D] | Providing all materials and labour required for doing earthing station with G.I earth pipe of 40 mm dia x 4.5 mtrs 20fts. long G.I pipe including accessories excavation of earth , providing masonry enclosure with cover plate having locking arrangement and watering pipe etc.with salt, charcoal,etc.as per IE & IS specification. |  | 1 | No
Rs.88500.00
Junior Engineer |  | Assistant Engineer |  | Executive Engineer
P.H. Division, Begusarai

## SP 09
Sub-Estimate No. - 35
Supplying, installation Testing & commissioning of Solar Pannel plate
S.N. | Particulars |  | Quantity |  | Unit | Rate | Amount
1 | Supplying and installation of Solar pannel plate of capacity 315 Watts each (1 nos x 315 W = 945W) |  | 315 | W | P/watt | 50 | 15750
TOTAL | [6 empty] | 15750
| Junior Engineer | Assistant Engineer |  |  |  | Executive Engineer
P.H. Division, Begusarai

## VFD 10
Sub Est. No. - 36
Supplying, installation Testing & commissioning of Varriable Frequency Drive (VFD), Change over Switch and Net Energy Metering (NEM) system
S.N. | Particulars |  | Quantity |  | Unit | Rate | Amount
1 | Supplying anf installation of VARRIABLE FREQUENCY DRIVE (VFD) of 2 H.P. Single Phase Motor range 220 V , 50 HZ , 2900 RPM for submersible pump set. |  | 1 | No. | Each | 35212 | 35212
2 | Supplying and installation 32 Amp 2 Pole Single Phase Change over switch. |  | 1 | No. | Each | 2985 | 2985
3 | Provision of Net Energy Metering (NEM) system including all accessories. |  | 1 | No. | Each | 22253 | 22253
TOTAL | [6 empty] | 60450
| Junior Engineer | Assistant Engineer |  |  |  | Executive Engineer
P.H. Division, Begusarai

## Battery 11
Sub Est. No.- 37
Providing and Fixing 12 VOLT Solar Battery
S.N. Code No. | Particulars |  | Quantity |  | Unit | Rate | Amount
1 | Providing and fixing 12 Volt Solar Battery 200 Ah all complete as per Direction of E/I |  | 1 | No. | Each | 35000 | 35000
TOTAL | [6 empty] | 35000
| Junior Engineer | Assistant Engineer |  |  |  | Executive Engineer
P.H. Division, Begusarai

## L-1
Sub Estimate-38
ANALYSIS OF RATES FOR LEKAGE REPIAR IN DIFFERENT SIZES OF LEAD JOINT G.I. PIPES
S.No. | Pipe Size | PCC Road Cutting (15.2.1) and restoring (4.1.3) |  |  | Jointing with cost of labour, Union socket, spun yarn, hemp & tools | Rate With PCC Rd Cutting | Rate Without Rd Cutting
|  | Size of Tench | Qty
1 | 40mm dia | 1.0M x 1.0Mx.15M = | 0.15 |  | 1
|  |  | 911.4 | 136.71 | 820
| 1:2:4 with 20 mmnominal size) |  | 3953.4 | 593.01
carriage
| Coarse Sand (Lead - 44 Km pucca & 1 km kaccha) |  | 802.89 | 54.1951
| Stone chips (Lead - 195 Km pucca & 5 km unsurfaced) |  | 2983.843 | 402.8188
|  |  |  | 1186.7339 | 820 | 2006.7339 | 820
2 | 50mm dia | 1.0M x 1.0Mx.15M = | 0.15 |  | 1
|  |  | 911.4 | 136.71 | 890
| 1:2:4 with 20 mmnominal size) |  | 3953.4 | 593.01
carriage
| Coarse Sand (Lead - 44 Km pucca & 1 km kaccha) |  | 802.89 | 54.1951
| Stone chips (Lead - 195 Km pucca & 5 km unsurfaced) |  | 2983.843 | 402.8188
|  |  |  | 1186.7339 | 890 | 2076.7339 | 890
3 | 65mm dia | 1.0M x 1.0Mx.15M = | 0.15 |  | 1
|  |  | 911.4 | 136.71 | 1180
| 1:2:4 with 20 mmnominal size) |  | 3953.4 | 593.01
carriage
| Coarse Sand (Lead - 44 Km pucca & 1 km kaccha) |  | 802.89 | 54.1951
| Stone chips (Lead - 195 Km pucca & 5 km unsurfaced) |  | 2983.843 | 402.8188
|  |  |  | 1186.7339 | 1180 | 2366.7339 | 1180
4 | 80mm dia | 1.0M x 1.0Mx.15M = | 0.15 |  | 1
|  |  | 911.4 | 136.71 | 1250
| 1:2:4 with 20 mmnominal size) |  | 3953.4 | 593.01
carriage
| Coarse Sand (Lead - 44 Km pucca & 1 km kaccha) |  | 802.89 | 54.1951
| Stone chips (Lead - 195 Km pucca & 5 km unsurfaced) |  | 2983.843 | 402.8188
|  |  |  | 1186.7339 | 1250 | 2436.7339 | 1250
Executive Engineer
P.H. Division, Begusarai

## L-2
Sub Estimate-38
ANALYSIS OF RATES FOR LEKAGE REPIAR IN DIFFERENT SIZES OF LEAD JOINT G.I. PIPES
1 | 40 mm dia nominal bore
Materials-
| 40 mm dia Union (1645) | each | 1 | 192 | 192
| White lead, hemp, Oil etc . | each | 1 | 3 | 3
Labour for cutting & theading of GI Pipes
| Plumber (OL27) | each | 0.1 | 367 | 36.7
| U/S labour (OL02) | each | 0.1 | 287 | 28.7
| Add for contractor's profit & overheads @ 15% |  |  |  | 39.06
Trenching and refilling etc.
| 1.0M x 1.0Mx 1.1 = | Cum | 1.1 | 360.7 | 396.77
| Refilling | Cum | 1.078 | 116.5 | 125.587
| Cost for I leakage reapir |  |  |  | 821.82
| Cost for 1 leakage repair |  |  | Rs. | 820
2 | 50 mm dia nominal bore
Materials-
| 50 mm dia Union (1646) | each | 1 | 249 | 249
| White lead, hemp, Oil etc . | each | 1 | 3 | 3
Labour for cutting & theading of GI Pipes
| Plumber (OL27) | each | 0.1 | 367 | 36.7
| U/S labour (OL02) | each | 0.1 | 287 | 28.7
| Add for contractor's profit & overheads @ 15% |  |  |  | 47.61
Trenching and refilling etc.
| 1.0M x 1.0Mx 1.1 = | Cum | 1.1 | 360.7 | 396.77
| Refilling | Cum | 1.078 | 116.5 | 125.587
| Cost for I leakage reapir |  |  |  | 887.37
| Cost for 1 leakage repair |  |  | Rs. | 890
3 | 65 mm dia nominal bore
Materials-
| 65 mm dia Union (1647) | each | 1 | 504 | 504
| White lead, hemp, Oil etc . | each | 1 | 3 | 3
Labour for cutting & theading of GI Pipes
| Plumber (OL27) | each | 0.1 | 367 | 36.7
| U/S labour (OL02) | each | 0.1 | 287 | 28.7
| Add for contractor's profit & overheads @ 15% |  |  |  | 85.86
Trenching and refilling etc.
| 1.0M x 1.0Mx 1.1 = | Cum | 1.1 | 360.7 | 396.77
| Refilling | Cum | 1.078 | 116.5 | 125.587
| Cost for I leakage reapir |  |  |  | 1180.62
| Cost for 1 leakage repair |  |  | Rs. | 1180
4 | 80 mm dia nominal bore
Materials-
| 80 mm dia Union (1648) | each | 1 | 563 | 563
| White lead, hemp, Oil etc . | each | 1 | 3 | 3
Labour for cutting & theading of GI Pipes
| Plumber (OL27) | each | 0.1 | 367 | 36.7
| U/S labour (OL02) | each | 0.1 | 287 | 28.7
| Add for contractor's profit & overheads @ 15% |  |  |  | 94.71
Trenching and refilling etc.
| 1.0M x 1.0Mx 1.1 = | Cum | 1.1 | 360.7 | 396.77
| Refilling | Cum | 1.078 | 116.5 | 125.587
| Cost for I leakage reapir |  |  |  | 1248.47
| Cost for 1 leakage repair |  |  | Rs. | 1250
Executive Engineer
P.H. Division, Begusarai

## Sheet8
Sub Est. No. 39
CLEANING OF RCC water storage VAT
S.N. | Particulars | Quantity |  | Unit | Rate | Amount
1 | Providing all labours, materials and cleaning of tank from inside and doing chlorination etc. all complete work as per specification & direction of E/I. 10000 Lit | 10000 | Ltr | P/Ltr | 0.1 | 1000
| Total- |  |  |  |  | 1000
Executive Engineer
P.H. Division, Begusarai

## (200 x 150 mm) UPVC
Sub Estimate No.40
Construction of 200mm x 150mm dia & 125M deep H/Y Tube well
S.No. | Description | Qty. |  | Unit | Rate | Amount
1 | Providing all materials, labours, & equipments for drilling by reverse rotary rig machine for following dia bore hole in all kind of soil mixed with kanker, sand stone including providing sample box, and collection strata sample at every 3.0M depth of drilling for asserting proper aquifer for completing high yielding T/well etc. as per IS:2800-1979 & PHED specification and direction of E/I.
24.1.1.3 | (a) 400mm dia bore from G.L. to 30M | 30 | M | P/M | 681.5 | 20445
24.1.1.2 | (b) 350 mm dia bore from 30M to 90M | 60 | M | P/M | 532.4 | 31944
24.2.1.2 | (c) 350 mm dia bore from 90M to 125M | 35 | M | P/M | 659.5 | 23082.5
2 | Supplying, assembling, lowering abd fixing in vertical position in borewell, unplasticized PVC medium well casing (CM) pipe of required dia, conforming to IS:12818, including required hire and labour charges, fittings & accessories etc. all complete for all depths, as per direction of E/I.
24.3.3 | (a) 200mm x 5mm thick pipe I.S.I. mark | 30 | M | P/M | 940.8 | 28224
24.3.2 | (a) 150mm x 5mm thick pipe I.S.I. mark | 60 | M | P/M | 660.1 | 39606
3 | Supplying, assembling, lowering abd fixing in vertical position in borewell, unplasticized PVC medium well screen (RMS) pipes with ribs,conforming to IS:12818, including hire and labour charges, fittings & accessories etc. all complete for all depths, as per direction of E/I.
24.4.2 | 150 mm dia and 1mm slot | 30 | M | P/M | 673.5 | 20205
4 | Providing all tools and labour including supplying fitting & fixing the following accessories for aforesaid 200mm x 150 mm T/Well as per direction of E/I.
L.S | (a) 200 mm x 150 mm dia M.S Reducer | 1 | No. | Each | 500 | 500
L.S | (b) 200 mm dia M.S. well cap | 1 | No. | Each | 260 | 260
24.15.2 | (c) 150 mm dia M.S well shoe plug | 1 | Nos. | Each | 281.8 | 281.8
L.S | (d) Center guide suitable for 200 mm dia pipe | 3 | Nos. | Each | 150 | 450
L.S | (e) Center guide suitable for 150 mm dia pipee | 8 | No. | Each | 100 | 800
24.14.3 | (f) M.S clamp 200 mm dia | 1 | No. | P.Pair | 1738 | 1738
5a 24.8 | Providing all materials, labours, & tools for providing and placing around tubewell double washed pea gravel confirming to IS:8419-1977 of size 4mm to 8mm from dalbhumgarh of east singhbhum (JH) inclusive of loading, carriage, unloading & stacking inproper shape for measurement at site. ( Stock measurement of clean and washed gravel shall be taken 13" as 12" in height to count void) as per direction of E/I. | 12 | M3 | P/M3 | 1343.2 | 16118.4
5b | Carriage of Pea Gravel from Dhalbhumigarh (taken distance 480km.Pakka+5Km unsurface road) (1.6*(480*11.20+5*13.50)+195.10)=8904.70+1% L.Cess+12%-GST)=Rs.10,062.31 | 12 | M3 | P/M3 | 10062.31 | 120747.72
6 24.12 | Development of tube well in accordance with IS : 2800 (part I) and IS: 11189, to establish maximum rate of usable water yield without sand content (beyond permissible limit), with required capacity air compressor, running the compressor for required time till well is fully develo ped, measuring yield of well by "V" notch method or any other approved method, measuring static level & draw down etc. by step draw down method, collecting water sampl & getting tested in approved laboratory, i/c disinfection of tubewell, all complete,including hire & labour charges of air compressor, tools & accessories etc., all as per requirement and direction of Engineer-in-charge. | 24 | Hrs. | Each | 916.8 | 22003.2
7 | Transportation and erection of drilling plants, developing equipments & all other required tools and M/C by and suitable mechanical means including all cost of loading, unloading, placing at work site and back after completion of work as per S/D of E/I. | 1 | No. | Each | 9200 | 9200
8 | Supplying all materials and labours for arrangement for additional water required during the drilling period for 80 Hrs & site clearance & leveling etc. all complete work as per specification & direction of E.I. | 1 | Job | Each | 25000 | 25000
9 | Chemical and bacteiological testing of water sample including the cost of collection, carrying to designed PHE laboratories and submission of report in triplicate as per direction of E/I. | 1 | No. | Each | 500 | 500
[5 empty] | TOTAL | 361105.62
[5 empty] | Say | 361106
| Assistant Engineer |  |  | Executive Engineer
P.H. Division, Begusarai

## (200 x 150 mm) MS pipe
Sub Estimate No.41
Construction of 200mm x 150mm dia & 125M deep H/Y Tube well
S.No. | Description | Qty. |  | Unit | Rate | Amount
1 | Providing all materials, labours, & equipments for drilling by Reverse Rotary rig machine for following dia bore hole in all kind of soil mixed with kanker, sand stone including providing sample box, and collection strata sample at every 3.0M depth of drilling for asserting proper aquifer for completing High Yielding Tube Well all complete as per IS:2800-1979 & PHED specification and direction of E/I.
24.1.1.3 | (a) 400mm dia bore from G.L. to 30M | 30 | M | P/M | 681.5 | 20445 |  |  | 375
24.1.1.2 | (b) 350 mm dia bore from 30M to 90M | 60 | M | P/M | 532.4 | 31944 | [6 empty] | 500
24.2.1.2 | (c) 350 mm dia bore from 90M to 125M | 35 | M | P/M | 659.5 | 23082.5 |  |  |  |  | 107585.09 |  | 375
2 | Supplying, assembling, lowering and fixing in vertical position in bore well, ERW (Electric resistance welded) EF 410 mild screwed and socketted/plain ended casing pipes of required dia confirming to IS:4270 of reputed and approved make including painted with outside surface with two coats of anti corrosive paint of approved brand and manufacturer including hire & labour charges, fitting & accessories all complete for all depth as per direction fo E/I.
24.10.3 | (a) 200mm x 5.4mm thick M.S.E.R.W. housing pipe | 36 | M | P/M | 2003.7 | 72133.2
24.10.2 | (b) 150mm x 5.0mm thick M.S.E.R.W. housing pipe | 54 | M | P/M | 1408.1 | 76037.4
3 | Supplying, assembling, lowering and fixing in vertical position in bore well, ERW (Electric Resistance Welded) FE 410 plain slotted (having slot of size 1.6/3.2 mm) mild steel threaded and socketed / plain bevel ended pipe (type A) of required dia, conforming to IS: 8110, of reputed and approved make, having wall thickness not less than 5.40 mm, including painted with outside surface with two coats of anticorrosive bitumestic paint of approved brand and manufacture,including hire & labour charges, fittings & accessories, all complete,for all depths, as per direction of Engineer -in-charge.
24.11.2 | 150 mm nominal size dia | 30 | M | P/M | 1727.2 | 51816
4 | Supplying the following fittings & fixing the same in position as per approved lowering assembly and strata chart including providing all equipments and welding the same on process of lowering the assay etc. all complete as per S/D of E/I.
| (a) 200 mm x 150 mm dia MS reducer | 1 | No. | Each | 1000 | 1000 |  |  | 20
24.13.3 | (b) 200 mm dia well cap | 1 | No. | Each | 281 | 281
24.15.3 | (c) Providing and fixing Bail plug/ Bottom plug of required dia to the bottom of pipe assembly of tubewell as per IS:2800 (part I). 200mm dia | 1 | No. | Each | 281.8 | 281.8
| (d) 200 mm dia center guide | 4 | Nos. | Each | 250 | 1000 | [5 empty] | 0.785
| (e) 150 mm dia center guide | 9 | Nos. | Each | 150 | 1350 | 10072.9966
24.14.3 | (f) Providing and fixing M.S. clamp of required dia to the top of casing/ housing pipe of tubewell as per IS: 2800 (part I), including necessary bolts & nuts of required size complete 200 mm | 1 | No. | Each | 1738 | 1738 | 8993.747 |  |  |  | 4.2704 | 5.3753 | 0.628 | 10.2737
5a 24.8 | Gravel packing in tubewell construction in accordance with IS: 4097,including providing gravel fine/ medium/ coarse, in required grading & sizes as per actual requirement, all complete as per direction of Engineer-in-charge. | 12 | M3 | P/M3 | 1343.2 | 16118.4 | 89.047 |  |  | 8904.7 | 89.047 | 1068.564 | 10062.311
5b | Carriage of Pea Gravel from Dhalbhumigarh (taken distance 480km.Pakka+5Km unsurface road) (1.6*(480*11.20+5*13.50)+195.10)=8904.70+1% L.Cess+12%-GST)=Rs.10073.00 | 12 | M3 | P/M3 | 10073 | 120876 | 8904.7 | 7381.5 | 73.815 | 7455.315 | 8904.7 | 89.047 | 1068.564 | 10062.311 | 1058.6266 | 10.5863 | 8709.6 | 195.1 | 8904.7 | 89.047 | 1068.564 | 10062.311
6- 24.12 | Development of tube well in accordance with IS : 2800 (part I) and IS: 11189, to establish maximum rate of usable water yield without sand content (beyond permissible limit), with required capacity air compressor, running the compressor for required time till well is fully develo ped, measuring yield of well by "V" notch method or any other approved method, measuring static level & draw down etc. by step draw down method, collecting water sampl &getting tested in approved laboratory, disinfection of tubewell, all complete,including hire & labour charges of air compressor, tools & accessories etc., all as per requirement and direction of Engineer-in-charge. | 24 | Hrs. | Each | 916.8 | 22003.2 |  |  | . | 8349.9528
7 | Transportation and erection of drilling plants, developing equipments & all other required tools and M/C by suitable mechanical means including all cost loading, unloading, placing at work site and back after completion of work as per S/D of E/I. | 1 | No. | Each | 9200 | 9200
8 | Supplying all materials and labours for arrangement for additional water required during the drilling period for 80 Hrs & site clearance & leveling etc. And providing the soap duster etc. to staff engaged in drilling etc. all complete work as per specification & direction of E.I. | 1 | No. | Each | 25000 | 25000
9 | Chemical and bactirological testing of water sample including the cost of collection, carrying to designated PHE/other laboratory and submission of reports in triplicate as per direction of E/I. | 1 | No. | Each | 500 | 500
|  | TOTAL |  |  |  | 474806.5
|  | SAY |  |  |  | 474807
| Junior Engineer Assistant Engineer | Executive Engineer
|  | P.H. Division, Begusarai | [8 empty] | 24156

## 300 x 200mm
Sub Estimate No.42
Construction of 300mm x 200mm dia & 125M deep H/Y Tube well
S.No. | Description | Qty. |  | Unit | Rate | Amount
1 | Providing all materials, labours, & equipments for drilling by Reverse Rotary rig machine for following dia bore hole in all kind of soil mixed with kanker, sand stone including providing sample box, and collection strata sample at every 3.0M depth of drilling for asserting proper aquifer for completing High Yielding Tube Well all complete as per IS:2800-1979 & PHED specification and direction of E/I.
| (a) 650 mm dia bore from G.L. to 30M | 30 | M | P/M | 2102 | 63060
| (b) 600 mm dia bore from 30M to 90M | 60 | M | P/M | 1402 | 84120
| (c) 600 mm dia bore from 90M to 150M | 35 | M | P/M | 1402 | 49070
2 | Supplying, assembling, lowering and fixing in vertical position in bore well, ERW (Electric resistance welded) EF 410 mild screwed and socketted/plain ended casing pipes of required dia confirming to IS:4270 of reputed and approved make including painted with outside surface with two coats of anti corrosive paint of approved brand and manufacturer including hire & labour charges, fitting & accessories all complete for all depth as per direction fo E/I.
| (a) 300mm x 6mm thick M.S.E.R.W blank pipe (TATA OR JINDAL and I.S.I mark. | 30 | M | P/M | 3406 | 102180 | 3304
24.10.3 | (b) 200mm x 5.4mm thick M.S.E.R.W. housing pipe | 60 | M | P/M | 2003.7 | 120222 |  | 1696.2
3 | Supplying, assembling, lowering and fixing in vertical position in bore well, ERW (Electric Resistance Welded) FE 410 plain slotted (having slot of size 1.6/3.2 mm) mild steel threaded and socketed / plain bevel ended pipe (type A) of required dia, conforming to IS: 8110, of reputed and approved make, having wall thickness not less than 5.40 mm, including painted with outside surface with two coats of anticorrosive bitumestic paint of approved brand and manufacture,including hire & labour charges, fittings & accessories, all complete,for all depths, as per direction of Engineer -in-charge.
24.11.3 | 200 mm nominal size dia | 30 | M | P/M | 2119.1 | 63573
4 | Supplying the following fittings & fixing the same in position as per approved lowering assembly and strata chart including providing all equipments and welding the same on process of lowering the assay etc. all complete as per S/D of E/I.
| (a) 300 mm x 200 mm dia MS reducer | 1 | No. | Each | 710 | 710
| (b) 300 mm dia well cap | 1 | No. | Each | 700 | 700
24.15.3 | (c) Providing and fixing Bail plug/ Bottom plug of required dia to the bottom of pipe assembly of tubewell as per IS:2800 (part I). 200mm dia | 1 | No. | Each | 308.5 | 308.5
| (d) 300 mm dia center guide | 3 | Nos. | Each | 350 | 1050
| (e) 200 mm dia center guide | 10 | Nos. | Each | 250 | 2500
24.14.2 | (f) Providing and fixing M.S. clamp of required dia to the top of casing/ housing pipe of tubewell as per IS: 2800 (part I), including necessary bolts & nuts of required size complete 300 mm | 1 | No. | Each | 1738 | 1738
5a 24.8 | Gravel packing in tubewell construction in accordance with IS: 4097,including providing gravel fine/ medium/ coarse, in required grading & sizes as per actual requirement, all complete as per direction of Engineer-in-charge. | 15 | M3 | P/M3 | 1343.2 | 20148
5b | Carriage of Pea Gravel from Dhalbhumigarh (taken distance 480km.Pakka+5Km unsurface road) (1.6*(480*11.20+5*13.50)+195.10)=8904.70+1% L.Cess+12%-GST)=Rs.10,062.31 | 15 | M3 | P/M3 | 10062.31 | 150934.65 |  |  | 1.6(480*8.4+5*10.10)+171 | 6703 | 6770.03 | 804.36 | 7574.39 | 1058.6266 | 10.5863
6- 24.12 | Development of tube well in accordance with IS : 2800 (part I) and IS: 11189, to establish maximum rate of usable water yield without sand content (beyond permissible limit), with required capacity air compressor, running the compressor for required time till well is fully develo ped, measuring yield of well by "V" notch method or any other approved method, measuring static level & draw down etc. by step draw down method, collecting water sampl &getting tested in approved laboratory, disinfection of tubewell, all complete,including hire & labour charges of air compressor, tools & accessories etc., all as per requirement and direction of Engineer-in-charge. | 30 | Hrs. | Each | 916.8 | 27504
7 | Transportation and erection of drilling plants, developing equipments & all other required tools and M/C by suitable mechanical means including all cost loading, unloading, placing at work site and back after completion of work as per S/D of E/I. | 1 | No. | Each | 14000 | 14000
8 | Supplying all materials and labours for arrangement for additional water required during the drilling period for 80 Hrs & site clearance & leveling etc. And providing the soap duster etc. to staff engaged in drilling etc. all complete work as per specification & direction of E.I. | 1 | No. | Each | 25000 | 25000
9 | Chemical and bactirological testing of water sample including the cost of collection, carrying to designated PHE/other laboratory and submission of reports in triplicate as per direction of E/I. | 1 | No. | Each | 500 | 500
|  | TOTAL |  |  |  | 727318.15
|  | SAY |  |  |  | 727318
Executive Engineer
|  | P.H. Division, Begusarai | [7 empty] | 24156

## 450 x 300 mm t-well
Sub Estimate No.43
Construction of 450mm x 300mm dia & 125M deep H/Y Tube well
S.No. | Description | Qty. |  | Unit | Rate | Amount
1 | Providing all materials, labours, & equipments for drilling by Reverse Rotary rig machine for following dia bore hole in all kind of soil mixed with kanker, sand stone including providing sample box, and collection strata sample at every 3.0M depth of drilling for asserting proper aquifer for completing High Yielding Tube Well all complete as per IS:2800-1979 & PHED specification and direction of E/I.
| (a) 900 mm dia bore from G.L. to 30M | 30 | M | P/M | 3000 | 90000
| (b) 600 mm dia bore from 30M to 90M | 60 | M | P/M | 1402 | 84120
| (c) 600 mm dia bore from 90M to 150M | 35 | M | P/M | 1402 | 49070
2 | Supplying all materials & providing all equipment & labours and lowering the following pipe with socket and cutting the pipe for required size as per approved assay and strata chart including welding along with the socket/MS Ring and strip as per required etc.all complete as per S/D of E/I.
| (a) 450mm x 7mm thick M.S.E.R.W housing pipe (TATA OR JINDAL and I.S.I mark). | 30 | M | P/M | 9944.68 | 298340.4 | 8573
| (b) 300mm x 6mm thick M.S.E.R.W blank pipe (TATA OR JINDAL and I.S.I mark. | 60 | M | P/M | 3406 | 204360 | 3304
| (c) 300mm x 6mm thick M.S slotted pipe I.S.I mark including cost at slotted pipe as per standard design as per S/D of E/I. (Johnson make) | 30 | M | P/M | 6945.26 | 208357.8
3 | Providing all tools and labour including supplying fitting & fixing the following accessories for aforesaid 450mm x 300mm T/Well as per direction of E/I.
| (a) 450 mm dia M.S. well cap | 1 | No. | Each | 950 | 950
| (b) M.S clamp set of required Dia as per IS 2800 including necessary bolts and nuts required | 1 | No. | P.Pair | 1600 | 1600
| (c) M.S Centre guide suitable for 450mm dia pipe | 4 | Nos. | Each | 375 | 1500
| (d) M.S Centre guide suitable for 300mm dia pipe | 6 | Nos. | Each | 350 | 2100
| (e) 450mm x 300 mm dia 6 mm wall thickness M.S Reducer | 1 | No. | Each | 1800 | 1800
| (f) 300 mm dia & 6 mm thick M.S shoe plug | 1 | Nos. | Each | 975 | 975
4a 24.8 | Providing all materials, labours, & tools for providing and placing around tubewell double washed pea gravel confirming to IS:8419-1977 of size 4mm to 8mm from dalbhumgarh of east singhbhum (JH) inclusive of loading, carriage, unloading & stacking in proper shape for measurement at site. ( Stock measurement of clean and washed gravel shall be taken 13" as 12" in height to count void) as per direction of E/I. | 30 | M3 | P/M3 | 1343.2 | 40296 |  | Carriage of Pea Gravel from Dhalbhumigarh (taken distance 480km.Pakka+5Km unsurface road) (1.6*(480*11.20+5*13.50)+195.10)=8904.70+1% L.Cess+12%-GST)=Rs.10,062.31
4b | Carriage of Pea Gravel from Dhalbhumigarh (taken distance 480km.Pakka+5Km unsurface road) (1.6*(480*11.20+5*13.50)+195.10)=8904.70+1% L.Cess+12%-GST)=Rs.10,062.31 | 30 | M3 | P/M3 | 10062.31 | 301869.3 |  | 1.6(480*8.4+5*10.10)+171 | 6703 | 6770.03 | 804.36 | 7574.39 | 1058.6266 | 10.5863
5 24.12 | Development of tube well in accordance with IS : 2800 (part I) and IS: 11189, to establish maximum rate of usable water yield without sand content (beyond permissible limit), with required capacity air compressor, running the compressor for required time till well is fully develo ped, measuring yield of well by "V" notch method or any other approved method, measuring static level & draw down etc. by step draw down method, collecting water sampl & getting tested in approved laboratory, i/c disinfection of tubewell, all complete,including hire & labour charges of air compressor, tools & accessories etc., all as per requirement and direction of Engineer-in-charge. | 72 | Hrs. | Each | 916.8 | 66009.6 |  | 594.6
6 | Transportation and erection of drilling plants, developing equipments & all other required tools and M/C by and suitable mechanical means including all cost of loading, unloading, placing at work site and back after completion of work as per S/D of E/I. | 1 | No. | Each | 14000 | 14000
7 | Supplying all materials and labours for arrangement for additional water required during the drilling period for 80 Hrs & site clearance & leveling etc. And providing the soap duster etc. to staff engaged in drilling etc. all complete work as per specification & direction of E.I. | 1 | Job | Each | 25000 | 25000
|  | TOTAL |  |  |  | 1390348.1
[5 empty] | Say | 1390348
Executive Engineer
P.H. Division, Begusarai

## 10000 Gallon
Sub-Estimate No.-44
Painting of 10000 Gallon Water Tower
S.N. | Description |  | Quantity |  | Unit | Rate | Amount
Water Tower
1 14.75A | Providing all labours, material and cleaning of tank from inside and doing chlorination etc. all complete as per specification & direction of E/I.
| 10000 Gallon x 4.54 Lit/Gallon = |  | 45400 | Ltr | P/Ltr | 0.2 | 9080
2 | Removing white or color wash by scraping and sand prepairing the surface smooth including necessary repair of scratches etc. all complete.
13.74 | Column | 6 Nos. x 3.14 x 0.35 x 18 | 118.692
| Bracings | 3 Nos.x 2 x 3.14 x 2.975 x 2 x (.25+.4)= | 78.4686
| Bottom Dome | 2 x 3.14 x 5.501 x(1.04-.15) | 30.7462
| Bottom Ring Beam | 2 x 3.14 x 2.975 x (0.35+2x0.75)= | 34.5635
| Top Dome | 2 x 3.14 x5.626 x 1.04= | 36.7445
| Cylindrical Wall | 2 x 3.14 x 3.15 x 3.24 | 64.0937
| Roof Dome Beam | 2 x 3.14 x 3.20 x (0.2+2x.05) | 6.0288
| Walk way both side | 2 x 3.14 x (3.15+1.00)x (3.15-1.00)= | 56.0333
| Border of Walky Way | 2 x 3.14 x 4.15 x 0.1 | 2.6062
| Stair Landing | 2 Nos. x 2 x 2.75 x 1.5 | 16.5
Office Accomodation
| Wall (inner & outer) | 6 Nos.x 2 x 2.76 x 3.75 = | 124.2
roof ceiling
| 3.14 x (2.725)² = |  | 23.7462 | [6 empty] | 0.05
| Chhaja (door+window) | 0.6 x 1.2 x 1.15 + 3 Nos.(0.9 x .45 x 1.15) | 2.2252
Deduction
| Door & Window | 1.2 x 2.1 + 3 x 0.9 x 1.2 | 5.76 | [5 empty] | 2.355
|  |  | 588.8884 | M² | P/M² | 7.7 | 4534.4403
3 5.11.1 | Providing materials for extra scaffolding for exterior surface of each consecutive floor etc. all complete. ( 2 x 3.14 x 3 x 18.54) |  | 349.2936 | M² | P/M² | 174 | 60777.0864
4 13.78.1 | Applying one coat of cement primer of approved brand and manufacture on wall surface: Cement primer |  | 588.8884 | M² | P/M² | 38.6 | 22731.0903
5 | Finishing walls with Acrylic Smooth exterior paint of required shade: Old work (Two or more coat applied @ 1.67 ltr/ 10 sqm) onexisting cement paint surface
14.66.1 | On old work |  | 588.8884 | M² | P/M² | 81.7 | 48112.1782
13.79.3 | Painting (one or more coats) on rain water, soil waste and vent pipes and fittings with black anticorrosive bitumastic paint approved brand and manufacture on old work: (including extra cost of scafolding)
13.79.4 | 100 mm dia | 2 Nos. x 15M | 30 | M | P/M | 15.9 | 477 |  |  |  | 18540
13.79.5 | 150 mm dia | 1No. x 15M | 15 | M | P/M | 23 | 345 | 2 |  |  | 18940
13.79.6 | Providing all labours, materilas and scafolding for wirting work for the monogram of P.H.E.D with capacity of water tower & name of division on both visible sides of Water Tower and also on pump chamber. |  | 1 | Job | Each | 7500 | 7500
13.79.7 | Providing all labours, materials for fixing perforrated mosquitto jali on ventilator shaft. |  | 1 | Job | Each | 1000 | 1000
13.79.8 | Painting G.I. pipes and fittings with two coats of anti-corrosive bitumastic paint of approved quality on ladder, railing, boundary wall grill etc.
13.79.9 | Old steel work (one or more coats) |  | 25 | M² | M² | 54.1 | 1352.5
[6 empty] | Total | 155909.2953 |  |  |  | M²
[6 empty] | Add 5.36% | 8356.7382
[6 empty] | Grand Total | 164266.0335 |  | 93
[6 empty] | Say | 164266

## 20000 Gallon
Sub-Estimate No.-45
Painting of 20000 Gallon Water Tower
S.N. | Description | [5 empty] | Quantity |  | Unit | Rate | Amount
Water Tower
1 | Providing all labours, material and cleaning of tank from inside and doing chlorination etc. all complete as per specification & direction of E/I.
| 20000 Gallon x 4.54 Lit/Gallon = | [5 empty] | 90800 | Ltr | P/Ltr | 0.2 | 18160
2 | Removing white or color wash by scraping and sand prepairing the surface smooth including necessary repair of scratches etc. all complete.
13.74 | Column | 6 Nos. x 3.14 x 0.35 x 15 |  |  |  |  | 98.91
| Bracings | 3 Nos.x 2 x 3.14 x 2.975 x 2 x (.25+.4)= |  |  |  |  | 78.4686
| Bottom Dome | 2 x 3.14 x 5.682 x(0.965-.15) |  |  |  |  | 29.0816
| Bottom Ring Beam | 2 x 3.14 x 2.975 x (0.35+2x1.1)= |  |  |  |  | 47.6417
| Top Dome | 2 x 3.14 x5.807 x 0.94= |  |  |  |  | 34.2799
| Cylindrical Wall | 2 x 3.14 x 3.15 x 4.665 |  |  |  |  | 92.283
| Roof Dome Beam | 2 x 3.14 x 3.20 x (0.2+2x.05) |  |  |  |  | 6.0288
| Walk way both side | 2 x 3.14 x (3.15+1.00)x (3.15-1.00)= |  |  |  |  | 56.0333
| Border of Walky Way | 2 x 3.14 x 4.15 x 0.1 |  |  |  |  | 2.6062
| Stair Landing | 2 Nos. x 2 x 2.75 x 1.5 |  |  |  |  | 16.5
Office Accomodation
| Wall (inner & outer) | 6 Nos.x 2 x 2.76 x 3.75 = |  |  |  |  | 124.2
| roof ceiling | 3.14 x (2.725)² = |  |  |  |  | 23.7462
| Toilet | 2 x (1.2 x 2.1 + 2.5 x 2.1) |  |  |  |  | 15.54
| Chhaja (door+window) | 0.6 x 1.2 x 1.15 + 3 Nos.(0.9 x .45 x 1.15) |  |  |  |  | 2.2252
Deduction
| Door & Window | 1 x 2.1 + 3 x 0.9 x 1.2 |  |  |  |  | 5.76
[7 empty] | 621.7846 | M² | P/M² | 7.7 | 4787.7412
3 | Providing materials for extra scaffolding for exterior surface of each consecutive floor etc. all complete. ( 2 x 3.14 x 3 x 18.54) | [5 empty] | 349.2936 | M² | P/M² | 174 | 60777.0864
4 13.78.1 | Applying one coat of cement primer of approved brand and manufacture on wall surface: Cement primer | [5 empty] | 621.7846 | M² | P/M² | 38.6 | 24000.8846
5 | Finishing walls with Acrylic Smooth exterior paint of required shade: Old work (Two or more coat applied @ 1.67 ltr/ 10 sqm) onexisting cement paint surface
14.66.1 | On old concrete work | [5 empty] | 621.7846 | M² | P/M² | 81.7 | 50799.7998
6- 13.82.3 | Painting with ready mixed paint of approved brand and manufacture in all shades to give an even shade | [12 empty] | 60.7
| In Door | [12 empty] | 60.7
| 1 | 2.25 | 1 | 2.1 | = | 4.725
In windows
| 3 | 2.25 | 0.9 | 1.2 | = | 7.29
| In Grill |  |  |  |  | 3.24
1.08
[6 empty] | 15.255 | 15.255 | M² | P/M² | 48 | 732.24
7 | Painting (one or more coats) on rain water, soil waste and vent pipes and fittings with black anticorrosive bitumastic paint approved brand and manufacture on old work: (including extra cost of scafolding)
13.85.3 | 100 mm dia | 2 Nos. x 15M |  |  |  |  | 30 | M | P/M | 15.9 | 477
13.85.4 | 150 mm dia | 1No. x 15M |  |  |  |  | 15 | M | P/M | 23 | 345 | 2
8 | Providing all labours, materilas and scafolding for wirting work for the monogram of P.H.E.D with capacity of water tower & name of division on both visible sides of Water Tower and also on pump chamber. | [5 empty] | 1 | Job | Each | 7500 | 7500
10 | Providing all labours, materials for fixing perforrated mosquitto jali on ventilator shaft. | [5 empty] | 1 | Job | Each | 1000 | 1000
11 | Painting G.I. pipes and fittings with two coats of anti-corrosive bitumastic paint of approved quality on ladder, railing, boundary wall grill etc.
13.82.3 | Old steel work (one or more coats) | [5 empty] | 25.3 | M² | M² | 54.1 | 1368.73
[10 empty] | Total | 169948.482 |  | M²
[10 empty] | Add 5.36% | 9109.2386
[10 empty] | Grand Total | 179057.7206
[10 empty] | Say | 179058

## 40000 Gallon
Sub-Estimate No.-46
Painting of 18 M 40000 Gallon Water Tower
S.N. | Description | [5 empty] | Quantity |  | Unit | Rate | Amount
Water Tower
1 | Providing all labours, material and cleaning of tank from inside and doing chlorination etc. all complete as per specification & direction of E/I.
| 40000 Gallon x 4.54 Lit/Gallon = | [5 empty] | 181600 | Ltr | P/Ltr | 0.2 | 36320
2 | Removing white or color wash by scraping and sand prepairing the surface smooth including necessary repair of scratches etc. all complete.
13.74 | Column | 6 Nos. x 3.14 x 0.40 x 18 |  |  |  |  | 60.288 |  |  |  |  | 1.413
| Bracings | 5 Nos.x 6 x 2 x2.55 x (0.45+0.25) |  |  |  |  | 107.1 |  |  |  |  | 4.6346
| Bottom Dome | 2 x 3.14 x 5.588 x(0.935-.15) |  |  |  |  | 27.5477
| Bottom Ring Beam | 3.14 x (3.200+2.800) x (3.200-2.800) |  |  |  |  | 7.536
|  | 2 x 3.14 x (3.200+2.800) x 0.950 |  |  |  |  | 35.796
| Conical Wall | 2 x 3.14 x (3.200+4.5)/2 x 1.75 |  |  |  |  | 42.3115
| Cylindrical Wall | 2 x 3.14 x 4.65 x 2.1 |  |  |  |  | 61.3242
| Roof Dome Beam | 2 x 3.14 x 4.8x0.25 |  |  |  |  | 7.536
| Top Dome | 2 x 3.14 x 8.638 x 1.37= |  |  |  |  | 74.3179
| Walk way both side | 2 x 3.14 x (5.575+4.65) x (5.575 - 4.65) |  |  |  |  | 59.397
| Border of Walky Way | 2 x 3.14 x 5.575 x 0.125 |  |  |  |  | 4.3764
| Bottom of Walky Way | 3.14 x (5.0+5.5) x (5.5-5.0) |  |  |  |  | 16.485
| Middle Ring beam | 3.14 x (5.0+4.5) x (5.0-4.5) |  |  |  |  | 14.915
|  | 2 x 3.14 x 5.0 x 0.40 |  |  |  |  | 12.56
| Stair Landing | 2 Nos. x 2 x 2.75 x 1.5 |  |  |  |  | 16.5
Office Accomodation
| Wall (inner & outer) | 6 Nos.x 2 x 2.55 x 3.95 = |  |  |  |  | 121.818
| roof ceiling | 3.14 x (2.8)² = |  |  |  |  | 24.6176
| Toilet | 2 x (2.25 x 2.1 + 0.95 x 2.1) |  |  |  |  | 13.44
| Chhaja (door+window) | 2 x 0.6 x1.2 x 1.15 + 3 Nos.x 2 x 1.2 x 0.45 x 1.15) |  |  |  |  | 5.382
Deduction
| Door & Window | 1.2 x 2.1 + 3 x 1.2 x 1.5 |  |  |  |  | 7.92
[7 empty] | 705.3283 | M² | P/M² | 7.7 | 5431.0281
3 | Providing materials for extra scaffolding for exterior surface of each consecutive floor etc. all complete. ( 2 x 3.14 x 3 x 27.295) | [5 empty] | 526.107 | M² | P/M² | 174 | 91542.618 | 27.295
4 13.78.1 | Applying one coat of cement primer of approved brand and manufacture on wall surface: Cement primer | [5 empty] | 705.3283 | M² | P/M² | 38.6 | 27225.6731
5 | Finishing walls with Acrylic Smooth exterior paint of required shade: Old work (Two or more coat applied @ 1.67 ltr/ 10 sqm) onexisting cement paint surface
14.66.1 | On concrete work | [5 empty] | 705.3283 | M² | P/M² | 81.7 | 57625.3237
6- 13.82.3 | Painting with ready mixed paint of approved brand and manufacture in all shades to give an even shade | [12 empty] | 60.7
| In Door | [12 empty] | 60.7
| 1 | 2.25 | 1.2 | 2.1 | = | 5.67
In windows
| 3 | 2.25 | 1.5 | 1.2 | = | 12.15
| In Grill |  |  |  |  | 3.24
1.08
[6 empty] | 21.06 | 21.06 | M² | P/M² | 48 | 1010.88
7 | Painting (one or more coats) on rain water, soil waste and vent pipes and fittings with black anticorrosive bitumastic paint approved brand and manufacture on old work: (including extra cost of scafolding)
13.85.3 | 100 mm dia | 2 Nos. x 21M |  |  |  |  | 42 | M | P/M | 15.9 | 667.8
13.85.4 | 150 mm dia | 1No. x 21M |  |  |  |  | 21 | M | P/M | 23 | 483 | 2
8 | Providing all labours, materilas and scafolding for wirting work for the monogram of P.H.E.D with capacity of water tower & name of division on both visible sides of Water Tower and also on pump chamber. | [5 empty] | 1 | Job | Each | 7500 | 7500
9 | Providing all labours, materials for fixing perforrated mosquitto jali on ventilator shaft. | [5 empty] | 1 | Job | Each | 1000 | 1000
10 | Painting G.I. pipes and fittings with two coats of anti-corrosive bitumastic paint of approved quality on ladder, railing, boundary wall grill etc.
13.82.3 | Old steel work (one or more coats) | [5 empty] | 34.2 | M² | M² | 54.1 | 1850.22
[10 empty] | Total | 230656.5429 |  | M²
[10 empty] | Add 5.36% | 12363.1907
[10 empty] | Grand Total | 243019.7336
[10 empty] | Say | 243020
Executive Engineer
P.H. Division, Begusarai

## 50000 Gallon
Sub-Estimate No.-47
Renovation of 50000 Gallon Water Tower
S.N. | Description | [5 empty] | Quantity |  | Unit | Rate | Amount
Water Tower
1 14.75A | Providing all labours, material and cleaning of tank from inside and doing chlorination etc. all complete as per specification & direction of E/I.
| 50000 Gallon x 4.54 Lit/Gallon = | [5 empty] | 227000 | Ltr | P/Ltr | 0.2 | 45400
2 | Dismantling old plaster or skirting raking out joints and cleaning the surface for plaster including disposal of rubbish to the dumping ground within 50 metres lead.
15.56 | Tank wall inner portion 2 x 3.14 x 6.0 x 5.20 | [5 empty] | 195.936 | M² | P/M² | 21.7 | 4251.8112
3 | 20 mm cement plaster of mix 1:3 (1 cement: 3 coarse sand)
13.13.1+ 13.36 | Tank wall inner portion 2 x 3.14 x 6.0 x 5.20 | [5 empty] | 195.936 | M² | P/M² | 227.4 | 44555.8464
4 | Removing white or color wash by scraping and sand prepairing the surface smooth including necessary repair of scratches etc. all complete.
13.74 | Column | 6 Nos. x 3.14 x 0.5 x 18 |  |  |  |  | 169.56
| Bracings | 5 Nos.x 6 x 2 x2.57 x (0.5+0.25) |  |  |  |  | 115.65
| Bottom Dome | 2 x 3.14 x 6.069 x(1.005-.15) |  |  |  |  | 32.5869
| Bottom Ring Beam | 3.14 x (3.575+2.925) x (3.575-2.925) |  |  |  |  | 13.2665
|  | 2 x 3.14 x (3.575+2.925) x 1.1 |  |  |  |  | 44.902
| Conical Wall | 2 x 3.14 x (3.575+4.75)/2 x 2.15 |  |  |  |  | 56.2021
| Cylindrical Wall | 2 x 3.14 x 4.9 x 3.95 |  |  |  |  | 121.5494
| Roof Dome Ring Beam | 2 x 3.14 x 5.05x0.3 |  |  |  |  | 9.5142
|  | 3.14 x (5.05+4.9) x (5.05-4.9) |  |  |  |  | 4.6864
| Top Dome | 2 x 3.14 x 9.019 x 1.44= |  |  |  |  | 81.5606
| Walk way top side | 3.14 x (5.9+4.9) x (5.9 - 4.9) |  |  |  |  | 33.912
| Border of Walky Way | 2 x 3.14 x 5.9 x 0.125 |  |  |  |  | 4.6315
| Bottom of Walky Way | 3.14 x (5.9+5.25) x (5.9-5.25) |  |  |  |  | 22.7572
| Middle Ring beam | 3.14 x (5.25+4.75) x (5.25-4.75) |  |  |  |  | 15.7
|  | 2x 3.14 x 5.25x.325 |  |  |  |  | 10.7152
| Stair Landing | [5 empty] | 16.5
Removing white or color wash by scraping and sand prepairing the surface smooth including necessary repair of scratches etc. all complete.
| Wall (inner & outer) | 6 Nos.x 2 x 2.57 x 3.95 = |  |  |  |  | 121.818
| roof ceiling | 3.14 x (2.8)² = |  |  |  |  | 24.6176
| Toilet | 2 x (2.25 x 2.1 + 0.95 x 2.1) |  |  |  |  | 13.44
| Chhaja (door+window) | 2 x 0.6 x1.2 x 1.15 + 3 Nos.x 2 x 1.2 x 0.45 x 1.15) |  |  |  |  | 5.382
Deduction
| Door & Window | 1.2 x 2.1 + 3 x 1.2 x 1.5 |  |  |  |  | 7.92
|  |  |  | Total Area |  |  | 916.9516 | M² | P/M² | 7.7 | 7060.5276
|  |  | Net Area to Removing |  |  |  | 687.7137
5 5.11.1 | Providing materials for extra scaffolding for exterior surface of each consecutive floor etc. all complete. ( 2 x 3.14 x 3 x 22) | [5 empty] | 414.48 | M² | P/M² | 174 | 72119.52 | 21.95
6 13.78.1 | Applying one coat of cement primer of approved brand and manufacture on wall surface: Cement primer | [5 empty] | 916.9516 | M² | P/M² | 38.6 | 35394.3331
7 | Finishing walls with Acrylic Smooth exterior paint of required shade:
14.66.1 | Old work (Two or more coat applied @ 1.67 ltr/ 10 sqm) on existing cement paint surface | [5 empty] | 916.9516 | M² | P/M² | 81.7 | 74914.9485
8- 13.82.3 | Painting with ready mixed paint of approved brand and manufacture in all shades to give an even shade
| In Door | [10 empty] | 1 | 2.25 | 1.05 | 1.95 | = | 4.6069
| 1 | 2.25 | 1.2 | 2.1 | = | 5.67 | [5 empty] | In windows
| In windows | [10 empty] | 2 | 2.25 | 0.9 | 1.2 | = | 4.86
| 3 | 2.25 | 1.5 | 1.2 | = | 12.15 | [5 empty] | In Grill |  |  |  |  | 2.16
| In Grill |  |  |  |  | 3.24 | [5 empty] | In R.S. Joist |  |  |  |  | 5
16.6269
[6 empty] | 21.06 | 21.06 | M² | P/M² | 54.1 | 1139.346
9 | Painting (one or more coats) on rain water, soil waste and vent pipes and fittings with black anticorrosive bitumastic paint approved brand and manufacture on old work: (including extra cost of scafolding)
13.85.3 | 100 mm dia | 2 Nos. x 18M |  |  |  |  | 36 | M | P/M | 15.9 | 572.4
13.85.4 | 150 mm dia | 1No. x 18M |  |  |  |  | 18 | M | P/M | 23 | 414
10 | Providing all labours, materilas and scafolding for wirting work for the monogram of P.H.E.D with capacity of water tower & name of division on both visible sides of Water Tower and also on pump chamber. | [5 empty] | 1 | Job | Each | 7500 | 7500
11 | Providing all labours, materials for fixing perforrated mosquitto jali on ventilator shaft. | [5 empty] | 1 | Job | Each | 1000 | 1000
12 | Painting G.I. pipes and fittings with two coats of anti-corrosive bitumastic paint of approved quality on ladder, railing, boundary wall grill etc.
13.82.3 | Old steel work (one or more coats) | [5 empty] | 35.5 | M² | P/M² | 54.1 | 1920.55
[10 empty] | Total | 296243.2828
[10 empty] | Add 5.36% | 15878.64
[10 empty] | Grand Total | 312121.9228
[10 empty] | Say | 312122