## (FINAL Scheduel of rate)
SCHEDULE OF RATE FOR INTERNAL ELECTRIFICATION WORK FOR LIBRARY BUILDING (GROUND FLOOR & FIRST FLOOR), KANKER DIST- KANKER (C.G.)
S.N. | SOR Item No. | Particulars of Item | Unit | Rate | Rate in Word
1 | 1.7 | Wiring for light/ fan/ exhaust fan / call bell point with 3x1.5 sqmm FRLS PVC insulated stranded copper conductor wire for phase, neutral and earth in concealed FRLS PVC conduit (heavy duty, thickness of pipe should be 2 mm) with 5/6 amp modular switch, modular base and cover plate, suitable size G.I. box as per specification and IS: 694 (2010), IS: 9537 (2000 Part 5) Make:- PVC Pipe Polycab/Precision/Saraswati (ISI) Wire- Polycab/Havells/RR Kable (ISI) Switch Socket & accessories- Legrand (Mylinc)/ Havells (Verona) (ISI)
| 1.7.1 | Short Point | Point | 235 | Two Hundred Thirty Five Only
| 1.7.2 | Medium Point | Point | 374 | Three Hundred Seventy Four Only
| 1.7.3 | Long Point | Point | 518 | Five Hundred Eighteen Only
2 | 1.9 | Extra for providing and fixing light plug point on board in concealed FRLS PVC conduit (heavy duty, thickness of pipe should be 2 mm) point wiring with modular type 3 pin 5/6 amp socket outlet and 5/6 amp switch including cost of base and cover plate and G. I. box etc. as per specification and IS: 694 (2010), IS: 9537 (2000 Part 5) Make:- PVC Pipe Polycab/Precision/Saraswati (ISI) Wire- Polycab/Havells/RR Kable (ISI) Switch Socket & accessories- Legrand (Myline)/ Havells (Verona) (ISI) | Point | 191 | One Hundred Ninty One Only
3 | 1.10 | Wiring for light plug point with 3x2.5 sq mm FRLS PVC insulated stranded copper conductor wire for phase, neutral and earth in concealed FRLS PVC conduit (heavy duty, thickness of pipe should be 2 mm) along with modular type 6 Amp switch and 3 pin 6 amps socket outlet with modular base and cover plate, suitable size G.I. box, earthing the switch box and socket outlet with same size wire etc. as per specification and IS: 694 (2010), IS: 9537 (2000 Part 5) Make:- PVC Pipe Polycab/Precision/Saraswati (ISI) Wire- Polycab/Havells/RR Kable (ISI) Switch Socket & accessories- Legrand (Mylinc)/ Havells (Verona) (ISI)
| 1.10.2 | Medium Point | Point | 582 | Five Hundred Eighty Two Only
| 1.10.3 | Long Point | Point | 814 | Eight Hundred Fourteen Only
| 1.10.4 | Extra Long Point- 1 | Point | 1149 | One Thousand One Hundred Fourty Nine Only
4 | 1.11 | Wiring for power plug point with 3x4 sq mm FRLS PVC insulated stranded copper conductor wire for phase, neutral and earth in concealed FRLS PVC conduit (heavy duty, thickness of pipe should be 2 mm) along with modular type 16 Amp switch and 6 pin 16 amps socket outlet with modular base and cover plate, suitable size G.I. box, earthing the switch box and socket outlet with same size wire etc. as per specification and IS: 694 (2010), IS: 9537 (2000 Part 5) Make:-PVC Polycab/Precision/Saraswati Wire- Polycab/Havells/RR Kable (ISI) Switch Socket & accessories- Legrand (Mylinc)/ Havells (Verona) (ISI)
| 1.11.2 | Medium Point | Point | 831 | Eight Hundred Thirty One Only
| 1.11.3 | Long Point | Point | 1191 | One Thousand One Hundred Ninty One Only
| 1.11.4 | Extra Long Point I | Point | 1594 | One Thousand Five Hundred Ninty Four Only
| 1.11.5 | Extra Long Point II | Point | 2042 | Two Thousand Fourty Two Only
5 | 1.13 | Wiring for circuit/ sub main wiring along with earth wire with the following sizes of FRLS PVC insulated copper conductor, wire in concealed FRLS PVC conduit (heavy duty, thickness of pipe should be 2 mm) as per specification and IS: 694 (2010), IS: 9537 (2000 Part 5) Make:- PVC Pipe- Polycab/Precision/Saraswati (ISI) Wire- Polycab/Havells/RR Kable (ISI)
| 1.13.2 | 3 X 2.5 sq. mm in 20mm conduit | Mtr | 98 | Ninty Eight Only
| 1.13.3 | 6 X 2.5 sq. mm in 25mm conduit | Mtr | 151 | One Hundred Fifty One Only
| 1.13.4 | 9 X 2.5 sq. mm in 32mm conduit | Mtr | 210 | Two Hundred Ten Only
| 1.13.14 | 6 X 10 sq. mm in 40mm conduit | Mtr | 454 | Four Hundred Fifty Four Only
6 | 1.15 | Supplying and fixing of following sizes FRLS PVC conduit (heavy duty, thickness of pipe should be 2 mm) along with accessories in concealed complete as per specification and IS: 9537 (2000 Part 5) Make:- PVC Pipe- Polycab/Precision/Saraswati (ISI) Wire- Polycab/Havells/RR Kable (ISI)
| 1.15.2 | 25 mm | Mtr | 46 | Fouty Six Only
7 | 3.11 | Supplying and drawing following sizes of FRLS PVC insulated copper conductor, multi strand wire in the existing surface/ concealed, FRLS PVC conduit / PVC casing caping as per specification and IS: 694 (2010) Make:- Wire- Polycab/Havells/RR Kable (ISI)
| 3.11.1 | 1 x 1.5 sq. mm | Mtr | 13 | Thirteen Only
8 | 3.12 | Supplying and drawing following pair 0.5 mm FRLS PVC insulated copper conductor, unarmored telephone wire in the existing surface/ concealed Steel/FRLS PVC conduit as per specification and IS: 694 (2010) Make:- Wire- Polycab/Havells/RR Kable (ISI)
| 3.12.2 | 2 Pair | Metre | 10 | Ten Only
9 | 3.13 | Supplying and drawing following grade co-axial TV wire FRLS PVC insulated, shielded with fine tinned copper braid and protected with PVC sheath in the existing surface/ concealed Steel/PVC conduit as per specification and IS: 694 (2010) Make:- Wire- Polycab/Havells/RR Kable (ISI)
| 3.13.1 | RG-6 grade | Mtr | 12 | Twelve Only
10 | 4.4 | Supplying and fixing following size/ modules, GI box along with modular base & cover plate for modular switches in recess etc as per specification. Make:- Wire- Legrand/Havell (ISI)
| 4.4.1 | 75mmX75mm (1/2 Module) | Each | 73 | Seventy Three Only
11 | 5.4 | Supplying and fixing following modular switch, socket, other accessories on the existing modular plate & switch box including connections but excluding modular plate etc. as per specification. Make:- Switch Socket & accessories- Legrand (Mylinc)/ Havells (Verona) (ISI)
| 5.4.9 | Fan regulator (two module size) electronic stepped type moving all rounds | Each | 196 | One Hundred Ninty Six Only
| 5.4.11 | Plug Top (Duluxe Type) 3 Pin 16 Amps (For Power plug). | Each | 75 | Seventy Five Only
| 5.4.15 | Telephone Socket outlet | Each | 62 | Sixty Two Only
| 5.4.16 | T.V. antenna socket outlet | Each | 65 | Sixty Five Only
| 5.4.18 | 25/32 amp A.C. Starter switch | Each | 217 | Two Hundred Seventy Only
12 | 5.6 | Providing and fixing composite unit for computer points having modular type 1 No 6 pin 16 amp socket outlet, 1 No 16 amp switch, 3 Nos 3 pin 6 amp socket outlets, 3 Nos 6 amp switches, suitable G.I. box, base and cover plates, earthing the sockets and switch box including etc. as per specification. Make:- Switch Socket & accessories- Legrand (Mylinc)/ Havells (Verona) (ISI) | Each | 720 | Seven Hundred Twenty Only
13 | 5.9 | Providing and fixing round/ hexagonal fan box (125mm dia) depth 75mm (max.) with 12mm dia steel bar hook, 1.6mm thick MS sheet cover, in RCC slab etc. as per specification. | Each | 37 | Thirty Seven Only
14 | 6.1 | Supplying, installation, testing and commissioning of following sizes ceiling fan including wiring the down rods of standard length up to 30 cm with 1.5 sq. mm FRLS PVC insulated, copper conductor, single core cable, earthing etc. complete as required.P.F. should be greater than 0.9, with BEE Starrating from 1 star and above, IS:374:2019 including all amendments. Make:- Usha/Havells/Crompton/Bajaj/Orient (ISI)
| 6.1.3 | 1200 mm sweep | Each | 1497 | One Thousand Four Hundred Ninty Seven Only
15 | 6.8 | Supplying, installation, testing and commissioning of following sizes fancy exhaust fan having built in louvers in existing opening in wall including earthing etc. complete as per specification. P.F. should be greater than 0.9 Make:- Usha/Havells/Crompton/Bajaj/Orient (ISI)
| 6.8.2 | 300 mm sweep | Each | 1120 | One Thousand One Hundred Twenty Only
16 | 6.11 | Supplying and fixing following sizes of down rod of 15/20mm dia M.S. pipe of thickness 2 mm to ceiling fan including painting with matching colour etc. as per specification.
| 6.11.2 | 60 cm long | Each | 35 | Thirty Five Only
17 | 6.12 | Providing and fixing phenolic laminated sheet cover of 180 mm dia 3 mm thick on the fan box etc. as per specification. (If provided at the time of installation of celing fan) | Each | 49 | Fourty Nine Only
18 | 6.16 | Supplying, installation, testing and commissioning of following sleek LED panel down lighters (luminaries) in round/ square shape complete with electronic driver heat sink capacitor and all other accessories on surface/ in false ceiling etc. as per specification and P.F. should be greater than 0.9. LED chip efficacy ratio ≥ 100 lumens /watt. Make:- Havells/Wipro/Philips (ISI)
| 6.16.1 | 24 watt, size 300 x 300mm | Each | 1566 | One Hundred Five Hundred Sixty Six Only
19 | 6.17 | Supplying, fixing, testing and commissioning of following LED lamps with inbuilt electronic driver heat sink and all other accessories in existing holder/ luminaries as per specification and P.F. should be greater than 0.9. LED chip efficacy ratio ≥ 100 lumens /watt. Make:- Havells/Wipro/Philips (ISI)
| 6.17.4 | 9 Watt | Each | 126 | One Hundred Twenty Six Only
20 | 6.19 | Supplying, installation, testing and commissioning of following LED tube light fitting including batten with Electronic Driver Heat sink Capacitor complete with all other accessories on surface/infalse ceiling, including connection, earthing etc complete as per specification and furnishing 5 Yrs Warranty certificate from manufacturer. IP20 P.F. should be greater than 0.9 LED chipe fficacy ratio ≥100 lumens/watt. Make:- Havells/Wipro/Philips (ISI)
| 6.19.3 | 18/20 watt {4feet} | Each | 390 | Three Hundred Ninty Only
21 | 6.28 | Supplying, installation, testing and commissioning of following 230/250 volts LED street light fitting with all accessories like driver, heat sink made of die cast aluminium with IP 66 protection and 15 KV surge protection on pole bracket, including connection, earthing, Separate housing for driver etc complete as per specification and P.F. should be greater than 0.9. LED chip efficacy ratio ≥ 120 lumens /watt. Make:- Havells/Wipro/Philips (ISI)
| 6.28.6 | 45 watt | Each | 2407 | Two Thousand Four Hundred Seven Only
22 | 7.17 | Providing and making interconnection in cubical panel between BBC and switchgears with following size FRLS PVC insulated copper conductor wire lead of length upto 50cm including providing copper thimbles on both ends as per specification (To be measured separately for each phase/ neutral). Make:- Wire- Polycab/Havells/RR Kable (ISI)
| 7.17.1 | 10 sqmm (32 amp) | Each | 67 | Sexty Seven Only
23 | 7.19 | Fabrication, supply, installation, testing and commissioning of cubicle type compartmentalized wall/ floor mounted power cum control panel board of specified size and following depth made out of not less than 2 mm thick CRCA MS sheet with suitable size compartments for bus bars, switchgears and necessary cutouts for voltmeters, ammeters etc as per specifications including powder coating painting but without busbars, switchgears and other accessories etc complete as per specification. (Only face area is to be measured)
| 7.19.2 | Above 300 mm and upto 450 mm deep | sqm | 6638 | Six Thousand Six Hundred Thirty Eight Only
24 | 7.20 | Supply, installation, testing and commissioning of 4 pole (3 phase + neutral) aluminium bus bars in existing cubicle type compartmentalized wall/ floor mounted panel board along with suitable size and shape insulators, necessary bolts and nuts etc complete as required.
| 7.20.2 | 200 amp (30x5mm) | Mtr. | 800 | Eight Hundred Only
25 | 9.1 | Providing and fixing following rating and breaking capacity MCCB in existing cubicle panel board including drilling holes in cubicle panel, making connections, etc. as per specification, IS/ IEC: 60947-2 and Ics = 100 % Icu. Make :- Legrand/ Havells (ISI)
| 9.1.1 | 3 pole MCCB, 25-63A, Fixed Thermal Release, 10KA | Each | 1309 | One Thousand Three Hundred Nine Only
| 9.1.26 | 4 pole MCCB, 160A, Adjustable Thermal - Magnetic Release, 35KA | Each | 7939 | Seven Thousand Nine Hundred Thirty Nine Only
26 | 9.4 | Supplying and fixing on surface/ recess horizontal type following way, 415 volts, TPN MCB distribution board of sheet steel phosphatized and powder painted, complete with tinned copper busbar, neutral busbar, earth bar, din bar, detachable gland plate, including interconnections, earthing etc. as per specification. (But without MCB/RCCB/Isolator) Make :- Legrand/ Havells (ISI)
| 9.4.5 | 6 way Double door | Each | 1798 | One Thousand Seven Hundred Ninty Eight Only
27 | 9.11 | Supplying and fixing SP MCB, 240 volts, 'C' curve, suitable for inductive load in the existing MCB DB complete with connections, testing and commissioning etc. as per specification. Make :- Legrand/ Havells (ISI)
| 9.11.2 | 6 amps to 32 amps | Each | 130 | One Hundred Thity Only
28 | 9.12 | Supplying and fixing DP MCB, 240 volts, 'C' curve, suitable for lighting and other loads in the existing MCB DB complete with connections, testing and commissioning etc. as per specification. Make :- Legrand/ Havells (ISI)
| 9.12.3 | 40 amps | Each | 569 | Five Hundred Sixty Nine Only
29 | 9.16 | Supplying and fixing TP&N MCB, 440 volts, 'C' curve, suitable for lighting and other loads in the existing MCB DB complete with connections, testing and commissioning etc. as per specification. Make :- Legrand/ Havells (ISI)
| 9.16.5 | 63 amps | Each | 1161 | One Thousand One Hundred Sixty One
30 | 10.15 | Providing and fixing following rating current transformer in existing cubical panel including, connections, testing and commissioning etc. as per specification.
| 10.15.3 | 200/5 amps | Each | 306 | Three Hundred Six Only
31 | 10.17 | Providing and fixing penal mounting 230 volt LED type indicating lamp in existing cubical panel including, connections, testing and commissioning etc. as per specification. | Each | 83 | Eighty Three Only
32 | 10.19 | Providing and fixing penal mounting following rating digital type ammeter of size 100x100 (NS) in existing cubical panel including, connections, testing and commissioning etc. as per specification.
| 10.19.2 | 0-200 amps | Each | 860 | Eight Hundred Sixty Only
33 | 10.20 | Providing and fixing penal mounting 0-500 volt voltmeter of size 100x100 (NS) in existing cubical panel including, connections, testing and commissioning etc. as per specification.
| 10.20.2 | Digital type | Each | 736 | Seven Hundred Thirty Six Only
34 | 10.21 | Providing and fixing penal mounting selector switch in existing cubical panel including, connections, testing and commissioning etc. as per specification.
| 10.21.1 | For voltmeter | Each | 167 | One Hundred Sixty Seven Only
| 10.21.2 | For ammeter | Each | 183 | One Hundred Eighty Three Only
35 | 12.16 | Providing and fixing 25 mm X 5 mm G.I. strip on surface or in recess for connections etc. as per specification. Make:- Legrand / Havells (ISI) | Metre | 101 | One Hundred One Only
36 | 12.19 | Providing maintenance free earthing with following size GI pipe including making bore pit of minimum 150mm dia, providing and laying approved make Earthing Electrode of Pipe-in-Pipe technology as per IS 3043(R 2016) -1987 made of corrosion free G.I. Pipes having outer pipe of 80mm dia and inner pipe of 50mm dia and filling with specified qty highly conductive compound around pipe and above that with soft soil in bore pit complete and providing masonry enclosure with cover plate having locking arrangement and watering pipe etc. as per specification:
| 12.19.2 | With 2 metre long GI Pipes and 25 kg back filling compound. | Each | 7253 | Seven Thousand Two Hundred Fifty Three Only
37 | 14.1 | Supplying and laying ISI marked double wall HDPE pipe (IS 14930 Part II) having corrugation on the outer wall and plan surface on inner wall in ground below road, path etc at a depth not less than 40 cm and upto 90 cm including excavation, dismantling of road if required and refilling the trench with excavated material, ramming and making the surface good etc. as per specification. Make:- Kissan/Supreme/ Finolex
| 14.1.4 | 120 mm outer dia and 103.5 mm Inner dia | Metre | 223 | Two Hundred Twenty Three Only
38 | 15.3 | Supplying and laying following sizes one number FRLS PVC insulated, PVC sheathed, steel armoured, aluminium conductor power cable of 1.1 KV grade in existing RCC/HUME/ STONEWARE/ METAL/HDPE pipe as perspecification, IS:9537 (2000,Part5) Make:- Polycab/Havells/KEI (ISI)
| 15.3.14 | 3.5 x 70 sq. mm. | Metre | 219 | Two Hundred Ninteen Only
39 | 15.23 | Supplying and making end termination with brass compression gland and aluminum lugs forfollowing size armoured aluminum conductor power cable of 1.1 KV grade as per specification..
| 15.23.15 | 3½ X 70 sq. mm (35 mm) | Each | 176 | One Hundred Seventy Six Only
40 | 20.6 | Supplying and erection of angle/channel iron cross arms/ bracket/ other fitting of approved size and shape including drilling of holes for insulator pins, bolts and nuts etc as per specification. | kg | 68 | Sixty Eight Only
41 | 26.17 | Supply and erecting following ISI marked Fire extenguishers on wall/ column including erecting bracket etc complete.
| 26.17.6 | CO2 type Fire Extinguisher ISI marked confirming to IS:15683:2018 Capacity 3Kg. INITIAL CHARGE:- Carbon dioxide used in extinguishers shall comply with IS 15222. FIRE RATING:- 34B. Complete with Hose Assembly and horn, locking arrangement, operation manual, bracket with two screw and sleeve | Each | 5633 | Five Thousand Six Hundred Thirty Three Only
Assistant Engineer (Elect)
CG Housing & Infra.Dev.Board
Electrical Sub-Div., Jagdalpur
Executive Engineer (Elect)
CG Housing & Infra.Dev.Board
Electrical Div- Jagdalpur
Sub Engineer (Elect)
CG Housing & Infra.Dev.Board
Electrical Sub-Div., Jagdalpur

## (FINAL Scheduel of rate) (2) (hidden)
SCHEDULE OF RATE FOR INTERNAL ELECTRIFICATION WORK FOR SPECIALIZED ADOPTION AGENCY & CHILD LINE BUILDING, AT KANKER DIST. KANKER (C.G.)
S.N. | SOR Item No. | Particulars of Item | Unit | Rate | Rate in Word
1 | 1.7 | Wiring for light/ fan/ exhaust fan / call bell point with 3x1.5 sqmm FRLS PVC insulated stranded copper conductor wire for phase, neutral and earth in concealed FRLS PVC conduit (heavy duty, thickness of pipe should be 2 mm) with 5/6 amp modular switch, modular base and cover plate, suitable size G.I. box as per specification and IS: 694 (2010), IS: 9537 (2000 Part 5) Make:- PVC Pipe Polycab/Precision/Saraswati (ISI) Wire- Polycab/Havells/RR Kable (ISI) Switch Socket & accessories- Legrand (Mylinc)/ Havells (Verona) (ISI)
| 1.7.1 | Short Point | Point | 235 | Two Hundred Thirty Five Only
| 1.7.2 | Medium Point | Point | 374 | Three Hundred Seventy Four Only
| 1.7.3 | Long Point | Point | 518 | Five Hundred Eighteen Only
2 | 1.8 | Wiring for twin control light point with 3x1.5 sqmm FRLS PVC insulated stranded copper conductor wire for phase, neutral and earth in concealed FRLS PVC conduit (heavy duty, thickness of pipe should be 2 mm) with 5/6 amp modular switch, modular base and cover plate, suitable size G.I. box as per specification and IS: 694 (2010), IS: 9537 (2000 Part 5) Make:- PVC Pipe Polycab/Precision/Saraswati (ISI) Wire- Polycab/Havells/RR Kable (ISI) Switch Socket & accessories- Legrand (Mylinc)/ Havells (Verona) (ISI) | Point | 370 | Three Hundred Seventy Only
3 | 1.9 | Extra for providing and fixing light plug point on board in concealed FRLS PVC conduit (heavy duty, thickness of pipe should be 2 mm) point wiring with modular type 3 pin 5/6 amp socket outlet and 5/6 amp switch including cost of base and cover plate and G. I. box etc. as per specification and IS: 694 (2010), IS: 9537 (2000 Part 5) Make:- PVC Pipe Polycab/Precision/Saraswati (ISI) Wire- Polycab/Havells/RR Kable (ISI) Switch Socket & accessories- Legrand (Myline)/ Havells (Verona) (ISI) | Point | 191 | One Hundred Ninty One Only
4 | 1.10 | Wiring for light plug point with 3x2.5 sq mm FRLS PVC insulated stranded copper conductor wire for phase, neutral and earth in concealed FRLS PVC conduit (heavy duty, thickness of pipe should be 2 mm) along with modular type 6 Amp switch and 3 pin 6 amps socket outlet with modular base and cover plate, suitable size G.I. box, earthing the switch box and socket outlet with same size wire etc. as per specification and IS: 694 (2010), IS: 9537 (2000 Part 5) Make:- PVC Pipe Polycab/Precision/Saraswati (ISI) Wire- Polycab/Havells/RR Kable (ISI) Switch Socket & accessories- Legrand (Mylinc)/ Havells (Verona) (ISI)
| 1.10.2 | Medium Point | Point | 582 | Five Hundred Eighty Two Only
| 1.10.3 | Long Point | Point | 814 | Eight Hundred Fourteen Only
5 | 1.11 | Wiring for power plug point with 3x4 sq mm FRLS PVC insulated stranded copper conductor wire for phase, neutral and earth in concealed FRLS PVC conduit (heavy duty, thickness of pipe should be 2 mm) along with modular type 16 Amp switch and 6 pin 16 amps socket outlet with modular base and cover plate, suitable size G.I. box, earthing the switch box and socket outlet with same size wire etc. as per specification and IS: 694 (2010), IS: 9537 (2000 Part 5) Make:-PVC Polycab/Precision/Saraswati Wire- Polycab/Havells/RR Kable (ISI) Switch Socket & accessories- Legrand (Mylinc)/ Havells (Verona) (ISI)
| 1.11.3 | Long Point | Point | 1191 | One Thousand One Hundred Ninty One Only
| 1.11.4 | Extra Long Point I | Point | 1594 | One Thousand Five Hundred Ninty Four Only
6 | 1.13 | Wiring for circuit/ sub main wiring along with earth wire with the following sizes of FRLS PVC insulated copper conductor, wire in concealed FRLS PVC conduit (heavy duty, thickness of pipe should be 2 mm) as per specification and IS: 694 (2010), IS: 9537 (2000 Part 5) Make:- PVC Pipe- Polycab/Precision/Saraswati (ISI) Wire- Polycab/Havells/RR Kable (ISI)
| 1.13.2 | 3 X 2.5 sq. mm in 20mm conduit | Mtr | 98 | Ninty Eight Only
| 1.13.3 | 6 X 2.5 sq. mm in 25mm conduit | Mtr | 151 | One Hundred Fifty One Only
| 1.13.4 | 9 X 2.5 sq. mm in 32mm conduit | Mtr | 210 | Two Hundred Ten Only
| 1.13.6 | 3 X 4 sq. mm in 25mm conduit | Metre | 128 | One Hundred Twenty Eight Only
| 1.13.7 | 3 X 6 sq. mm in 25mm conduit | Metre | 161 | One Hundred Sixty One Only
| 1.13.13 | 6 X 6 sq. mm in 32mm conduit | Mtr | 275 | Two Hundred Seventy Five Only
7 | 1.15 | Supplying and fixing of following sizes FRLS PVC conduit (heavy duty, thickness of pipe should be 2 mm) along with accessories in concealed complete as per specification and IS: 9537 (2000 Part 5) Make:- PVC Pipe- Polycab/Precision/Saraswati (ISI) Wire- Polycab/Havells/RR Kable (ISI)
| 1.15.2 | 25 mm | Mtr | 46 | Fouty Six Only
8 | 3.13 | Supplying and drawing following grade co-axial TV wire FRLS PVC insulated, shielded with fine tinned copper braid and protected with PVC sheath in the existing surface/ concealed Steel/PVC conduit as per specification and IS: 694 (2010) Make:- Wire- Polycab/Havells/RR Kable (ISI)
| 3.13.1 | RG-6 grade | Mtr | 12 | Twelve Only
9 | 3.11 | Supplying and drawing following sizes of FRLS PVC insulated copper conductor, multi strand wire in the existing surface/ concealed, FRLS PVC conduit / PVC casing caping as per specification and IS: 694 (2010) Make:- Wire- Polycab/Havells/RR Kable (ISI)
| 3.11.1 | 1 x 1.5 sq. mm | Mtr | 13 | Thirteen Only
10 | 4.4 | Supplying and fixing following size/ modules, GI box along with modular base & cover plate for modular switches in recess etc as per specification. Make:- Wire- Legrand/Havells (ISI)
| 4.4.1 | 75mmX75mm (1/2 Module) | Each | 73 | Seventy Three Only
11 | 5.4 | Supplying and fixing following modular switch, socket, other accessories on the existing modular plate & switch box including connections but excluding modular plate etc. as per specification. Make:- Switch Socket & accessories- Legrand (Mylinc)/ Havells (Verona) (ISI)
| 5.4.9 | Fan regulator (two module size) electronic stepped type moving all rounds | Each | 196 | One Hundred Ninty Six Only
| 5.4.16 | T.V. antenna socket outlet | Each | 65 | Sixty Five Only
| 5.4.18 | 25/32 amp A.C. Starter switch | Each | 217 | Two Hundred Seventy Only
12 | 5.7 | Supplying and fixing call bell/ buzzer suitable for single phase, 230 volts A.C. supply, complete as per specification. Make:- Havells/Cona/Polycab/Vinay (ISI)
| 5.7.2 | Deluxe | Each | 95 | Ninty Five Only
13 | 5.9 | Providing and fixing round/ hexagonal fan box (125mm dia) depth 75mm (max.) with 12mm dia steel bar hook, 1.6mm thick MS sheet cover, in RCC slab etc. as per specification. | Each | 37 | Thirty Seven Only
14 | 6.1 | Supplying, installation, testing and commissioning of following sizes ceiling fan including wiring the down rods of standard length up to 30 cm with 1.5 sq. mm FRLS PVC insulated, copper conductor, single core cable, earthing etc. complete as required.P.F. should be greater than 0.9, with BEE Starrating from 1 star and above, IS:374:2019 including all amendments. Make:- Usha/Havells/Crompton/Bajaj/Orient (ISI)
| 6.1.3 | 1200 mm sweep | Each | 1497 | One Thousand Four Hundred Ninty Seven Only
15 | 6.6 | Supplying, installation, testing and commissioning of following sizes heavy duty (continuous running) 1400 rpm exhaust fan in existing opening in wall including earthing etc. complete as per specification. P.F. should be greater than 0.9 Make:- Usha/Havells/Crompton/Bajaj/Orient (ISI)
| 6.6.1 | 300 mm sweep | Each | 2158 | Two Thousand One Hundred Fifty Eight Only
16 | 6.8 | Supplying, installation, testing and commissioning of following sizes fancy exhaust fan having built in louvers in existing opening in wall including earthing etc. complete as per specification. P.F. should be greater than 0.9 Make:- Usha/Havells/Crompton/Bajaj/Orient (ISI)
| 6.8.2 | 300 mm sweep | Each | 1120 | One Thousand One Hundred Twenty Only
17 | 6.12 | Providing and fixing phenolic laminated sheet cover of 180 mm dia 3 mm thick on the fan box etc. as per specification. (If provided at the time of installation of celing fan) | Each | 49 | Fourty Nine Only
18 | 6.17 | Supplying, fixing, testing and commissioning of following LED lamps with inbuilt electronic driver heat sink and all other accessories in existing holder/ luminaries as per specification and P.F. should be greater than 0.9. LED chip efficacy ratio ≥ 100 lumens /watt. Make:- Havells/Wipro/Philips (ISI)
| 6.17.4 | 9 Watt | Each | 126 | One Hundred Twenty Six Only
19 | 6.19 | Supplying, installation, testing and commissioning of following LED tube light fitting including batten with Electronic Driver Heat sink Capacitor complete with all other accessories on surface/infalse ceiling, including connection, earthing etc complete as per specification and furnishing 5 Yrs Warranty certificate from manufacturer. IP20 P.F. should be greater than 0.9 LED chipe fficacy ratio ≥100 lumens/watt. Make:- Havells/Wipro/Philips (ISI)
| 6.19.3 | 18/20 watt {4feet} | Each | 390 | Three Hundred Ninty Only
20 | 6.22 | Supplying, installation, testing and commissioning of following 230/250 volts LED BOLLARD fitting cool white/warm white {Colour Temperature 3000/4000/5600/6000 K} with electronic driver, heat sink, capacitor and all other accessories on existing foundation/ pole bracket, including connection, earthing etc complete as per specification. P.F. should be greater than 0.9. LED chip efficacy ratio ≥ 100 lumens /watt. Make:- Havells/Wipro/Philips (ISI)
| 6.22.1 | 9 watt | Each | 3186 | Three Thousand One Hundred Eighty Six Only
21 | 6.28 | Supplying, installation, testing and commissioning of following 230/250 volts LED street light fitting with all accessories like driver, heat sink made of die cast aluminium with IP 66 protection and 15 KV surge protection on pole bracket, including connection, earthing, Separate housing for driver etc complete as per specification and P.F. should be greater than 0.9. LED chip efficacy ratio ≥ 120 lumens /watt. Make:- Havells/Wipro/Philips (ISI)
| 6.28.6 | 45 watt | Each | 2407 | Two Thousand Four Hundred Seven Only
22 | 7.17 | Providing and making interconnection in cubical panel between BBC and switchgears with following size FRLS PVC insulated copper conductor wire lead of length upto 50cm including providing copper thimbles on both ends as per specification (To be measured separately for each phase/ neutral). Make:- Wire- Polycab/Havells/RR Kable (ISI)
| 7.17.1 | 10 sqmm (32 amp) | Each | 67 | Sexty Seven Only
23 | 7.19 | Fabrication, supply, installation, testing and commissioning of cubicle type compartmentalized wall/ floor mounted power cum control panel board of specified size and following depth made out of not less than 2 mm thick CRCA MS sheet with suitable size compartments for bus bars, switchgears and necessary cutouts for voltmeters, ammeters etc as per specifications including powder coating painting but without busbars, switchgears and other accessories etc complete as per specification. (Only face area is to be measured)
| 7.19.2 | Above 300 mm and upto 450 mm deep | sqm | 6638 | Six Thousand Six Hundred Thirty Eight Only
24 | 7.20 | Supply, installation, testing and commissioning of 4 pole (3 phase + neutral) aluminium bus bars in existing cubicle type compartmentalized wall/ floor mounted panel board along with suitable size and shape insulators, necessary bolts and nuts etc complete as required.
| 7.20.1 | 100 amp (20x5mm) | Mtr. | 633 | Six Hundred Thirty Three Only
| 7.20.2 | 200 amp (30x5mm) | Mtr. | 800 | Eight Hundred Only
25 | 9.1 | Providing and fixing following rating and breaking capacity MCCB in existing cubicle panel board including drilling holes in cubicle panel, making connections, etc. as per specification, IS/ IEC: 60947-2 and Ics = 100 % Icu. Make :- Legrand/ Havells (ISI)
| 9.1.1 | 3 pole MCCB, 25-63A, Fixed Thermal Release, 10KA | Each | 1309 | One Thousand Three Hundred Nine Only
| 9.1.24 | 4 pole MCCB, 100A, Adjustable Thermal - Magnetic Release, 35KA | Each | 5626 | Five Thousand Six Hundred Twenty Six Only
26 | 9.2 | Supplying and fixing on surface/ recess following way, 240 volts SP&N MCB distribution board of sheet steel phosphatized and powder painted complete with tinned copper busbar, neutral busbar, earth bar, din bar, detachable gland plate, including interconnections, earthing etc. as per specification. (But without MCB/RCCB/Isolator) Make :- Legrand/ Havells (ISI)
| 9.2.5 | 4 way, Double door | Each | 692 | Six Hundred Ninty Two Only
27 | 9.4 | Supplying and fixing on surface/ recess horizontal type following way, 415 volts, TPN MCB distribution board of sheet steel phosphatized and powder painted, complete with tinned copper busbar, neutral busbar, earth bar, din bar, detachable gland plate, including interconnections, earthing etc. as per specification. (But without MCB/RCCB/Isolator) Make :- Legrand/ Havells (ISI)
| 9.4.5 | 6 way Double door | Each | 1798 | One Thousand Seven Hundred Ninty Eight Only
28 | 9.11 | Supplying and fixing SP MCB, 240 volts, 'C' curve, suitable for inductive load in the existing MCB DB complete with connections, testing and commissioning etc. as per specification. Make :- Legrand/ Havells (ISI)
| 9.11.2 | 6 amps to 32 amps | Each | 130 | One Hundred Thity Only
29 | 9.12 | Supplying and fixing DP MCB, 240 volts, 'C' curve, suitable for lighting and other loads in the existing MCB DB complete with connections, testing and commissioning etc. as per specification. Make :- Legrand/ Havells (ISI)
| 9.12.3 | 40 amps | Each | 569 | Five Hundred Sixty Nine Only
| 9.12.5 | 63 amps | Each | 567 | Five Hundred Sixty Seven Only
30 | 9.16 | Supplying and fixing TP&N MCB, 440 volts, 'C' curve, suitable for lighting and other loads in the existing MCB DB complete with connections, testing and commissioning etc. as per specification. Make :- Legrand/ Havells (ISI)
| 9.16.5 | 63 amps | Each | 1161 | One Thousand One Hundred Sixty One
31 | 10.15 | Providing and fixing following rating current transformer in existing cubical panel including, connections, testing and commissioning etc. as per specification.
| 10.15.2 | 100/5 amps | Each | 308 | Three Hundred Eight Only
32 | 10.17 | Providing and fixing penal mounting 230 volt LED type indicating lamp in existing cubical panel including, connections, testing and commissioning etc. as per specification. | Each | 83 | Eighty Three Only
33 | 10.18 | Providing and fixing penal mounting following rating digital type ammeter of size 100x100 (NS) in existing cubical panel including, connections, testing and commissioning etc. as per specification.
| 10.18.2 | 0-100 amps | Each | 328 | Three Hundred Twenty Eight Only
34 | 10.20 | Providing and fixing penal mounting 0-500 volt voltmeter of size 100x100 (NS) in existing cubical panel including, connections, testing and commissioning etc. as per specification.
| 10.20.2 | Digital type | Each | 736 | Seven Hundred Thirty Six Only
35 | 10.21 | Providing and fixing penal mounting selector switch in existing cubical panel including, connections, testing and commissioning etc. as per specification.
| 10.21.1 | For voltmeter | Each | 167 | One Hundred Sixty Seven Only
| 10.21.2 | For ammeter | Each | 183 | One Hundred Eighty Three Only
36 | 12.13 | Supplying and laying 25 mm X 6 mm G.I. strip at 0.50 metre below ground as strip earth electrode, including soldering, excavation and refilling the trench etc. as per specification. | Metre | 83 | Eight Hundred Three Only
37 | 12.19 | Providing maintenance free earthing with following size GI pipe including making bore pit of minimum 150mm dia, providing and laying approved make Earthing Electrode of Pipe-in-Pipe technology as per IS 3043(R 2016) -1987 made of corrosion free G.I. Pipes having outer pipe of 80mm dia and inner pipe of 50mm dia and filling with specified qty highly conductive compound around pipe and above that with soft soil in bore pit complete and providing masonry enclosure with cover plate having locking arrangement and watering pipe etc. as per specification:
| 12.19.2 | With 2 metre long GI Pipes and 25 kg back filling compound. | Each | 7253 | Seven Thousand Two Hundred Fifty Three Only
38 | 14.2 | Supplying and laying HDPE pipe of 4kg/cum in ground below road, path etc at a depth not less than 40 cm and upto 90 cm including excavation, dismantling of road if required and refilling the trench with excavated material, ramming and making the surface good etc. as per specification. Make :- Finolex/Supreme/Kissan (ISI)
| 14.2.3 | 90 mm outer dia | Metre | 216 | Two Hundred Sixteen Only
39 | 15.3 | Supplying and laying following sizes one number FRLS PVC insulated, PVC sheathed, steel armoured, aluminium conductor power cable of 1.1 KV grade in existing RCC/HUME/ STONEWARE/ METAL/HDPE pipe as perspecification, IS:9537 (2000,Part5) Make:- Polycab/Havells/KEI (ISI)
| 15.3.11 | 3.5 x 25 sq. mm. | Metre | 103 | One Hundred Three Only
| 15.3.12 | 3.5 x 35 sq. mm. | Metre | 118 | One Hundred Eighteen Only
40 | 15.23 | Supplying and making end termination with brass compression gland and aluminum lugs forfollowing size armoured aluminum conductor power cable of 1.1 KV grade as per specification..
| 15.23.12 | 3½ X 25 sq. mm (25 mm) | Each | 92 | Ninty Two Only
| 15.23.13 | 3½ X 35 sq. mm (28 mm) | Each | 135 | One Hundred Thirty Five Only
41 | 20.6 | Supplying and erection of angle/channel iron cross arms/ bracket/ other fitting of approved size and shape including drilling of holes for insulator pins, bolts and nuts etc as per specification. | kg | 68 | Sixty Eight Only
42 | 26.17 | Supply and erecting following ISI marked Fire extenguishers on wall/ column including erecting bracket etc complete.
| 26.17.5 | CO2 type Fire Extinguisher ISI marked confirming to IS:15683:2018 Capacity 4.5Kg. INITIAL CHARGE:- Carbon dioxide used in extinguishers shall comply with IS 15222. FIRE RATING:- 55B. Complete with Hose Assembly and horn , locking arrangement, operation manual, bracket with two screw and sleeve | Each | 7253 | Seven Thousand Two Hundred Fifty Three Only
Assistant Engineer (Elect)
CG Housing & Infra.Dev.Board
Electrical Sub-Div., Jagdalpur
Executive Engineer (Elect)
CG Housing & Infra.Dev.Board
Electrical Div- Jagdalpur
Sub Engineer (Elect)
CG Housing & Infra.Dev.Board
Electrical Sub-Div., Jagdalpur