SCOPE OF WORKS

Name of Work -	Operation & maintenance (O & M) of water treatment plant clear water pumping station, raw water pumping station including raw and clear water electric substation of 80 MLD & 150 MLD i/c all the ancillary components & premises for Raipur City water supply System.

Location of Works	-

- Raw water pumping station & raw water electric substation – It is located on the bank of Kharoon river near village Bhatagaon 3.5 km away from Raipur City.

- Water treatment plant, clear water pumping station & clear water electric substation –

These are located at Rawanbhata along ring road no.1 are at distance of 5 km from Raipur City.

Scope & specification of works under the contract –

- The work under the contract consists of –

Operation & maintenance of following works –

- Raw water pumping station & raw water electric substation.

- Clear water pumping station & clear water substation.

- Water treatment plant at Rawanbhata 80 MLD & 150 MLD

- All O&M works shall be carried out as per –

- Government (state & central ) laws & rules such as indian electricity act 1948, factory act 1948, contract & labor (regulation & abolition) act 1972, compensation act, provident fund act etc and rules framed under the said acts by the competent authority with all up to date amendments.

- Laws and rules prevailing during contract and pertaining to the scope of contract.

- Time to time directions, instructions & entire satisfaction of Executive engineer/engineer In charge of Raipur municipal corporation .

- All plant, machinery & equipments shall be maintained & operated by the contractor.

- The electrical energy for O & M of pumps at raw water & clear water pump houses and all electrical & mechanical equipments at water treatment plants shall be made available at respective locations by Executive engineer/engineer- in-charge of Raipur Municipal Corporation. at no cost. However diesel, petrol, kerosenc etc. required for any dewatering operation at these locations during O&M will have to be arranged by contractor at his own cost only.

- All chemicals viz-alum, liquefied chlorine, bleaching powder and coagulant aides for O&M of water treatment plant shall be arranged by the Executive engineer/ engineer-in-charge of Raipur municipal corporation.

- Raw water up to Bhatagaon anicut shall be made available by Executive engineer/ engineer-in-charge of Raipur Municipal Corporation.

- All materials required for smooth running of mechanical part and leak proofness of valves as well as electrical maintenance etc. gland packing, rubber & metallic washers. All electrical/mechanical items etc shall be arranged by contractor at his cost only.

- All routine maintenance & operational works i/c all minor & major repair will have  to be carried out by contractors only.

- All breakdown or essential repairs must be carried out immediately so that water supply does not get affected. In case contactor fails to take repair rectification work in time, the Executive engineer/engineer-in-charge of Raipur Municipal Corporation can deploy other agency for such job and expenditure incurred on such job will be recovered from contractor’s bill and penalty will be imposed.

- Minor civil/mechanical/electrical engineering repair works replacement of materials (Providing materials & spares) will be on contactor’s account however the cost of major repair works which is not included in contract will be paid by the Executive engineer/engineer-in-charge of Raipur Municipal Corporation after prior approval of Executive engineer-in-charge/ commissioner.

- All measuring devices in pump houses & WTP must be kept in working order duly calibrated as per relevant standards by the contractor with his own expences.

- In case of power breakdown for insufficient supply of raw water immediate intimation must be given to Executive engineer/engineer-in-charge of Raipur municipal corporation. through telephone or in writing and necessary entries must be made in the relevant log books.

- Format of logbooks shall be printed by contractor & after approval of the bulk quantities shall got printed by the contractor attached for hourly record of  year use by this own cost. Hourly record of running of pumps, & WTP with respect to quantity of water as well as electrical & flow parameters must be maintained in  separate for each pumps log books.

- Contractor has to keep the substation premises clean and free from shrub, roots, plants if any & he has to maintain the earth pits in proper working condition.

- Contractor shall maintain the W.T.P. & pumping machinery in good operational condition, round the clock, specifically it should be checked that foundation & ‘v’ notches & launders of clarifier, free from algae and filter bed should not have any mud ball. Back washing should be taken as soon as a head loss of 1.8 mts. is attained or once in 24 hours whichever come first. Alum solution tank & alum solution pipe line should be maintained clean and its & mixing machine should be in operating condition. Alum solution dosing pipe line must be flushed thoroughly after every use.

- Contractor should hold sufficient stock of spares and required material by submitting demand to Executive engineer/engineer-in-Charge of Raipur Municipal Corporation in advance. If contractor fails to build up the stock of the spares and material and put the requirement just at the time of repair works/ maintenance work and if any loss occur to RMC by due to non availability of spares and material in time, then same will be recovered from contractors payment due and if there is any loss of pumping hour then penalty will be imposed.

- Each and every filter bed should be chemically treated and back wash thoroughly with solution of sodium hydroxide (NaOH) of 1% strength, to maintain the media in good condition. This chemical treatment should be given as and when required or once in 6 months.

- The dose of chemical for coagulation & disinfections should be fixed on actual laboratory test to be carried out at regular intervals as prescribed in CPHEEO manual.

- The physical, chemical & bacteriological quality of settled water, filtered water at filter beds & clear water sump must be maintained as per CPHEEO norms.

- Contractor is responsible for supplied of quality water as per norms of CPHEEO manual. In case of less supply due to contractors negligence a penalty of Rs. 5000/- per MLD shall be imposed and shall be deducted from running bill. Similarly in case the quality of water gets affected with respect to bacteriological standards a penalty @ Rs. 50,000/- per day for number of days of default shall be imposed. In case physical & chemical standards are affected a penalty @ Rs. 5000/- per hour shall be imposed.

- Day to day record of all consumables must be maintained and must be produced for verification as and when demanded by the Executive engineer/ engineer-in-Charge of Raipur Municipal Corporation. or Any inspection authority assigned by Executive engineer/engineer-in-Charge of Raipur Municipal Corporation.

- Disinfection of water shall be done by chlorinators as per required dosing at Clear water sump , so that the residual chlorine shall be maintained as directed by Executive engineer/engineer-in-Charge of Raipur Municipal Corporation at 0.20 ppm to 0.50 ppm at consumer end. If filled toners are not available, then bleaching powder /sodium hypochlorite solution shall be used for disinfection

Special conditions of contract

- Maintenance work and if any loss occur to Nagar Nigam Raipur then same will be recovered from contactors payment due and if there is any loss of pumping hour then penalty will imposed as per clause.

- All machinery & equipment at pump houses & WTP must be in working conditions all the time. In case any equipment requires repair or replacement then it must be done maximum within 72 hours in case of failure penalty may be imposed as deem fit by the Executive engineer/engineer-in-Charge of Raipur Municipal Corporation.

- Chemicals required for laboratory testing and preparation of standard solution will be made available by Executive engineer/engineer-in-charge of Raipur Municipal Corporation.

- If contractor fails to attend machine. instruments, equipments in time and fails to put the same in working order within stipulated time as decided by the Executive engineer/engineer-in-charge of Raipur Municipal Corporation reserve the right to bring the same in working order by deputing another agency at the risk and cost of the contractor and same will be recovered from monthly bills of the contractor. A penalty will also be imposed as dim fit by the Executive engineer/engineer-in-charge of Raipur Municipal Corporation.

- It will be contractors responsibility to provide all safety articles to the working staff like, hand gloves, long boots, safety caps, head masks, proper electrical safety mates, torch all safety articles helmets against chlorine hazard dress code & proper  approved dress with identity card, otherwise Rs. 100/- penalty will be imposed per day per worker.

- All the charges regarding operation and maintenance of the scheme shall be borne by the contractor except energy charges and raw water charges.

- If Executive engineer/engineer-in-charge of Raipur Municipal Corporation  fixes time limit for any repairs/work then contractor will have to complete the work within the fixed time at any cost by deputing staff round the clock. If contractor fails to complete that job within the fixed time, penalty @ Rs. 500/- per hour for delay in time limit will be imposed. In this respect the decision of the Executive engineer/ engineer-in-charge of Raipur Municipal Corporation. Representative will be final and binding on the contractor.

- The operational technical, skilled, semiskilled, unskilled staff for running & maintenance of raw & clear water pumps, water treatment plant, electric       substations in required number has to be deployed as mentions in tender documents bidder on prescribed in CPHEEO manual on water supply & treatment manual of Govt. India, ministry of urban development for all the three shifts of 8 hour duration will have to be deployed by the contractor & preference shall be given to deploy local labours.

- In case of accidental death/injury, causing danger to health/ loss of any kind of property and life due to negligence/lapse in the filtration plant. The sole responsibility and liability will be fixed against the contractor. He will be liable to any kind of proceeding investigation damage claim occurred inside the filtration plant and in the city due to any fault in part of contractor in the filtration plant. All the wash rooms/toilets tape sinks/septic tanks contractor has to keep clean & hygienic as per best engineering practices. Contractor has to maintain clean dry & hygienic conditions in all units alum tank/lime flash mixing tank, all corridors, up stairs, washing area launder, offices, labs,  walkways, area around autoclariflocculator, filter house, clear water channels, compartments, stores chlorine rooms, pump house, control rooms.

- Workers to be engaged on the work under contract should posses technical qualification and experience as per schedule of quantity .

- All the workers engaged on the work shall be the employees of the contractor & contractor shall be completely responsible for their regular payment as per minimum wages act PF, ESIC. Insurance & their safety. appointment/dismissal and condition of their services & other liabilities regarding workers engaged under the contract shall also be the sole responsibility of the contractor.

- The Executive engineer/engineer-in-charge of Raipur Municipal Corporation reserves the right to ask the contractor to discontinue any worker/ labour for misbehavior/misconduct or negligence on duty. In any case the worker should not be found in intoxicated condition. They should be medically fit and the contractor shall submit a medical fitness certificate issue from the competent authority before engaging any worker.

- Executive engineer/engineer-in-charge of Raipur Municipal Corporation representative shall have authority to ask the contractor to change any employee who is found physically/technically unfit for the job and these instructions shall be followed by the contractor.

- Contractor shall maintain the record of attendance, wages paid to employees and PF subscription. The record shall be open for verification of Executive engineer/engineer-in-charge of Raipur Municipal Corporation as well as the authorities from Govt. Organizations..

- Cleaning of all units of WTP for all sorts of depositions viz-silt, algae, floting materials etc. shall be done by the contractor regularly in cascade aerators, launders, channels, flash mixers, autoclariflocculators outside channels by using long handled net catchers, long handle’s scrappers regularly in all shifts.

- Contractor should extend full co-operation to electrical safety inspector Dy Director Factories and any other Statutory Authority visiting the plant as per rules. Contractor shall have to comply the suggestions and direction covered under the respective act and rule. Contractor will have to arrange necessary to and fro conveyance to them for their inspection of plants. He will responsible to get necessary clearances from electrical safety dept. and Deputy Director, factories to run the plant.

- Contractor will maintain cleanliness ventilation and lighting in the plant & its premises in all three shifts i/c provision of torch lights 04 nos. in each locations. This include sweeping removing of cobwebs, dust etc. from plant machines and premises. All the materials required for maintaining cleanliness will be on contractor’s account.

- Contractor has to clean the steps of aerator at the time of shut downs of intake well or as and when required to keep the aerator clean and algae free.

- Contractor has to maintain all the valves chambers in working & operating conditions by doing all maintenance works for chambers/chamber cover & has to keep then clean & dry free of algae & all foreign materials so as to access easily for maintenance.

- Contractor has to maintain the wash water tank in good working conditions i/c water level indicator and main hole cover, cowl  air vent caps inlets & outlets pipes are to be maintained properly any seepage in wash water tank if  occur it should be repaired immediately.

- All equipments, machineries, flow meters, flow controlling device, LOH, ROF, meters, chlorinators shall be in perfectly working condition. The leakage in should not be observed. There should be no leakage in pipe gallery.

- In event of any major breakdown the work should be attended by the contractor after consent/concurrence from Executive engineer/engineer-in- charge of Raipur Municipal Corporation, the detailed approved rates by the Municipal Corporation Raipur will be the basis of such repair works and payment. These works can also be done by the corporation after receiving the report by the O & M agency if required.

- The plant manager will monitor the activity and based on raw water quality, through a skilled chemist the dosing will be decided based on the obtained water quality parameters. The consumption pattern to keep the water quality parameter in limits till the battery limit will be strictly monitored by the contractor through a deployed chemist, day to day report of pure water parameters will be intimated to RMC and uploaded on website. The special coating and painting of the mechanical structure should be in the scope of the contractor once in a year. This covers clari flocculator, agitator, bridge, motor, flash mixer etc should be in scope of the contractor. The repair on the same for clearing the bending, truing, welding of the parts cracked and the necessary spare replacement should be in the scope of the contractor.

- When there is breakdown in water supply or operation of machinery due to negligence or fault of contractor, the Executive engineer/engineer-in-charge of Raipur Municipal Corporation. Representative shall assess the extent of loss. The contractor shall have to restore the loss without disturbing water supply schedule and the loss will have to be borne by the contractor

- Entire components right from intake well, pumping stations and WTPs shall be maintained as per CPHEEO norms and as per the guidelines mentioned in the CPHEEO manual of operation and maintenance published by MoUD in 2005. If the maintenance is not found in the parameters of CPHEEO, RMC will take action against the contractor as per the conditions of  the contract.

- Contractor shall be responsible for supply of quality drinking water to the consumer, it shall be chlorinated as per CPHEEO norms. If any instance it is not found and problem occurs due to the supply of impure water to the consumer. Then the responsibility lies with contractor and RMC can take judicial action against the contractor.

- Contractor shall maintain instruction book at intake well & WTP premises to receive the instruction/orders from the department. The instruction/orders given in the register should be complied immediately.

- The contractor has to maintain the water supply system in accordance with the agreement and will hand over to RMC in good and working condition on completion of the term.

Executive Engineer

Filter plant

Municipal corporation (Raipur)