SCOPE OF WORK FOR BI-ANNUAL RATE CONTRACT FOR REWINDING WORKS OF BURNT OUT MOTORS AT NANDINI HITECH MEGA POWDER PLANT, RAMANAGARA

- LOCATION

The Rewinding work of burnt motors is required to be carried out at Nandini Hitech Mega Powder plant, a unit of Karnataka co-operative Milk Producers Federation Limited, Ramanagara District, well connected by Road & Train.

- BRIEF OBJECT.

The object is providing Bi-Annual Rate Contract For Rewinding Works of Burnt out Motors of the said plant to ensure smooth functioning of the plant by carrying out rewinding works in accordance with motor manufacturers by following best engineering practices within battery limits.

- SCOPE OF THE CONTRACT AND TERMS AND CONDITIONS

  - Material to be used and process of Rewinding/Servicing:

The following to be adhered to while carrying out the rewinding of burnt motors.

- Materials used for rewinding shall be of superior quality. The workmanship &materials shall be as per IER.

- Winding (after varnishing) shall be baked in heating oven.

- Testing of winding in stages should be carried out.

- Test certificate with test results shall be furnished at the time of delivering the motor without fail.

- Copper wire made of "Indo American" Atlas super enameled copper wire of polyester base as per I.S. 4080 part - 5 to be used.

- Varnish Dr. Breaks grade Elmotherm - 50 HP to be used.

- Fiber glass sleeve of class F insulation to be used.

- Insulation paper - Hypertherm paper of class F insulation to be used.

- End connection cable - Fiberglass sleeves to be used with necessary lugs crimped/soldered.

- Contractor should furnish motor test certificate, DC and bill at time of delivering the motor.

- After rewinding Motor should be painted.

  - RATES FOR REWINDING OF MOTORS:

The rate should be quoted taking into consideration that the old copper coils released from the motors shall be retained by the Contractor.

  - On any other account increase / decrease in rate will not be allowed during the contract period

  - Burnt Motors shall be collected by the contractor under acknowledgement from KMF-CATTLE FEED PLANT RAJANUKUNTE, BANGALORE. And the transportation to the contractor workshop & delivering back to KMF-CATTLE FEED PLANT RAJANUKUNTE, BANGALORE after rewinding has to be done by the contractor.

  - CUSTODY OF MOTORS:

On taking delivery of motors from KMF-CATTLE FEED PLANT RAJANUKUNTE, BANGALORE DIST. the contractor have to keep the motors under safe custody and will be held responsible for the loss of motors if any and the value of the same will be recovered from the contractor.

  - AGREEMENT:

An Agreement shall be executed as per our format for proper and prompt performance of the contract.

  - PERIOD OF CONTRACT:

The contract would be in force for a period of TWO years. The contract can be extended for future period of three months if required. However the KMF reserves the right to terminate the contract during the currency period by giving a notice in writing.

  - The tenderer would be subject to termination with three month’s notice in the case services are not satisfactory.

  - During the transportation of material if material is damaged/defaced/faded etc., the contractor will be the responsible.

  - The tenderer shall procure / review all licence / certificate from the respective authorities as per the prevailing acts and in case of default the contractor shall be responsible for the consequence.

  - TRANSPORTATION:

It is the responsibility of the tenderer to collect the burnt motor from KMF-Nandini Hitech Mega Powder Plant, Ramanagara and to return the same after rewinding. If rewinded motors are not returned back within the stipulated time Penalty will be imposed.

  - GUARANTEE:

The rewinded motors shall be guaranteed at least for a period of 6 months. If the motors are burnt out within the guarantee period such motors shall have to rewinded by the contractor at free of cost.

  - WOKSHOP:

Tenderer workshop should be in or around Channapattana- Ramanagara city and within a span of 100kms only.

  - SPARE PARTS:

If Motor spare parts like Bearing, Motor Fan, Terminal Connector, Oil Seal, Motor End Cover Machine Work or Providing Additional Bush, Rotor Repair work, Stator Repair work, etc., have to be replaced it should be informed before replacing and should get approval from KMF-cattle feed plant NHMPP, Ramanagara

  - PAYMENT:

The payment shall be made within 15 days on certification for the quality rewinding by the Electrical Section head. The payment to the supplier shall be by A/C payee Cheque/ NEFT/RTGS. The cheques shall be forwarded by Speed Post/Courier services.

  - JURISDICTION:

For settlement of any dispute arising out of this contract, it   shall be subject to the jurisdiction of the COURTS in Bangalore City.

- BILL OF QUANTITIES:

| KMF-NHMPP-RAMANAGARA |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| DETAILS OF ELECTRICAL MOTORS FOR RE-WINDING |  |  |  |  |  |
| SINGLE PHASE ELECTRICAL MOTOR & FANS DETAILS |  |  |  |  |  |
| Sl.No. | PHASE | HP | KW | RPM | QTY |
| 1 | 1 | 0.25 | - | 900-1500 | 5 |
| 2 | 1 | 0.5 | - | 900-1500 | 5 |
| 3 | 1 | 0.75 | - | 900-1500 | 3 |
| 4 | 1 | 1 | - | 900-1500 | 3 |
| 5 | 1 | - | 65 W | 900-1500 | 70 |
| 6 | 1 | - | 150-370 W | 900-1500 | 50 |
| 7 | 1 | - | 2.00 | 900-1500 | 1 |
| THREE PHASE ELECTRICAL INDUCTION MOTORS DETAILS |  |  |  |  |  |
| Sl.No. | PHASE | HP | KW | RPM | QTY |
| 8 | 3 | 0.25 | - | 1400-1500 | 6 |
| 9 | 3 | 0.5 | 0.40 | 219-800 | 2 |
| 10 | 3 | 0.5 | 0.40 | 960-1000 | 2 |
| 11 | 3 | 0.5 | 0.40 | 1440-1500 | 7 |
| 12 | 3 | 0.5 | 0.40 | 2880-3000 | 2 |
| 13 | 3 | 0.75 | 0.60 | 219-800 | 1 |
| 14 | 3 | 0.75 | 0.60 | 960-1000 | 1 |
| 15 | 3 | 0.75 | 0.60 | 1440-1500 | 1 |
| 16 | 3 | 0.75 | 0.60 | 2880-3000 | 1 |
| 17 | 3 | 1 | 0.74 | 219-800 | 4 |
| 18 | 3 | 1 | 0.74 | 960-1000 | 4 |
| 19 | 3 | 1 | 0.74 | 1440-1500 | 5 |
| 20 | 3 | 1 | 0.74 | 2880-3000 | 21 |
| 21 | 3 | 1.5 | 1.20 | 219-800 | 1 |
| 22 | 3 | 1.5 | 1.20 | 960-1000 | 1 |
| 23 | 3 | 1.5 | 1.20 | 1440-1500 | 15 |
| 24 | 3 | 1.5 | 1.20 | 2880-3000 | 7 |
| 25 | 3 | 2 | 1.50 | 219-800 | 1 |
| 26 | 3 | 2 | 1.50 | 960-1000 | 2 |
| 27 | 3 | 2 | 1.50 | 1440-1500 | 16 |
| 28 | 3 | 2 | 1.50 | 2880-3000 | 6 |
| 29 | 3 | 4 | 3.00 | 1440-1500 | 12 |
| 30 | 3 | 5 | 3.73 | 2880-3000 | 5 |
| 31 | 3 | 4 | 2.98 | 219-800 | 1 |
| 32 | 3 | 4 | 2.98 | 960-1000 | 1 |
| Sl.No. | PHASE | HP | KW | RPM | QTY |
| 33 | 3 | 4 | 2.98 | 1440-1500 | 2 |
| 34 | 3 | 4 | 2.98 | 2880-3000 | 2 |
| 35 | 3 | 5 | 3.73 | 1440-1500 | 4 |
| 36 | 3 | 5 | 3.73 | 2880-3000 | 18 |
| 37 | 3 | 5.5 | 4.10 | 219-800 | 1 |
| 38 | 3 | 5.5 | 4.10 | 960-1000 | 1 |
| 39 | 3 | 5.5 | 4.10 | 1440-1500 | 1 |
| 40 | 3 | 5.5 | 4.10 | 2880-3000 | 1 |
| 41 | 3 | 6 | 4.48 | 219-800 | 1 |
| 42 | 3 | 6 | 4.48 | 960-1000 | 1 |
| 43 | 3 | 6 | 4.48 | 1440-1500 | 1 |
| 44 | 3 | 6 | 4.48 | 2880-3000 | 3 |
| 45 | 3 | 7 | 5.22 | 960-1000 | 8 |
| 46 | 3 | 7 | 5.22 | 1440-1500 | 8 |
| 47 | 3 | 7 | 5.22 | 2880-3000 | 10 |
| 48 | 3 | 7.5 | 5.60 | 219-800 | 1 |
| 49 | 3 | 7.5 | 5.60 | 960-1000 | 1 |
| 50 | 3 | 7.5 | 5.60 | 1440-1500 | 13 |
| 51 | 3 | 7.5 | 5.60 | 2880-3000 | 11 |
| 52 | 3 | 10 | 7.46 | 219-800 | 2 |
| 53 | 3 | 10 | 7.46 | 960-1000 | 1 |
| 54 | 3 | 10 | 7.46 | 1440-1500 | 8 |
| 55 | 3 | 10 | 7.46 | 2880-3000 | 10 |
| 56 | 3 | 12 | 8.95 | 1440-1500 | 3 |
| 57 | 3 | 12 | 8.95 | 2880-3000 | 3 |
| 58 | 3 | 12.5 | 9.33 | 1440-1500 | 4 |
| 59 | 3 | 12.5 | 9.33 | 2880-3000 | 1 |
| 60 | 3 | 15 | 11.19 | 1440-1500 | 1 |
| 61 | 3 | 15 | 11.19 | 2880-3000 | 7 |
| 62 | 3 | 20 | 14.92 | 960-1000 | 1 |
| 63 | 3 | 20 | 14.92 | 1440-1500 | 2 |
| 64 | 3 | 20 | 14.92 | 2880-3000 | 12 |
| 65 | 3 | 25 | 18.65 | 219-800 | 1 |
| 66 | 3 | 25 | 18.65 | 960-1000 | 1 |
| 67 | 3 | 25 | 18.65 | 1440-1500 | 3 |
| Sl.No. | PHASE | HP | KW | RPM | QTY |
| 68 | 3 | 25 | 18.65 | 2880-3000 | 6 |
| 69 | 3 | 29.49 | 22.00 | 960-1000 | 2 |
| 70 | 3 | 29.49 | 22.00 | 1440-1500 | 1 |
| 71 | 3 | 30 | 22.38 | 2880-3000 | 8 |
| 72 | 3 | 30 | 22.38 | 1440-1500 | 1 |
| 73 | 3 | 30 | 22.38 | 2880-3000 | 1 |
| 74 | 3 | 40 | 29.84 | 1440-1500 | 2 |
| 75 | 3 | 40 | 29.84 | 2880-3000 | 2 |
| 76 | 3 | 55 | 41.03 | 1440-1500 | 1 |
| 77 | 3 | 60 | 44.76 | 1440-1500 | 6 |
| 78 | 3 | 60 | 44.76 | 2880-3000 | 3 |
| 79 | 3 | 100.54 | 75.00 | 1440-1500 | 1 |
| 80 | 3 | 100.54 | 75.00 | 2880-3000 | 2 |
| 81 | 3 | 120 | 89.52 | 1440-1500 | 2 |
| 82 | 3 | 147.45 | 110.00 | 1440-1500 | 1 |
| 83 | 3 | 176.94 | 132.00 | 1440-1500 | 1 |
| 84 | 3 | 180 | 134.28 | 2880-3000 | 3 |
| 85 | 3 | 214.48 | 160.00 | 1440-1500 | 1 |
| 86 | 3 | 422.25 | 315.00 | 960-1000 | 1 |
| 87 | 3 | 475.87 | 355.00 | 2880-3000 | 3 |
| 88 | 3 | 536.19 | 400.00 | 2880-3000 | 2 |
| THREE PHASE ELECTRICAL SUBMERSIBLE MOTORS DETAILS |  |  |  |  |  |
| Sl.No. | PHASE | HP | KW | RPM | QTY |
| 89 | 3 | 5.36 | 4.00 | 2880-3000 | 4 |
| 90 | 3 | 10 | 7.46 | 2880-3000 | 12 |
| 91 | 3 | 15 | 11.19 | 2880-3000 | 2 |
| THREE PHASE ELECTRICAL BORE-WELL MOTORS DETAILS |  |  |  |  |  |
| Sl.No. | PHASE | HP | KW | RPM | QTY |
| 92 | 3 | 10 | 7.46 | 2880-3000 | 4 |
| 93 | 3 | 30 | 22.38 | 2880-3000 | 2 |
| SERVICE CHARGES FOR DAM MOTOR & PUMP LIFTING & INSTALLATION 30HP- 5 STAGE |  |  |  |  |  |
| Sl.No. | PHASE | HP | KW | RPM | QTY |
| 94 | 3 | 30 | 22.38 | 2880-3000 | 1 |

****