8.0    COUPLING DEVICES:

8.1    Coupling device shall be interposed between the CVT and the coaxial cable from the carrier cabinets.

8.2 The coupling devices in conjunction with the CVT and shall

a) Ensure efficient transfusion of carrier frequency signals between the communication equipment and the power line.

b) Safety to operating personnel by insulating the low voltage telecommunication equipment from the effects of power frequency normal and transient voltage.

c) Form an electric signal filter of the band pass (50 to 500 kHz) type.

d) Match the characteristic impedance of the O.H line with that of the H.F coaxial cable.

e) Provide galvanic isolation between the primary and the secondary terminals of the coupling device.

f) To drain power & frequency current discharge from CC/CVT to earth through an inductance drainage coil of suitable rating.

g) To limit the transfer voltage surges appearing across the power line by a suitable non- linear resistor. The protective device shall be a composite unit consisting of the line matching unit drainage coil and lightening arresters.

a) Line Matching Unit (LMU and/or LMDU):

I) It shall consists of an impedance transformer to match the impedance of the coaxial cable and that of the of the high voltage power line. The units shall be tuned to the bandwidth of the carrier frequency range namely 50 to 500 kHz.

II) The LMU shall be used for phase to ground coupling. However, for phase to phase coupling or inter-circuit coupling a combination of the line matching unit & line matching distribution unit shall be used.

III) The LMU shall be housed in a steel casing or in fiber casing with the various components mounted on insulated plate and fixed inside, The LMU shall be suitable for outdoors mounting on the structure of the CVT itself

IV) The technical requirements shall be as follows

i) Attenuation in pass band.  Less than                                                2dB

ii) Return loss for whole of the pass band Greater than                       12 dB

iii) Standard pass band for mm                                                            50 - 500 kHz. capacitance of CC/C VT of 8000pF

iv) Normal peak envelope power for                                                   1000 Watts intermodulation product of 80 dB

b) Drainage coil:

The drainage coil shall be suitably Insulated for outdoor use. The core of the coil shall be made of powdered iron to increase the inductance of the drainage coil. This high impedance shall prevent the high frequency carrier signals from flowing into the earth. Drainage coil shall lead the capacitive displacement current to earth so as to prevent the accumulation of charge on the low voltage side of the coupling capacitor.

c) Lightning Arresters.

It shall have a discharge gap with a resistor connected in series. The resistance of this resistor shall be an inverse function of the current. Lightning arresters shall lead the high voltage transient impulse to earth that may appear across LMU / LMDU unit.

8.4 Grounding Switch

This shall be a single throw, of a manually operated or through a hickory rod insulated knife switch. The live terminal of which shall be insulated from the structure by an insulator of 33 kV voltage class. Grounding switch shall provide grounding facility on the LT side, in order to protect operating personnel during maintenance work on the LMU and other protective devices.

8.5 MOUNTING:

All the elements as foresaid shall be suitable for outdoor mounting on the structure of the CVT itself

Grounding switch shall be separate and shall not be housed on the casing of the composite unit.

8.6 Technical Requirements:

a) Drainage coil  Inductance                                38 mH at 50 Hz (suggested value) Rated current                                                        5 Amps

Maximum current                                                50 Amps for 1 min duration.

b) Lightning Arresters:

Rated Voltage                                                       1000 volts

Minimum power frequency spark over voltage    1100 volts

c) Grounding Switch

Rated voltage                                                         3,300 volts

Ratedcurrent  200Amps