1.0 BATERRY CHARGER

1.1 GENERAL

1. The charger shall be natural air-cooled thyristor  / IGBT  controlled type.

2.The   charger   shall   be   self  protective   against   all   AC   and   DC   voltage   transient   and steady/abnormal currents and voltages.

3.The charger must of soft start type and shall not exceed the set voltage even at start

4. They shall be capable of operating in Manual and Auto mode.

5. They shall be capable of operating in Float and Boost mode.

6. The charger shall resume feeding DC loads automatically immediately after AC supply is resumed following an interruption.

7. Normally each station will be provided with two numbers of chargers and two numbers of battery sets feeding two independent loads. In case of emergency, a single charger will have to charge two sets of battery and the entire load.

1.2 Construction

1.The charger shall be free standing, independent floor mounted sheet steel type.

2. The panels shall have a high degree of protection and the minimum thickness of sheet steel used shall be 2 mm.

3. The DC distribution boards shall be a separate panel and situated in between  the two independent charger panels..

4. Each charger and DCDB shall have independent access door with concealed hinges and neoprene gaskets. Ventilating louvers shall be covered with the fine wire mesh. Doors over 600mm width shall be of double leaf design.

5. All equipment within the panels shall be arranged in modular unit and laid out with sufficient space for easy maintenance.

The DC distribution board shall be built within the charger and shall have 10numbers of feeders with 10amps capacity with fuse protection and indication. Also have main load switch with fuse protection.

1.3 Wiring/Cabling

1. All interconnecting cables shall be of adequate rating and of multi-strand copper. The busbars provided shall also be of copper. The rating and size of a cables used shall be shown in the drawings to be submitted for approval.

2- The ends of all cables, control wires secured by means of clamps etc, shall be fitted with copper lugs of adequate rating and shall be soldered or clamped effectively to the conductor to ensure that the temperature rise at the joints do not exceed that of the conductor.

3. All wiring shall be routed through wiring troughs, wires shall be ferruled at both ends for identification.

4. Panels shall have removable gland plates at the bottom for cable entry. All incoming and outgoing cable shall be terminated to suitable terminal blocks.

5. All terminals shall be clearly indicated with polarity indications. The terminal blocks shall be separate for AC supply, DC supply and control.

6. Wiring shall follow color code scheme described below. Color of the core        Circuit where used

*Red                                 D.C  + ve

* Black                             D.C    - ve

* Grey22 | P a g e

A.C supply

Charger Equipment

1.The float-cum boost charger shall meet the following current and voltage characteristics a) Input voltage  : 415V , - 30% to +20% , 3 phase 4 wire 50 Hz A.C.

b) Output voltage  : 40 to 70 volts D.C

c) Load current : 40Amps

d) Battery current : 30 Amps e) Total current : 70 Amps

2. The charger must have the facility for setting the current limit and output voltage at predetermined values

3 Manual resetting type mini circuit breakers of suitable rating shall be provided on A.C side of the charger for automatic tripping of the AC supply to the charger in case of DC over voltage or over load conditions.

4. The variation of the DC voltage shall be within +/- 1% for a variation in input AC supply voltage of +/-

20% and for a output current variation from no load to full load.

5. Provisions for adjusting the DC output in all mode of operation shall be provided. Provision for adjusting the upper limit of current shall also be provided in the auto mode. Potentiometer used for such adjustment shall be located on the front side of the panel and shall be calibrated in 3 or 4 ranges marked

6. Provision for boost charging the battery while keeping the voltage at load terminal from 46 volts to 52 volts by means of selector switch (preferably 4 positions) to select the required number of dropper diodes.

7. It shall have provision for automatic bypassing of dropper diodes and disconnection of bleeder resistor in case of failure of AC supply and also in case of failure of DC source to control circuits of charger.

8, The float cum boost charger shall also incorporate the following devices

a) One set of potentiometers for selecting output voltage in the following, modes of operation:

1. Manual

2. Boost

3. Float

a) One set of potentiometer for setting the voltage and current limit in auto mode.

b) The wound air-cooled mains transformer of sufficient rating shall be used for the charger and all details such as VA rating etc., shall be furnished. The tap selection shall be of half load type. The following taping shall also be provided.

Single phase 200,230,250 V , Three phase 380,415,450 V

d) One set of ripple filtering device to ensure that ripple content less than 500 mV

e) One set of automatic voltage regulator units. The regulators PCBs must be connected to the external circuit using fixing type sockets and connectors

f) Separate fuse protection shall be provided for AC_ supply, DC load, battery, capacitor bank- and control circuits.

g) Indicating meters of suitable rating to indicate:

1. Output DC voltage at load end battery terminals

2. One Ammeter to indicate total DC current

3. One centre Zero ammeter to indicate charge/discharge current through battery set h) All indicating shall be of flush mounted type with dust proof covers.

The instruments shall be square shaped Aluminium dimension of 96mm x 96mm. The dial shall be

white in color unit black numbers and lettering.

i) Indicating lamps to Indicate the healthiness of AC supply an AC-DC output shall be provided in the front side of the panels.

J) One set spare heaters with ON and OFF switch.

k) One lamp of sufficient voltage working on single phase AC to illuminate the interior of the battery charger, ON/OFF switch to be provided.

l) All semiconductor devices used for rectification of AC supply shall be protected using semiconductor HRC fuses which shall be fast acting.

m) The charger shall be effectively screened against causing interference to radio and other communication equipments which may be installed in the same row. They shall be fitted with RF suppressers.

n) The supplier of the charger shall take note of the fact that the DC positive (+ ve) lead of the charger will be maintained at ground potential.

o) Alarms Audio and visual alarms shall be provided to indicate the following  minimum points i)     Any fuse failure

ii)    Under voltage iii)   Over voltage

iv) AC mains failure

v) DC output failure

vi) Bridge diode SCR fuse failure vii) Filter fuse failure

viii) Overload

The arrangement shall be such that on occurrence of a fault, the corresponding, window will light up and stays lighted until the fault is cleared and reset button is pressed. Each time a window lights up, a master relay shall get energized to provide audible alarm in addition to group alarm signals for purchaser remote panel. The audible alarm shall stop on acknowledgement of the fault.

1.5 EARTHING

Two power earth terminals to be provided to make effective electrical contact with the panel frame. All metal part components of the units, which do not carry current, shall be connected thereto. Two earthing lugs suitable for receiving 10 sq. mm copper conductor shall be provided to the terminals.

1.6 PAINTING

The panel shall be chemically cleaned phosphate and sprayed with two coats of high quality primer and stored after each coat. The color of enamel paint to be used for finish shall be light gray.

Sufficient quantity of touch up paint shall be finished for application at site.

1.7 The following tests on battery charger- shall be carried out

1 . Dielectric tests

2. Voltage regulation check from 0% to 100% load at input supply variation

3. Ripple content measurement

4. Heat run test.

5. Test on current limiting value.

6. Routine test on component parts.

Necessary type testes as per relevant international standards shall be performed.

Tests shall be performed in the presence of Boards representative and the specified reports of the tests carried out at works shall be furnished for approval.

2 BATTERY SET

The specification covers the design, manufacture testing at works and supply of 48 V, 200Ah/300Ah

/400Ah battery with a battery stand, inter cell/ row connections and accessories complete as per IS

1652:2013 and latest ammendments. The batteries are required to provide DC supply (48 Volt) to PLCC

equipment.

2.0 GENERAL:

The battery shall be lead acid type with ‘plante’ positive plates

The plates shall be designed for maximum durability, during all service conditions including high rate of discharge and rapid fluctuations of load.

2.1 CONSTRUCTION

a) Each cell shall be assembled in heat resistant shock absorbing robust, clear glass or polymer container, the float type I level indicator.

b) Electrolyte level shall be marked on the container or external float indicators shall be provided. The marking as shall be for upper and Lower limits.

c) Sufficient sediment space shall be provided so that the cells will not have to be cleaned out during normal life.

d) Open type cells shall be provided with suitable spray arresters and separate perforated transparent plastic covers; anti-splash type vent plug shall be provided for type cell.

e) Separator between plates shall permit free flow of electrolyte. Separator shall be of acid resisting materials.

f) The cells shall be supported on porcelain insulator fixed on to the rack with adequate clearance between adjacent cells.

g) The battery shall consist of 24 cells of 2 volts each and of 100 AH capacity at 10 hours discharge rate. h) The cell terminal posts shall be provided with connector bolts and nuts effectively coated with

lead to prevent corrosion.

i) Lead or lead coated copper connectors shall be furnished to connect up cells of battery set.

j) Positive and negative terminal posts shall be clearly and indelibly marked for easy identification.

k) Lead coated bent copper plate, tubular copper lugs, teak wood clamp, bolts, nuts, washers etc., shall be furnished for connection of outgoing aluminium conductor cables.

Where the cells are called upon to discharge at very high rates, the fitness of lead coating of connectors shall be greater than 0.025 mm.

2.2 RACKS

a) The racks for supporting battery cells shall be designed for double row double tier arrangement and shall be constructed of best quality teak- wood, painted with at least three coats of anti-acid black paint.

b) Rack shall be free standing type, mounted an porcelain insulators.

c) Porcelain number plates for each cell shall be provided for being fixed on to the racks

2.3 TESTS

The supplier shall carry out necessary tests for local action, internal resistance, efficiency test and other routine test as stipulated in relevant IS.

The bidder should furnish along with his bid copies of the type and routine test conducted on similar equipment in accordance with relevant standards.

2.4  Fitting and Accessories:

Each battery set shall be furnished complete with the following:

a) First charge of electrolyte +10% extra over the required quantity. b) Teak-wood racks three coats of anti- acid paints.

c) Strand insulators plus 5% extra on and above the required quantities.

d) Cell insulator plus 5% extra over the required quantity. e) Cell inter connectors and take - off

f) Cell numbering tag with fixing arrangements. g) Teak wood cable clamps with hardware.

The following- accessories shall be supplied along with battery set for each station.

a) One (1) inter connector bolt wrench. b) One (1) Hydrometer with handle.

c) One (1) Thermometer the specific gravity correction scales. d) One (1) cell test in volumetric Arith leads.

D. C -Distribution Board (DC-DB): Void for 200Ah and applicable for 300AH and 400AH

The panel housing the DC Distribution Board shall be similar in construction to that of the charger. Each charger shall be provided with an independent DC Board. Suitable interlock to prevent paralleling of two DC sources shall be provided.

2.5 The D.C.D.B be designed such that:

a) The DC output of the charger and battery set is terminated on to DC busses inside the D.C.D.B. The charger connections shall be taken through circuit breakers and DPDT switches.

b) Twenty (20) feeder outlets of 10 Amps., capacity each with fuse protection to be provided in each of the DC distribution board. It shall be possible to transfer any feeder on to any of the charger.

c) One-volt meter with selector switch shall be provided to indicate bus voltage. 2 Ammeters One each for each source.

d) A detailed sketch indicating the construction and wiring of the D.C.D.B and the mode of various controls, shall be furnished.

e) Indicating Lamps shall be provided wherever necessary.

f) A single line diagram indicating the path of control shall be incorporated in the front panel of the

D.C.D.B.

g) DB shall be totally assembled wired and tested at factory.

h) The bus bars-wiring, and other conductor materials shall be of copper only.

2.6 TESTS AND INSPECTION:

2.7  The type of test and routine tests shall be carried out in the presence  of owner’s representative as per the IS applicable to that particular equipment.

2.8  If IS does not Match for any equipment, the testing shall be in accordance with EEC. In other cases 2th6e| bPidadgere shall furnish the details of the tests that will be carried out.