LINE TRAP OR WAVE TRAP:

The line trap shall confirm to IS 8792 and shall be of the broad band type suitable for operation in the frequency range 50 to 500 kHz. Blocking band selectable at site shall be 50 to 150kHz and 150 to 500 kHz.

1.The line trap shall be suitable for either suspension mounting from the power conductor or for pedestal mounting.  In  either  case  it  shall  withstand  the  stress  developed  at  the  maximum  wind pressure of 260 kgs,/sq. mtr. In case of wave traps of 2000 Amps and above current rating they shall be pedestal mounted type only.

2. If the weight of the wave traps are such that, they cannot be suspended to the line conductor, the bidder shall include in his bid pedestal stack, mounting structure, solid core porcelain insulators etc.

3.The bidder shall also quote as optional items for pedestal mounting equipments such as mounting structure, solid core porcelain insulator. The owner may order for these, if there are other constraints in suspension of wave traps at site

4. The line trap shall be suitable for being connected to the line ACSR conductor through electric power connectors. The power connector shall be of non-magnetic metal such as aluminium alloy and shall conform in all respects to IS 5561. The connectors shall be suitable for either vertical or horizontal take-off and shall be subject for all the type, acceptance and routine tests specified therein. Generally the conductors that will be used for connection will be DRAKE for all voltage systems.  However, the same will  be confirmed at the time of approval of drawings.

5. The line trap and the connections shall be suitable for the current ratings specified in clause (4) supra. The line trap impedance shall be negligible at the nominal power frequency of 50Hz so as not to disturb power transmission through it but shall be relatively high over the frequency band associated with carrier transmission. The recommended value of inductance of the main coil is 0.5mH or 1mH

6. The line trap shall consist main coil designed to carry continuously the rated current without exceeding in any part the limits of temperature rise. It shall be supplied with a protective device and a tuning device. The protective device shall be in the form of a lightning arrester designed and arranged such that neither significant change in its protective function nor physical damage shall result from either temperature rise or due to the magnetic field of the main coil either at maximum continuous rated current or at short time rated current. The protective device shall neither enter into operation nor remain in operation following transient actuation at the power frequency voltage developed across the line trap by the rated short time current. It shall be shunt connected across the main coil and the tuning device. The lighting arrester shall be of the station class current limiting active gap type and shall curator to IS

3070 in all respects.

7. The  inter  conductor  of  the  main  coil  shall  be  separated  by  insulator  bridges  or  separators provided all round the circumference at equidistant spacing.

8.The auxiliary tuning circuits consisting of tuning coil,  tuning condenser, resistor etc., shall be assembled in a porcelain or fiber glass insulated container and shall form an integral part of the wave trap.

9. The complete assembly shall show no signs of visible corona discharge voltage as per relevant IS

10. The assembly shall be provided with pre-fabricated bird barriers to prevent birds from entering and nesting within the wave traps. The bird barriers shall be of nonmagnetic insulating material such as fiber glass.

11. The complete  assembly shall  be  treated  with  a  special  silicon  varnish  in  order to  ensure its electrical longevity and finally spray palmed with a light grey enamel paint.