## Sheet2
Sl. No. | Item Code | Item Name | Unit | Qty | Item Specifications | Bidders Compliance | GSTpercent included in quoted rate | HSN Code
1 | 571540101R | AIR FILTER REGULATOR 0-2.1 KSC | Nos | 40 | Air filter regulator with mounting accessories & measuring gauge 1.Range : 0 - 2.1 KSC 2.Body : Aluminium 3.Spring : 304SS 4.Trim : 304SS 5.Packing : Teflon 6.Filter : Sintered Bronze 15 microns 7.Diaphragm with adjustable screw & manual drain facility. 8.Input & Output End connection : 1/4" NPT(F) 9.Output Pressure gauge Connection : 1/4" NPT(F). 10.Maximum Pressure Input : 18 KSC 11.Standard Pressure gauge(50mm): 0 - 2.1 ksc, 1/4" NPT(M)Rear Centre. 12.Mounting: field vertical 13:Mounting bracket: Yes 14.Operating Output Pressure: 1.75KSc 15.Operating Input Pressure: 7 KSc 16.Operating Temp: 0-60 Deg 17.Media: Compressed instrument air L/f : 1.10.38 CC: 5715401012 Make:PLACKA/SHAVO/NORGREN
| 571540101R | AIR FILTER REGULATOR 0-2.1 KSC
2 | 571540201R | AIR FILTER REGULATOR 0-4.2KSC | Nos | 40 | Air filter regulator with mounting accessories & measuring gauge 1.Range : 0 - 4.2 KSC 2.Body : Aluminium 3.Spring : 304SS 4.Trim : 304SS 5.Packing : Teflon 6.Filter : Sintered Bronze 15 microns 7.Diaphragm with adjustable screw & manual drain facility. 8.Input & Output End connection : 1/4" NPT(F) 9.Output Pressure gauge Connection : 1/4" NPT(F). 10.Maximum Pressure Input : 18 KSC 11.Standard Pressure gauge(50mm): 0 - 4.2 ksc, 1/4" NPT(M)Rear Centre. 12.Mounting: field vertical 13:Mounting bracket: Yes 14.Operating Output Pressure: 3 KSc 15.Operating Input Pressure: 7 KSc 16.Operating Temp: 0-60 Deg 17.Media: Compressed instrument air L/f : 1.10.37 CC: 5715402019 Make:PLACKA/SHAVO/NORGREN
| 571540201R | AIR FILTER REGULATOR 0-4.2KSC
3 | 571540301R | AIR FILTER REGULATOR 0-7.1 KSC | Nos | 20 | Air filter regulator with mounting accessories & measuring gauge 1.Range : 0 - 7.1 KSC 2.Body : Aluminium 3.Spring : 304SS 4.Trim : 304SS 5.Packing : Teflon 6.Filter : Sintered Bronze 15 microns 7.Diaphragm with adjustable screw & manual drain facility. 8.Input & Output End connection : 1/4" NPT(F) 9.Output Pressure gauge Connection : 1/4" NPT(F). 10.Maximum Pressure Input : 18 KSC 11.Standard Pressure gauge(50mm): 0 - 7.1 ksc, 1/4" NPT(M)Rear Centre. 12.Mounting: field vertical 13:Mounting bracket: Yes 14.Operating Output Pressure: 5.5 KSc 15.Operating Input Pressure: 7 KSc 16.Operating Temp: 0-60 Deg 17.Media: Compressed instrument air L/f : 1.10.36 CC: 5715403015 Make:PLACKA/SHAVO/NORGREN
| 571540301R | AIR FILTER REGULATOR 0-7.1 KSC
4 | 571540620R | PRESSURE GAUGE 0 - 4.2 KSC | Nos | 40 | 50 mm Pressure gauge 1.Range : 0 - 4.2 KSC 2.Body : All SS 3.Pressure element : Bourdon 4.Type : Direct reading 5.Mounting : Field 6.Dial size : 50 mm 7.Dial Colour : White 8.End connection : 1/4" NPT(M), Back entry (Centre). 9.Measuring Instrument class: 2.5(EN 837 - 1) 10.Temperature : 0 to 60 deg C 11.Media : compressed instrument air 12.Numerals : Black or standard with fine graduation 13.Front ring : Screwed 14.Accuracy : +/- 1% 15.Case : Weather Proof. 16.Resolution : 0.1 KSC 17.Service : Air regulators L/f : 1.10.07 CC: 5715406201 Make:PLACKA/SHAVO/NORGREN
| 571540620R | PRESSURE GAUGE 0 - 4.2 KSC
5 | 571540621R | PRESSURE GAUGE 0 - 7 KSC | Nos | 25 | 50 mm Pressure gauge 1.Range : 0 - 7 KSC 2.Body : All SS 3.Pressure element : Bourdon 4.Type : Direct reading 5.Mounting : Field 6.Dial size : 50 mm 7.Dial Colour : Circular White 8.End connection : 1/4" NPT(M), Back entry (Centre). 9.Measuring Instrument class: 2.5(EN 837 - 1) 10.Temperature : 0 to 60 deg C 11.Media : compressed instrument air 12.Numerals : Black or standard with fine graduation 13.Front ring : Screwed 14.Accuracy : +/- 1% 15.Case : Weather Proof. 16.Resolution : 0.2 KSC 17.Service : Air regulators L/f : 1.10.08 CC: 5715406219 Make:PLACKA/SHAVO/NORGREN
| 571540621R | PRESSURE GAUGE 0 - 7 KSC