## HT UG cable GTP
General Technical Particulars of 11kV Class HT UG Cable
Sl. No. | Particulars | unit | HT UG Cable | Reference
1 | Cables
a) Name of manufacturer
b) Place of manufacture
2 | Cable Type |  | A2XWY | IS 7098-II/2011 clause 21.3
3 | Applicable specificaton & standards voltage Grade |  | IS: 7098 (Part-2) /11kV
4 | Suitable for effective Earth/Unearth system
5 | Conductor screen, Insulation and insulation screen is manufactured by Tripple extrusion techniq only
6 | Permissible voltage & frequency variation for satisfactory operation
7 | Continuous current for standard conditon as per IS:
| a) In air (45⁰ C) | Amps |  | Table 10 of IS 3961 (P7)/2017
| b) In Ground (30⁰ C) | Amps
| c) In Duct | Amps
8 | Conductor
| a) Material |  | Aluminium (H2/H4 Grade) | BESCOM TS Clause 8.1 & 10.0 & Clause 4 of IS: 8310:2013
b) Purity & Resistivity of Conductor@20ºC
| c) Shape of conductor |  | Strandard compacted circular | BESCOM TS Clause 8.1 & Clause 4 of IS 8130/2013
| d) Geometrical cross sectional area | mm²
| e) Number of wire: (min) | No |  | BESCOM TS Clause 8.1/ Table 2 of IS 8130/2013
| f) Diameter of Wire : mm before compacting & strand Diameter | mm |  | However, the effective cross section should be as specified as specified at Sl. 8d
| f) Maximum DC resistance of the conductor at 20⁰ C | Ω/KM | ……………..(CR value only for reference) | Table 2 of IS 8130:2013
| g) Sampling batch for test |  | IS 7098-II/2011 Annex D | Annex D of IS 7098-II/2011
9 | Conductor Screening
| a) Material |  | Pressure Extruded Semiconducting compound
| b) Process |  | Triple Extrusion
| c) Thickness (Min) | mm | 0.4mm | BESCOM requirement as per clause No.10.02 of BESCOM TS & Clause: 11.1 of IS-7098 Part-2: 2011
| d) Continuous working temp | deg.C | 90
| e) Max allowable temp at termination of short circuit | deg.C | 250 | PART 3 of IS 13573/
10 | Insulation:
| a) Material |  | XLPE | BESCOM requirement, As per clause No.10.03 & Table 1, Annexure TS-2 of BESCOM TS and clause 5 of IS 7098-II /2011
| b) Thickness of Insulation (Nom) | mm |  | Table 4 of IS 7098-II /2011
| i) Between Cores | mm
ii) Between Cores & Inner Sheath
| c) Minimum thickness of insulation at any one point | (mm)
| d) Extrusion Type |  | Tripple Pressure Extruded
| e) Specific insulation resistance at 90⁰ C | Ohm-cm |  | Table 1 of IS 7098-II /2011
f) Hot Set test:
| a) Elongation under load (Max) | % | 90% Max | BESCOM requirement TS Schedule-II Annexure TS-2
| b) Maximum Permanent elongation after cooling (Max) | % | 10% Max
| c) Tensile Strength at break (Min) | N/mm² | ………... Min | Table-1 of IS 7098-II /2011
| d) Elongation at break (Min) | % | ………….. Min
| e) Shrinkage (Max) | % | ………….. Max
11 | Insulation Screening:
| a) Material |  | Extruded Cross linked semi conducting compond | As per Bescom Clause 10.4 of BESCOM TS & clause 13 of IS 7098 P-II /2011
| b) Min. Thickness of extruded semi conducting layer | mm | 0.3mm (Min) | BESCOM requirement and Clause 10.4.1 of TS
| c) Metallic Part: (Material) |  | Plain copper tape | BESCOM requirement and clause 10.4.2 of TS
| d) Size of copper Tape (Minimum) | mm | 0.045 | BESCOM requirement and clause 10.4.2 of TS
| e) Whether over lapping provided |  | Min 5% of Overlaping | BESCOM requirement and Clause 10.4.2 of TS
| f) Short Circuit rating in 1 sec. | KA |  | Calcualtion sheet shall be enclosed
12 | Inner Sheath
| a) Material |  | PVC copound Type -ST2 | Clause 10.6.1 of Bescom TS. & IS 5831-1984
| b) Extrusion Type |  | Pressure Extruded
| c) Thickness (Min) | mm |  | Table 5 of IS 7098-II /2011
| d) Nominal Dia over Inner Sheath | mm |  | 10462(P-1)/1983 Ficticious calculation
13 | Armouring
| a) Material |  | Galvanised Steel | Clause 10.7.2 of Bescom TS.
| b) Type of armouring |  | Round wire
| c) Nominal Dimensionof Armour wire | mm | ………. Dimension and % of Tolerance | IS 3975/ 1999 (RA 2004) & Tolerance shall be ± 5 %. As per Clause 10.7.2 of TS
| d) Minimum Number of Armour wire |  | ………. Numbers (Minimum) | IS-7098-II/2011 & 10462(P2)/1983
e) Whether Galvanised
| f) Mass of Zinc coating | gm/M² |  | Table 2 of IS-4826/1979 & IS 3975 /1999
| g) Nominal Dia over Armouring | mm |  | IS-10462(P-1)/1983
| h) Short Circuit rating in 1 sec | KA |  | By Formula
| i) Resistivity of the Aroured wire | ohm -cm (max) |  | Clause No. 10.7.2 of BESCOM T.S. & IS 3975/ 1999 (RA 2004) Clause 8.4.1
14 | Outer Sheath
| a) Material |  |  | Extruded PVC Compound Type ST-2 as per IS 5831-1984
| b) Extrution type |  |  | Extruded
| c) Min. thickness of sheath | mm |  | Table 7 of IS 7098-II/2011
| d) Nominal Overall diameter of cable | mm |  | IS-10462/1983 Ficticious dia
| e) Tensile Strength at break | N/mm²
| f) Elongation at break | %
| g) Shrinkage | %
| h)Thermal stability test for sheath | Minutes | 100 minutes(Min) | BESCOM Requirement 100 Minutes (Min) as per Clause No. 10.8.1 of BESCOM T.S.
15 | Short circuit withstand capacity
| a) Short Circuit withstand capacity | KA
| b) Duration of short circuit | sec | one
16 | AC resistance per core at operating temperature | ohm/km |  | Calculation sheet shall be enclosed
17 | Reactance Ohm/Km | ohm/km
18 | Capicitance per core | μF/Km
19 | Allowable maximum conductor temperature when carrying current
20 | Insulation resistance at 27⁰ C | ohm-cm |  | Table 1 of IS 7098-II/2011
21 | Loss tangent at Ambient Temperature at Uo |  |  | Clause 20.4.2 of IS 7098-II/2011
22 | Maximum cable charging current at normal operating volt | A/km |  | Calculation sheet shall be enclosed
Additional data
23 | Core identification |  | Application of coloured stripes Red, Yellow & Blue | IS-10418/1982
24 | Standard Packing Length and Tolerance | Mtrs | 250/500 Mtrs | Clause No. 13.2.4 of BESCOM T.S.
25 | Scheme of identification of the cable |  | Manufacturer’s name or trade mark, voltage grade, year of manufacture and the letters “BESCOM". The identification shall repeat every 300/350 mm along with length of the cable. | Clause 21.1 of IS 7098-II/2011

## hotset (hidden)
General Technical Parameters
Sl. No. | Particulars | unit | HT UG Cable
1 | Cables
a) Name of manufacturer
b) Place of manufacture
2 | Cable Type
f) Hot Set test:
| a) Elongation under load | % | ……….. Max
| b) Maximum Permanent elongation after cooling | % | ……………..Max
| c) Tensile Strength at break | N/mm² | ………... Minimum
| d) Elongation at break | % | ………….. Min