## combined cover
482459198
482459198
GOVERNMENT OF BIHAR
PUBLIC HEALTH ENGINEERING DEPARTMENT
TECHNICAL SANCTION
NAME OF THE WORK:- CONSTRUCTION OF RURAL PIPED WATER SUPPLY SCHEMES UNDER "HAR GHAR NAL JAL" IN PRD LEFT OUT HABITATION THAT HAS BEEN TAKEN OVER BY PHED, FOR SATURATION OF UNCOVERED HABITATION HAVING 16589 HOUSEHOLD UNDER DIFFERENT BLOCKS OF VAISHALI DISTRICT UNDER P.H.DIVISION HAJIPUR FOR YEAR 2026-27.
ESTIMATED COST- Rs. 48,24,59,198.00
P.H. DIVISION HAJIPUR

## ABST PANCHAYAT
Government Of Bihar
PUBLIC HEALTH ENGINEERING DEPARTMENT
ABSTRACT OF COST FOR PANCHAYAT
NAME OF THE WORK:- CONSTRUCTION OF RURAL PIPED WATER SUPPLY SCHEMES UNDER "HAR GHAR NAL JAL" IN PRD LEFT OUT HABITATION THAT HAS BEEN TAKEN OVER BY PHED, FOR SATURATION OF UNCOVERED HABITATION HAVING 16589 HOUSEHOLD UNDER DIFFERENT BLOCKS OF VAISHALI DISTRICT UNDER P.H.DIVISION HAJIPUR FOR YEAR 2026-27.
S.N. | Description |  |  |  | Unit | Qty / No | Rate ( Rs) | Amount ( Rs)
I | CONSTRUCTION OF TUBE WELL OF DIFFERENT SIZE .
A | 150mm X100mmx 125m deep T/W etc. all complete and as per direction of E/I. (As per work details 1C) |  |  |  | Each | 199 | 279342 | 55589058
II | Constructing masonry Chamber 100x100x75 cm inside, in brick work in cement mortar 1:4 (1 cement : 4 coarse sand) for Tube Well, and RCC top slab 1:1.5:3 mix (1 cement : 1.5 coarse sand : 3 graded stone aggregate 20mm nominal size ) , necessary excavation, foundation concrete 1:2:4(1 cement : 2 fine sand : 4 graded stone aggregate 20 mm nominal size) and inside plastering with cement mortar 1:3 (1 cement : 3coarse sand) 12 mm thick with 5% cico fnished with a floating coat of neat cement, out side plastering with cement mortar 1:4 (1 cement : 4coarse sand) 12 mm thick complete as per standard specifications & direction of E/I. (As per work details.- 2) |  |  |  | Each | 199 | 14535 | 2892465
III | Providing and Laying Distrbution network of High Density Polyethyene pipe (HDPE pipe) including 10000 liter PVC tank installed at 8M high MS staging etc all complete as per direction of E/I. (As per work details.- 3)
1 | MAHUA | RASULPUR MUBARAK | Ward No | 13 | Item | 1 | 824719.2378 | 824719.2378
2 | MAHUA | FULWARIYA | Ward No | 4 | Item | 1 | 971546.5924 | 971546.5924
3 | MAHUA | MADHUL | Ward No | 15 | Item | 1 | 768783.1128 | 768783.1128
4 | MAHUA | MADHUL | Ward No | 3 | Item | 1 | 676999.2655 | 676999.2655
5 | MAHUA | GOVINDPUR | Ward No | 14 | Item | 1 | 684237.3355 | 684237.3355
6 | MAHUA | KANULI DHANRAJ | Ward No | 3 | Item | 1 | 768783.1128 | 768783.1128
7 | MAHUA | JAHAGIRPUR SALKHANNI | Ward No | 5 | Item | 1 | 1093704.9446 | 1093704.9446
8 | MAHUA | HASANPUR OSTI | Ward No | 8 | Item | 1 | 1039214.1804 | 1039214.1804
9 | MAHUA | HASANPUR OSTI | Ward No | 3 | Item | 1 | 1431358.8896 | 1431358.8896
10 | MAHUA | KANHAULI DHANRAJ | Ward No | 2 | Item | 1 | 1419186.9515 | 1419186.9515
11 | MAHUA | JAHAGIRPUR SALKHANNI | Ward No | 6 | Item | 1 | 634567.3082 | 634567.3082
12 | MAHUA | GAUSPUR CHKMJAHID | Ward No | 12 | Item | 1 | 734132.2497 | 734132.2497
13 | MAHUA | RASULPUR MOBARK | Ward No | 8 | Item | 1 | 1230779.0361 | 1230779.0361
14 | MAHUA | SHERPUR MANIKPUR | Ward No | 3&5 | Item | 1 | 912668.6259 | 912668.6259
15 | MAHUA | TAJPUR BUZURAG | Ward No | 5 | Item | 1 | 1047559.5804 | 1047559.5804
16 | MAHUA | RAMPUR CHANDRABHAN URF DAGARU | Ward No | 14 | Item | 1 | 610665.2952 | 610665.2952
17 | MAHUA | RAMPUR CHANDRABHAN URF DAGARU | Ward No | 11 | Item | 1 | 977587.8032 | 977587.8032
18 | MAHUA | RAMPUR CHANDRABHAN URF DAGARU | Ward No | 12 | Item | 1 | 918919.952 | 918919.952
19 | MAHUA | SHERPUR MANIKPUR | Ward No | 5 | Item | 1 | 939207.3401 | 939207.3401
20 | MAHUA | BISUNPUR HIRARAM URF PAHARPUR | Ward No | 7 | Item | 1 | 815399.0997 | 815399.0997
21 | MAHUA | BISUNPUR HIRARAM URF PAHARPUR | Ward No | 8 | Item | 1 | 1202508.3827 | 1202508.3827
22 | MAHUA | MANGURAHI | Ward No | 12 | Item | 1 | 832943.1759 | 832943.1759
23 | MAHUA | MANGURAHI | Ward No | 1 | Item | 1 | 806508.3759 | 806508.3759
24 | MAHUA | LAXMINARAYANPUR | Ward No | 3 | Item | 1 | 794226.0367 | 794226.0367
25 | MAHUA | MIRJANAGAR | Ward No | 4 | Item | 1 | 663626.7344 | 663626.7344
26 | MAHUA | MIRJANAGAR | Ward No | 2 | Item | 1 | 873734.9639 | 873734.9639
27 | MAHUA | SAMASPURA | Ward No | 7 | Item | 1 | 881194.6889 | 881194.6889
28 | CHEHRAKALA | BASTI SARSIKAN | Ward No | 8B | Item | 1 | 582168.3556 | 582168.3556
29 | CHEHRAKALA | AKHTIYARPUR | Ward No | 14B | Item | 1 | 561838.6828 | 561838.6828
30 | CHEHRAKALA | RASULPUR FATAH | Ward No | 3B | Item | 1 | 804538.0509 | 804538.0509
31 | CHEHRAKALA | RASULPUR FATAH | Ward No | 4B | Item | 1 | 793003.7778 | 793003.7778
32 | CHEHRAKALA | SAHPUR KHURD | Ward No | 4,5 | Item | 1 | 629148.6639 | 629148.6639
33 | CHEHRAKALA | BASTI SARSIKAN | Ward No | 7 | Item | 1 | 509248.2014 | 509248.2014
34 | CHEHRAKALA | BASTI SARSIKAN | Ward No | 14 | Item | 1 | 509248.2014 | 509248.2014
35 | CHEHRAKALA | BASTI SARSIKAN | Ward No | 15 | Item | 1 | 518262.7103 | 518262.7103
36 | CHEHRAKALA | ABABAKARPUR | Ward No | 3 | Item | 1 | 516793.254 | 516793.254
37 | CHEHRAKALA | KARAHATIYA BUZURG | Ward No | 2B | Item | 1 | 507778.7451 | 507778.7451 | 37432757.6767
38 | CHEHRAKALA | BISUNPUR ARRA | Ward No | 5,7 | Item | 1 | 513020.7277 | 513020.7277
39 | CHEHRAKALA | BISUNPUR ARRA | Ward No | 8,14 | Item | 1 | 511551.2714 | 511551.2714
40 | CHEHRAKALA | RASULPUR FATAH | Ward No | 14,12 | Item | 1 | 509248.2014 | 509248.2014
41 | CHEHRAKALA | RASULPUR FATAH | Ward No | 9 | Item | 1 | 514490.184 | 514490.184
42 | HAJIPUR | Daulatpur Chandi | Ward No | 2 | Item | 1 | 1520841.8026 | 1520841.8026
43 | HAJIPUR | Daulatpur Chandi | Ward No | 4 | Item | 1 | 921834.2803 | 921834.2803
44 | HAJIPUR | Daulatpur Chandi | Ward No | 8 | Item | 1 | 785133.5617 | 785133.5617
45 | HAJIPUR | Daulatpur Chandi | Ward No | 11 | Item | 1 | 862992.6009 | 862992.6009
46 | HAJIPUR | Daulatpur Chandi | Ward No | 3 | Item | 1 | 864304.9139 | 864304.9139
47 | HAJIPUR | Daulatpur Dewariya | Ward No | 5 | Item | 1 | 824719.2378 | 824719.2378
48 | HAJIPUR | Gadai Sarai | Ward No | 7 | Item | 1 | 728110.0105 | 728110.0105
49 | HAJIPUR | Gadai Sarai | Ward No | 8 | Item | 1 | 697133 | 697133
50 | HAJIPUR | Gadai Sarai | Ward No | 9 | Item | 1 | 758923.6486 | 758923.6486
51 | HAJIPUR | Gadai Sarai | Ward No | 12 | Item | 1 | 1047661.6174 | 1047661.6174
52 | HAJIPUR | Bisunpur Baladhari | Ward No | 5 | Item | 1 | 1055662.9554 | 1055662.9554
53 | HAJIPUR | Bisunpur Baladhari | Ward No | 6 | Item | 1 | 974289.9043 | 974289.9043
54 | HAJIPUR | Bisunpur Baladhari | Ward No | 8 | Item | 1 | 1520841.8026 | 1520841.8026
55 | HAJIPUR | Gadai Sarai | Ward No | 11 | Item | 1 | 1128918.2696 | 1128918.2696
56 | HAJIPUR | Ismailpur | Ward No | 1&2 | Item | 1 | 1117290.2316 | 1117290.2316
57 | HAJIPUR | Ismailpur | Ward No | 3 | Item | 1 | 999951.7174 | 999951.7174
58 | HAJIPUR | Ismailpur | Ward No | 4 | Item | 1 | 950935.9912 | 950935.9912
59 | HAJIPUR | Ismailpur | Ward No | 6 | Item | 1 | 950935.9912 | 950935.9912
60 | HAJIPUR | Ismailpur | Ward No | 15 | Item | 1 | 864304.9139 | 864304.9139
61 | HAJIPUR | Manua | Ward No | 6 | Item | 1 | 977803.9162 | 977803.9162
62 | HAJIPUR | Manua | Ward No | 7 | Item | 1 | 969686.1793 | 969686.1793
63 | HAJIPUR | Manua | Ward No | 8 | Item | 1 | 1200629.8969 | 1200629.8969
64 | HAJIPUR | Thathan Buzurg | Ward No | 13 | Item | 1 | 842157.1128 | 842157.1128
65 | HAJIPUR | Pahetiya | Ward No | 4 | Item | 1 | 997327.0912 | 997327.0912
66 | HAJIPUR | Pahetiya | Ward No | 10 | Item | 1 | 911350.3151 | 911350.3151
67 | HAJIPUR | Pahetiya | Ward No | 5 | Item | 1 | 902578.277 | 902578.277
68 | HAJIPUR | Pahetiya | Ward No | 8 | Item | 1 | 1409959.453 | 1409959.453
69 | HAJIPUR | Pahetiya | Ward No | 14 | Item | 1 | 996778.9912 | 996778.9912
70 | HAJIPUR | Afjalpur Dhobaghatti | Ward No | 1 | Item | 1 | 695759.1725 | 695759.1725
71 | HAJIPUR | Afjalpur Dhobaghatti | Ward No | 7 | Item | 1 | 1409959.453 | 1409959.453
72 | HAJIPUR | Afjalpur Dhobaghatti | Ward No | 8 | Item | 1 | 855532.8759 | 855532.8759
73 | HAJIPUR | Afjalpur Dhobaghatti | Ward No | 4 | Item | 1 | 969686.1793 | 969686.1793
74 | HAJIPUR | Afjalpur Dhobaghatti | Ward No | 11 | Item | 1 | 822633.9378 | 822633.9378
75 | HAJIPUR | Afjalpur Dhobaghatti | Ward No | 12 & 13 | Item | 1 | 988436.3674 | 988436.3674
76 | HAJIPUR | Senduari | Ward No | 14 | Item | 1 | 1228270.8089 | 1228270.8089
77 | HAJIPUR | Bisunpur Basant | Ward No | 3 | Item | 1 | 966288.5662 | 966288.5662
78 | HAJIPUR | Bisunpur Basant | Ward No | 4 | Item | 1 | 824719.2378 | 824719.2378
79 | HAJIPUR | Bisunpur Basant | Ward No | 12 | Item | 1 | 803883.7497 | 803883.7497
80 | HAJIPUR | Bisunpur Basant | Ward No | 10 | Item | 1 | 1036912.7674 | 1036912.7674
81 | HAJIPUR | Bishunpur Basant | Ward No | 14 | Item | 1 | 1409959.453 | 1409959.453
82 | HAJIPUR | Panapur Langa | Ward No | 1 | Item | 1 | 728110.0105 | 728110.0105
83 | HAJIPUR | Panapur Langa | Ward No | 2 | Item | 1 | 803883.7497 | 803883.7497
84 | HAJIPUR | Panapur Langa | Ward No | 8 | Item | 1 | 1138125.7196 | 1138125.7196
85 | HAJIPUR | Panapur Langa | Ward No | 9 | Item | 1 | 1098540.0435 | 1098540.0435
86 | HAJIPUR | Chankunda urf Milki | Ward No | 5 | Item | 1 | 1130124.3816 | 1130124.3816
87 | HAJIPUR | Chankunda urf Milki | Ward No | 4 | Item | 1 | 957516.5282 | 957516.5282
88 | HAJIPUR | Chankunda urf Milki | Ward No | 3 | Item | 1 | 969686.1793 | 969686.1793
89 | HAJIPUR | Kashipur chakbibi | Ward No | 12 | Item | 1 | 907952.702 | 907952.702
90 | HAJIPUR | Kashipur chakbibi | Ward No | 7 | Item | 1 | 951594.0032 | 951594.0032
91 | HAJIPUR | Kasipur Chakbibi | Ward No | 8 | Item | 1 | 690384.7475 | 690384.7475
92 | HAJIPUR | Bahuara | Ward No | 1 | Item | 1 | 1119373.2446 | 1119373.2446
93 | HAJIPUR | Bahuara | Ward No | 10 | Item | 1 | 1128918.2696 | 1128918.2696
94 | HAJIPUR | Bahuara | Ward No | 14 | Item | 1 | 697000 | 697000
95 | HAJIPUR | Andharbara | Ward No | 2 | Item | 1 | 593775.5202 | 593775.5202
96 | HAJIPUR | Andharbara | Ward No | 3 | Item | 1 | 938766.3401 | 938766.3401
97 | HAJIPUR | Andharbara | Ward No | 4 | Item | 1 | 938766.3401 | 938766.3401
98 | HAJIPUR | Andharbara | Ward No | 9 | Item | 1 | 860907.3009 | 860907.3009
99 | HAJIPUR | Andharbara | Ward No | 10 | Item | 1 | 738088.1605 | 738088.1605
100 | HAJIPUR | Andharbara | Ward No | 11 | Item | 1 | 1128918.2696 | 1128918.2696
101 | HAJIPUR | Andharbara | Ward No | 13 | Item | 1 | 1034827.4674 | 1034827.4674
102 | HAJIPUR | Hilalpur | Ward No | 1 | Item | 1 | 785133.5617 | 785133.5617
103 | HAJIPUR | Hilalpur | Ward No | 9 & 10 | Item | 1 | 1196461.5839 | 1196461.5839
104 | HAJIPUR | Hilalpur | Ward No | 8 | Item | 1 | 969686.1793 | 969686.1793
105 | HAJIPUR | Sultanpur | Ward No | 3 | Item | 1 | 912779.027 | 912779.027
106 | HAJIPUR | Sultanpur | Ward No | 9 | Item | 1 | 830093.6628 | 830093.6628
107 | HAJIPUR | Hilalpur | Ward No | 5 | Item | 1 | 1128918.2696 | 1128918.2696
108 | BIDUPUR | Bidupur | Ward No | 12 | Item | 1 | 931187.9293 | 931187.9293
109 | BIDUPUR | Dilawarpur Govardhan | Ward No | 13,12 | Item | 1 | 734132.2497 | 734132.2497
110 | BIDUPUR | Sahdulapur Dhobauli | Ward No | 9 | Item | 1 | 1230779.0361 | 1230779.0361
111 | BIDUPUR | Sahdulapur Dhobauli | Ward No | 15A | Item | 1 | 912668.6259 | 912668.6259
112 | BIDUPUR | Amer | Ward No | 8,13 | Item | 1 | 610665.2952 | 610665.2952
113 | BIDUPUR | Khanpur Pakri | Ward No | 6 | Item | 1 | 977587.8032 | 977587.8032
114 | BIDUPUR | Kathuliya | Ward No | 7 | Item | 1 | 918919.952 | 918919.952
115 | BIDUPUR | Chakatkurshi | Ward No | 8 | Item | 1 | 939207.3401 | 939207.3401
116 | BIDUPUR | Saidpur Ganesh | Ward No | 6 | Item | 1 | 1202508.3827 | 1202508.3827
117 | BIDUPUR | Mail | Ward No | 12 | Item | 1 | 806508.3759 | 806508.3759
118 | BIDUPUR | Dilawarpur Govardhan | Ward No | 13 | Item | 1 | 992882.6385 | 992882.6385
119 | BIDUPUR | Bidupur | Ward No | 10 | Item | 1 | 1060764.5546 | 1060764.5546
120 | BIDUPUR | Rahimapur | Ward No | 6&7 | Item | 1 | 648047.5925 | 648047.5925
121 | BIDUPUR | Kanchanpur | Ward No | 4 | Item | 1 | 644495.5813 | 644495.5813
122 | BIDUPUR | Rahimapur | Ward No | 9& 10 | Item | 1 | 924656.2762 | 924656.2762
123 | BIDUPUR | Khanpur Pakri | Ward No | 15&16 | Item | 1 | 881948.1562 | 881948.1562
124 | BIDUPUR | Kathuliya | Ward No | 11&12 | Item | 1 | 716893.2217 | 716893.2217
125 | BIDUPUR | Saidpur Ganesh | Ward No | 9B | Item | 1 | 710672.1355 | 710672.1355
126 | RAJAPAKAR | JAFARPATTI | Ward No | 10 | Item | 1 | 862873.9151 | 862873.9151
127 | RAJAPAKAR | BAIKUNTHPUR | Ward No | 7,9 | Item | 1 | 1056092.3696 | 1056092.3696
128 | RAJAPAKAR | Bakhari bari | Ward No | 11B, 8 | Item | 1 | 1520841.8026 | 1520841.8026
129 | RAJAPAKAR | RAMPUR RATNAKAR | Ward No | 08,11 & 16B | Item | 1 | 1520841.8026 | 1520841.8026
130 | RAJAPAKAR | BARAI | Ward No | 9,6 | Item | 1 | 1093704.9446 | 1093704.9446
131 | RAJAPAKAR | MIRPUR PATHAD | Ward No | 1,6,5 | Item | 1 | 1419186.9515 | 1419186.9515
132 | RAJAPAKAR | BAIKUNTPUR | Ward No | 1,2,11 | Item | 1 | 1230779.0361 | 1230779.0361
133 | RAJAPAKAR | Bakarpur | Ward No | 11,13 | Item | 1 | 1093704.9446 | 1093704.9446
134 | RAJAPAKAR | Narayanpur Bujurg | Ward No | 11,14 | Item | 1 | 1431358.8896 | 1431358.8896
135 | RAJAPAKAR | Jafarpatti | Ward No | 3 | Item | 1 | 1419186.9515 | 1419186.9515
136 | RAJAPAKAR | Gauspur | Ward No | 2,4 | Item | 1 | 1520841.8026 | 1520841.8026
137 | RAJAPAKAR | Bakarpur | Ward No | 3 | Item | 1 | 921834.2803 | 921834.2803
138 | RAJAPAKAR | Rajapakar Uttari | Ward No | 3 | Item | 1 | 862992.6009 | 862992.6009
139 | RAGHOPUR | RUSTAMPUR | Ward No | 4 | Item | 1 | 610665.2952 | 610665.2952
140 | RAGHOPUR | CHANDPURA | Ward No | 1 | Item | 1 | 1047559.5804 | 1047559.5804
141 | RAGHOPUR | CHANDPURA | Ward No | 6 | Item | 1 | 977587.8032 | 977587.8032
142 | RAGHOPUR | CHANDPURA | Ward No | 11 | Item | 1 | 918919.952 | 918919.952
143 | RAGHOPUR | CHANDPURA | Ward No | 5 | Item | 1 | 939207.3401 | 939207.3401
144 | RAGHOPUR | RUSTAMPUR | Ward No | 5B,20 | Item | 1 | 1419186.9515 | 1419186.9515
145 | RAGHOPUR | JAHAGIRPUR | Ward No | 1 | Item | 1 | 1047559.5804 | 1047559.5804
146 | RAGHOPUR | JAHAGIRPUR | Ward No | 7 | Item | 1 | 1093704.9446 | 1093704.9446
147 | RAGHOPUR | JAHAGIRPUR | Ward No | 5 | Item | 1 | 1039214.1804 | 1039214.1804
148 | RAGHOPUR | JAHAGIRPUR | Ward No | 4 | Item | 1 | 1431358.8896 | 1431358.8896
149 | RAGHOPUR | SARAIPUR | Ward No | 5 | Item | 1 | 1419186.9515 | 1419186.9515
150 | RAGHOPUR | TERASIYA | Ward No | 11 | Item | 1 | 939207.3401 | 939207.3401
151 | RAGHOPUR | TERASIYA | Ward No | 12 | Item | 1 | 939207.3401 | 939207.3401
152 | RAGHOPUR | RAMPUR SHAYAMCHAND | Ward No | 13 | Item | 1 | 815399.0997 | 815399.0997
153 | RAGHOPUR | RAGHOPUR EAST | Ward No | 7 | Item | 1 | 1202508.3827 | 1202508.3827
154 | RAGHOPUR | BAHARAMAPUR | Ward No | 2,3 | Item | 1 | 832943.1759 | 832943.1759
155 | RAGHOPUR | BAHARAMAPUR | Ward No | 13 | Item | 1 | 806508.3759 | 806508.3759
156 | RAGHOPUR | BAHARAMAPUR | Ward No | 10 | Item | 1 | 794226.0367 | 794226.0367
157 | VAISHALI | Amritpur | Ward No | 8 | Item | 1 | 821202.9389 | 821202.9389
158 | VAISHALI | Majhauli | Ward No | 8 | Item | 1 | 1128918.2696 | 1128918.2696
159 | PATEDHI BELSAR | Nagawan | Ward No | 10 | Item | 1 | 1093704.9446 | 1093704.9446
160 | PATEDHI BELSAR | Nagawan | Ward No | 1 | Item | 1 | 1039214.1804 | 1039214.1804
161 | PATEDHI BELSAR | Sain | Ward No | 1 | Item | 1 | 1431358.8896 | 1431358.8896
162 | PATEDHI BELSAR | Sain | Ward No | 4 | Item | 1 | 1419186.9515 | 1419186.9515
163 | PATEDHI BELSAR | Sorahattha | Ward No | 1 | Item | 1 | 1230779.0361 | 1230779.0361
164 | PATEDHI BELSAR | Manora | Ward No | 13 | Item | 1 | 912668.6259 | 912668.6259
165 | PATEDHI BELSAR | Mishrauliya | Ward No | 8 | Item | 1 | 939207.3401 | 939207.3401
166 | PATEDHI BELSAR | Manora | Ward No | 1 | Item | 1 | 1202508.3827 | 1202508.3827
167 | PATEDHI BELSAR | Chakgulamuddin | Ward No | 2 | Item | 1 | 806508.3759 | 806508.3759
168 | PATEDHI BELSAR | Chakgulamuddin | Ward No | 1 | Item | 1 | 794226.0367 | 794226.0367
169 | PATEDHI BELSAR | Mishrauliya | Ward No | 10 | Item | 1 | 656167.0094 | 656167.0094
170 | PATEDHI BELSAR | Karneji | Ward No | 5 | Item | 1 | 678634.1617 | 678634.1617
171 | GORAUL | Katarmala | Ward No | 2 | Item | 1 | 526548.9321 | 526548.9321
172 | GORAUL | ISMAILPUR | Ward No | 11&12 | Item | 1 | 752115.9378 | 752115.9378
173 | GORAUL | ISMAILPUR | Ward No | 4B | Item | 1 | 907834.0162 | 907834.0162
174 | GORAUL | BHUALPUR UF BAHADURPUR | Ward No | 7&8 | Item | 1 | 481588.831 | 481588.831
175 | GORAUL | LODIPUR | Ward No | 6 | Item | 1 | 1520841.8026 | 1520841.8026
176 | GORAUL | BAKSAMA | Ward No | 13 | Item | 1 | 921834.2803 | 921834.2803
177 | LALGANJ | Atwarpur Sisaula | Ward No | 02&03 | Item | 1 | 881948.1562 | 881948.1562
178 | LALGANJ | Yusufpur | Ward No | 5 | Item | 1 | 1039214.1804 | 1039214.1804
179 | LALGANJ | Bhatuli Bhagwan | Ward No | 10,11,12 | Item | 1 | 785133.5617 | 785133.5617
180 | LALGANJ | Shital Bhakurahar | Ward No | 3 | Item | 1 | 824719.2378 | 824719.2378
181 | LALGANJ | Yusufpur | Ward No | 3 | Item | 1 | 918919.952 | 918919.952
182 | BHAGWANPUR | Sahmia Rahua | Ward No | 1 | Item | 1 | 1093704.9446 | 1093704.9446
183 | BHAGWANPUR | MAGANPUR | Ward No | 6 | Item | 1 | 1039214.1804 | 1039214.1804
184 | BHAGWANPUR | SAHTHA | Ward No | 2 | Item | 1 | 1431358.8896 | 1431358.8896
185 | SAHDEI BUZURG | Naya Gaow West | Ward No | 11 | Item | 1 | 748455.3745 | 748455.3745
186 | SAHDEI BUZURG | Sultanpur | Ward No | 9 | Item | 1 | 1093704.9446 | 1093704.9446
187 | MAHNAR | Gorigama | Ward No | 9 | Item | 1 | 748455.3745 | 748455.3745
188 | PATEPUR | Malpur | Ward No | 2 | Item | 1 | 745204.3128 | 745204.3128
189 | PATEPUR | Govindpur Bela | Ward No | 6 | Item | 1 | 725906.0247 | 725906.0247
190 | PATEPUR | Harlochanpur Sukki | Ward No | 3 | Item | 1 | 725906.0247 | 725906.0247
191 | JANDAHA | Mahipura | Ward No | 7 | Item | 1 | 992882.6385 | 992882.6385
192 | JANDAHA | Said Mohammad Urf Salaha | Ward No | 9 | Item | 1 | 1060764.5546 | 1060764.5546
193 | JANDAHA | Chandsarai | Ward No | 12 | Item | 1 | 648047.5925 | 648047.5925
194 | JANDAHA | Dih Bichauli | Ward No | 8&1 | Item | 1 | 644495.5813 | 644495.5813
195 | JANDAHA | Khopi | Ward No | 3 | Item | 1 | 924656.2762 | 924656.2762
196 | JANDAHA | Rasulpur Purushottam | Ward No | 4,5,6 | Item | 1 | 716893.2217 | 716893.2217
197 | JANDAHA | Laxmipur Barbatta | Ward No | 8 | Item | 1 | 588943.5713 | 588943.5713
198 | JANDAHA | Harprasad | Ward No | 10 | Item | 1 | 849687.1751 | 849687.1751
199 | JANDAHA | Harprasad | Ward No | 3 | Item | 1 | 813523.6892 | 813523.6892
IV | Supply Installation, commissioning and testing of single phase submersible pump set of different capacity of KSB/ Kirloskar or equivalent make with all accessories & fittings etc including loading unloading and transportation of the pump set to the work site with all required labour, materials, tools and tackles installation, testing & commissioning as per standards specifications and direction of E/I.
| 3 H.P. submersible pump set having discharging capacity 3.35 lps at a total head of 35 meter(approx) (As per work details 4 ) |  |  |  | Nos | 199 | 105000 | 20895000
V | Providing house connection for each house hold including supplying all materials, labours, tools and making ferrule connection with 20 mm dia MDPE and 15mm CPVC Pipes with all fittings etc all complete. (As per work details.- 5)
| Total no of House connection |  |  |  | Each | 16589 | 2600 | 43131400
VI | Providing and erecting 8M high staging with ladder of ISA65x65x6 and 16mm dia MS bar as trade @ 400mm c/c and GI enclosure to house electric switch panel & treatment unit (where required) of suitably designed MS section of angle, channel, etc. as per drawing attached. (As per Work details.- 6A) |  |  |  | Item | 199 | 697000 | 138703000
VII | Installation of Electronically Regulated Doser type chlorinator using Sodium Hypo Chlorite (Hypo NaOCl) (As per Work details.- 7) |  |  |  | Nos | 199 | 23515 | 4679485
VIII | Surveying and levelling using Total Station/DGPS or auto level instruments of the project area including transfer of relevant bench mark to establish the levels of strategic points at the selected position of the T/Well, pumping station & attach the surveying data sheet with design & drawing of pipe line, map of location of HYDT & Steel structure etc. all complete work.
1 | MAHUA | RASULPUR MUBARAK | Ward No | 13 |  | 1.2 | Km
2 | MAHUA | FULWARIYA | Ward No | 4 |  | 1.6 | Km
3 | MAHUA | MADHUL | Ward No | 15 |  | 1.2 | Km
4 | MAHUA | MADHUL | Ward No | 3 |  | 1 | Km
5 | MAHUA | GOVINDPUR | Ward No | 14 |  | 1 | Km
6 | MAHUA | KANULI DHANRAJ | Ward No | 3 |  | 1.2 | Km
7 | MAHUA | JAHAGIRPUR SALKHANNI | Ward No | 5 |  | 1.8 | Km
8 | MAHUA | HASANPUR OSTI | Ward No | 8 |  | 1.65 | Km
9 | MAHUA | HASANPUR OSTI | Ward No | 3 |  | 2.45 | Km
10 | MAHUA | KANHAULI DHANRAJ | Ward No | 2 |  | 2.4 | Km
11 | MAHUA | JAHAGIRPUR SALKHANNI | Ward No | 6 |  | 0.8 | Km
12 | MAHUA | GAUSPUR CHKMJAHID | Ward No | 12 |  | 1.15 | Km
13 | MAHUA | RASULPUR MOBARK | Ward No | 8 |  | 2.15 | Km
14 | MAHUA | SHERPUR MANIKPUR | Ward No | 3&5 |  | 1.25 | Km
15 | MAHUA | TAJPUR BUZURAG | Ward No | 5 |  | 1.65 | Km
16 | MAHUA | RAMPUR CHANDRABHAN URF DAGARU | Ward No | 14 |  | 0.75 | Km
17 | MAHUA | RAMPUR CHANDRABHAN URF DAGARU | Ward No | 11 |  | 1.45 | Km
18 | MAHUA | RAMPUR CHANDRABHAN URF DAGARU | Ward No | 12 |  | 1.35 | Km
19 | MAHUA | SHERPUR MANIKPUR | Ward No | 5 |  | 1.4 | Km
20 | MAHUA | BISUNPUR HIRARAM URF PAHARPUR | Ward No | 7 |  | 1.15 | Km
21 | MAHUA | BISUNPUR HIRARAM URF PAHARPUR | Ward No | 8 |  | 1.85 | Km
22 | MAHUA | MANGURAHI | Ward No | 12 |  | 1.25 | Km
23 | MAHUA | MANGURAHI | Ward No | 1 |  | 1.25 | Km
24 | MAHUA | LAXMINARAYANPUR | Ward No | 3 |  | 1.1 | Km
25 | MAHUA | MIRJANAGAR | Ward No | 4 |  | 0.9 | Km
26 | MAHUA | MIRJANAGAR | Ward No | 2 |  | 1.3 | Km
27 | MAHUA | SAMASPURA | Ward No | 7 |  | 1.2 | Km
28 | CHEHRAKALA | BASTI SARSIKAN | Ward No | 8B |  | 0.79 | Km
29 | CHEHRAKALA | AKHTIYARPUR | Ward No | 14B |  | 0.76 | Km
30 | CHEHRAKALA | RASULPUR FATAH | Ward No | 3B |  | 1.25 | Km
31 | CHEHRAKALA | RASULPUR FATAH | Ward No | 4B |  | 1.2 | Km
32 | CHEHRAKALA | SAHPUR KHURD | Ward No | 4,5 |  | 0.86 | Km
33 | CHEHRAKALA | BASTI SARSIKAN | Ward No | 7 |  | 0.64 | Km |  | 51.4
34 | CHEHRAKALA | BASTI SARSIKAN | Ward No | 14 |  | 0.64 | Km |  | 8.6
35 | CHEHRAKALA | BASTI SARSIKAN | Ward No | 15 |  | 0.655 | Km
36 | CHEHRAKALA | ABABAKARPUR | Ward No | 3 |  | 0.65 | Km
37 | CHEHRAKALA | KARAHATIYA BUZURG | Ward No | 2B |  | 0.635 | Km
38 | CHEHRAKALA | BISUNPUR ARRA | Ward No | 5,7 |  | 0.645 | Km
39 | CHEHRAKALA | BISUNPUR ARRA | Ward No | 8,14 |  | 0.64 | Km
40 | CHEHRAKALA | RASULPUR FATAH | Ward No | 14,12 |  | 0.64 | Km
41 | CHEHRAKALA | RASULPUR FATAH | Ward No | 9 |  | 0.65 | Km
42 | HAJIPUR | Daulatpur Chandi | Ward No | 2 |  | 2.5 | Km
43 | HAJIPUR | Daulatpur Chandi | Ward No | 4 |  | 1.42 | Km
44 | HAJIPUR | Daulatpur Chandi | Ward No | 8 |  | 1.1 | Km
45 | HAJIPUR | Daulatpur Chandi | Ward No | 11 |  | 1.25 | Km
46 | HAJIPUR | Daulatpur Chandi | Ward No | 3 |  | 1.3 | Km
47 | HAJIPUR | Daulatpur Dewariya | Ward No | 5 |  | 1.2 | Km
48 | HAJIPUR | Gadai Sarai | Ward No | 7 |  | 1 | Km
49 | HAJIPUR | Gadai Sarai | Ward No | 8 |  | 0.953 | Km
50 | HAJIPUR | Gadai Sarai | Ward No | 9 |  | 1.05 | Km
51 | HAJIPUR | Gadai Sarai | Ward No | 12 |  | 1.6 | Km
52 | HAJIPUR | Bisunpur Baladhari | Ward No | 5 |  | 1.65 | Km
53 | HAJIPUR | Bisunpur Baladhari | Ward No | 6 |  | 1.55 | Km
54 | HAJIPUR | Bisunpur Baladhari | Ward No | 8 |  | 2.5 | Km
55 | HAJIPUR | Gadai Sarai | Ward No | 11 |  | 1.8 | Km
56 | HAJIPUR | Ismailpur | Ward No | 1&2 |  | 1.75 | Km
57 | HAJIPUR | Ismailpur | Ward No | 3 |  | 1.6 | Km
58 | HAJIPUR | Ismailpur | Ward No | 4 |  | 1.5 | Km
59 | HAJIPUR | Ismailpur | Ward No | 6 |  | 1.5 | Km
60 | HAJIPUR | Ismailpur | Ward No | 15 |  | 1.3 | Km
61 | HAJIPUR | Manua | Ward No | 6 |  | 1.5 | Km
62 | HAJIPUR | Manua | Ward No | 7 |  | 1.55 | Km
63 | HAJIPUR | Manua | Ward No | 8 |  | 2 | Km
64 | HAJIPUR | Thathan Buzurg | Ward No | 13 |  | 1.2 | Km
65 | HAJIPUR | Pahetiya | Ward No | 4 |  | 1.5 | Km
66 | HAJIPUR | Pahetiya | Ward No | 10 |  | 1.4 | Km
67 | HAJIPUR | Pahetiya | Ward No | 5 |  | 1.35 | Km
68 | HAJIPUR | Pahetiya | Ward No | 8 |  | 2.314 | Km
69 | HAJIPUR | Pahetiya | Ward No | 14 |  | 1.5 | Km
70 | HAJIPUR | Afjalpur Dhobaghatti | Ward No | 1 |  | 0.95 | Km
71 | HAJIPUR | Afjalpur Dhobaghatti | Ward No | 7 |  | 2.314 | Km
72 | HAJIPUR | Afjalpur Dhobaghatti | Ward No | 8 |  | 1.25 | Km
73 | HAJIPUR | Afjalpur Dhobaghatti | Ward No | 4 |  | 1.55 | Km
74 | HAJIPUR | Afjalpur Dhobaghatti | Ward No | 11 |  | 1.2 | Km
75 | HAJIPUR | Afjalpur Dhobaghatti | Ward No | 12 & 13 |  | 1.6 | Km
76 | HAJIPUR | Senduari | Ward No | 14 |  | 1.95 | Km
77 | HAJIPUR | Bisunpur Basant | Ward No | 3 |  | 1.5 | Km
78 | HAJIPUR | Bisunpur Basant | Ward No | 4 |  | 1.2 | Km
79 | HAJIPUR | Bisunpur Basant | Ward No | 12 |  | 1.15 | Km
80 | HAJIPUR | Bisunpur Basant | Ward No | 10 |  | 1.6 | Km
81 | HAJIPUR | Bishunpur Basant | Ward No | 14 |  | 2.314 | Km
82 | HAJIPUR | Panapur Langa | Ward No | 1 |  | 1 | Km
83 | HAJIPUR | Panapur Langa | Ward No | 2 |  | 1.15 | Km
84 | HAJIPUR | Panapur Langa | Ward No | 8 |  | 1.8 | Km
85 | HAJIPUR | Panapur Langa | Ward No | 9 |  | 1.7 | Km
86 | HAJIPUR | Chankunda urf Milki | Ward No | 5 |  | 1.75 | Km
87 | HAJIPUR | Chankunda urf Milki | Ward No | 4 |  | 1.45 | Km
88 | HAJIPUR | Chankunda urf Milki | Ward No | 3 |  | 1.55 | Km
89 | HAJIPUR | Kashipur chakbibi | Ward No | 12 |  | 1.35 | Km
90 | HAJIPUR | Kashipur chakbibi | Ward No | 7 |  | 1.45 | Km
91 | HAJIPUR | Kasipur Chakbibi | Ward No | 8 |  | 0.95 | Km
92 | HAJIPUR | Bahuara | Ward No | 1 |  | 1.8 | Km
93 | HAJIPUR | Bahuara | Ward No | 10 |  | 1.8 | Km
94 | HAJIPUR | Bahuara | Ward No | 14 |  | 0.936 | Km
95 | HAJIPUR | Andharbara | Ward No | 2 |  | 0.75 | Km
96 | HAJIPUR | Andharbara | Ward No | 3 |  | 1.4 | Km
97 | HAJIPUR | Andharbara | Ward No | 4 |  | 1.4 | Km
98 | HAJIPUR | Andharbara | Ward No | 9 |  | 1.25 | Km
99 | HAJIPUR | Andharbara | Ward No | 10 |  | 1 | Km
100 | HAJIPUR | Andharbara | Ward No | 11 |  | 1.8 | Km
101 | HAJIPUR | Andharbara | Ward No | 13 |  | 1.6 | Km
102 | HAJIPUR | Hilalpur | Ward No | 1 |  | 1.1 | Km
103 | HAJIPUR | Hilalpur | Ward No | 9 & 10 |  | 1.95 | Km
104 | HAJIPUR | Hilalpur | Ward No | 8 |  | 1.55 | Km
105 | HAJIPUR | Sultanpur | Ward No | 3 |  | 1.35 | Km
106 | HAJIPUR | Sultanpur | Ward No | 9 |  | 1.2 | Km
107 | HAJIPUR | Hilalpur | Ward No | 5 |  | 1.8 | Km
108 | BIDUPUR | Bidupur | Ward No | 12 |  | 1.55 | Km
109 | BIDUPUR | Dilawarpur Govardhan | Ward No | 13,12 |  | 1.15 | Km
110 | BIDUPUR | Sahdulapur Dhobauli | Ward No | 9 |  | 2.15 | Km
111 | BIDUPUR | Sahdulapur Dhobauli | Ward No | 15A |  | 1.25 | Km
112 | BIDUPUR | Amer | Ward No | 8,13 |  | 0.75 | Km
113 | BIDUPUR | Khanpur Pakri | Ward No | 6 |  | 1.45 | Km
114 | BIDUPUR | Kathuliya | Ward No | 7 |  | 1.35 | Km
115 | BIDUPUR | Chakatkurshi | Ward No | 8 |  | 1.4 | Km
116 | BIDUPUR | Saidpur Ganesh | Ward No | 6 |  | 1.85 | Km
117 | BIDUPUR | Mail | Ward No | 12 |  | 1.25 | Km
118 | BIDUPUR | Dilawarpur Govardhan | Ward No | 13 |  | 1.7 | Km
119 | BIDUPUR | Bidupur | Ward No | 10 |  | 1.8 | Km
120 | BIDUPUR | Rahimapur | Ward No | 6&7 |  | 0.95 | Km
121 | BIDUPUR | Kanchanpur | Ward No | 4 |  | 0.955 | Km
122 | BIDUPUR | Rahimapur | Ward No | 9& 10 |  | 1.5 | Km
123 | BIDUPUR | Khanpur Pakri | Ward No | 15&16 |  | 1.5 | Km
124 | BIDUPUR | Kathuliya | Ward No | 11&12 |  | 1.1 | Km
125 | BIDUPUR | Saidpur Ganesh | Ward No | 9B |  | 1 | Km
126 | RAJAPAKAR | JAFARPATTI | Ward No | 10 |  | 1.4 | Km
127 | RAJAPAKAR | BAIKUNTHPUR | Ward No | 7,9 |  | 1.8 | Km
128 | RAJAPAKAR | Bakhari bari | Ward No | 11B, 8 |  | 2.5 | Km
129 | RAJAPAKAR | RAMPUR RATNAKAR | Ward No | 08,11 & 16B |  | 2.5 | Km
130 | RAJAPAKAR | BARAI | Ward No | 9,6 |  | 1.8 | Km
131 | RAJAPAKAR | MIRPUR PATHAD | Ward No | 1,6,5 |  | 2.4 | Km
132 | RAJAPAKAR | BAIKUNTPUR | Ward No | 1,2,11 |  | 2.15 | Km
133 | RAJAPAKAR | Bakarpur | Ward No | 11,13 |  | 1.8 | Km
134 | RAJAPAKAR | Narayanpur Bujurg | Ward No | 11,14 |  | 2.45 | Km
135 | RAJAPAKAR | Jafarpatti | Ward No | 3 |  | 2.4 | Km
136 | RAJAPAKAR | Gauspur | Ward No | 2,4 |  | 2.5 | Km
137 | RAJAPAKAR | Bakarpur | Ward No | 3 |  | 1.42 | Km
138 | RAJAPAKAR | Rajapakar Uttari | Ward No | 3 |  | 1.25 | Km
139 | RAGHOPUR | RUSTAMPUR | Ward No | 4 |  | 0.75 | Km
140 | RAGHOPUR | CHANDPURA | Ward No | 1 |  | 1.65 | Km
141 | RAGHOPUR | CHANDPURA | Ward No | 6 |  | 1.45 | Km
142 | RAGHOPUR | CHANDPURA | Ward No | 11 |  | 1.35 | Km
143 | RAGHOPUR | CHANDPURA | Ward No | 5 |  | 1.4 | Km
144 | RAGHOPUR | RUSTAMPUR | Ward No | 5B,20 |  | 2.4 | Km
145 | RAGHOPUR | JAHAGIRPUR | Ward No | 1 |  | 1.65 | Km
146 | RAGHOPUR | JAHAGIRPUR | Ward No | 7 |  | 1.8 | Km
147 | RAGHOPUR | JAHAGIRPUR | Ward No | 5 |  | 1.65 | Km
148 | RAGHOPUR | JAHAGIRPUR | Ward No | 4 |  | 2.45 | Km
149 | RAGHOPUR | SARAIPUR | Ward No | 5 |  | 2.4 | Km
150 | RAGHOPUR | TERASIYA | Ward No | 11 |  | 1.4 | Km
151 | RAGHOPUR | TERASIYA | Ward No | 12 |  | 1.4 | Km
152 | RAGHOPUR | RAMPUR SHAYAMCHAND | Ward No | 13 |  | 1.15 | Km
153 | RAGHOPUR | RAGHOPUR EAST | Ward No | 7 |  | 1.85 | Km
154 | RAGHOPUR | BAHARAMAPUR | Ward No | 2,3 |  | 1.25 | Km
155 | RAGHOPUR | BAHARAMAPUR | Ward No | 13 |  | 1.25 | Km
156 | RAGHOPUR | BAHARAMAPUR | Ward No | 10 |  | 1.1 | Km
157 | VAISHALI | Amritpur | Ward No | 8 |  | 1.3 | Km
158 | VAISHALI | Majhauli | Ward No | 8 |  | 1.8 | Km
159 | PATEDHI BELSAR | Nagawan | Ward No | 10 |  | 1.8 | Km
160 | PATEDHI BELSAR | Nagawan | Ward No | 1 |  | 1.65 | Km
161 | PATEDHI BELSAR | Sain | Ward No | 1 |  | 2.45 | Km
162 | PATEDHI BELSAR | Sain | Ward No | 4 |  | 2.4 | Km
163 | PATEDHI BELSAR | Sorahattha | Ward No | 1 |  | 2.15 | Km
164 | PATEDHI BELSAR | Manora | Ward No | 13 |  | 1.25 | Km
165 | PATEDHI BELSAR | Mishrauliya | Ward No | 8 |  | 1.4 | Km
166 | PATEDHI BELSAR | Manora | Ward No | 1 |  | 1.85 | Km
167 | PATEDHI BELSAR | Chakgulamuddin | Ward No | 2 |  | 1.25 | Km
168 | PATEDHI BELSAR | Chakgulamuddin | Ward No | 1 |  | 1.1 | Km
169 | PATEDHI BELSAR | Mishrauliya | Ward No | 10 |  | 0.9 | Km
170 | PATEDHI BELSAR | Karneji | Ward No | 5 |  | 1.1 | Km
171 | GORAUL | Katarmala | Ward No | 2 |  | 0.7 | Km
172 | GORAUL | ISMAILPUR | Ward No | 11&12 |  | 1.2 | Km
173 | GORAUL | ISMAILPUR | Ward No | 4B |  | 1.5 | Km
174 | GORAUL | BHUALPUR UF BAHADURPUR | Ward No | 7&8 |  | 0.6 | Km
175 | GORAUL | LODIPUR | Ward No | 6 |  | 2.5 | Km
176 | GORAUL | BAKSAMA | Ward No | 13 |  | 1.42 | Km
177 | LALGANJ | Atwarpur Sisaula | Ward No | 02&03 |  | 1.5 | Km
178 | LALGANJ | Yusufpur | Ward No | 5 |  | 1.65 | Km
179 | LALGANJ | Bhatuli Bhagwan | Ward No | 10,11,12 |  | 1.1 | Km
180 | LALGANJ | Shital Bhakurahar | Ward No | 3 |  | 1.2 | Km
181 | LALGANJ | Yusufpur | Ward No | 3 |  | 1.35 | Km
182 | BHAGWANPUR | Sahmia Rahua | Ward No | 1 |  | 1.8 | Km
183 | BHAGWANPUR | MAGANPUR | Ward No | 6 |  | 1.65 | Km
184 | BHAGWANPUR | SAHTHA | Ward No | 2 |  | 2.45 | Km
185 | SAHDEI BUZURG | Naya Gaow West | Ward No | 11 |  | 1.13 | Km
186 | SAHDEI BUZURG | Sultanpur | Ward No | 9 |  | 1.8 | Km
187 | MAHNAR | Gorigama | Ward No | 9 |  | 1.13 | Km
188 | PATEPUR | Malpur | Ward No | 2 |  | 1.2 | Km
189 | PATEPUR | Govindpur Bela | Ward No | 6 |  | 1.15 | Km
190 | PATEPUR | Harlochanpur Sukki | Ward No | 3 |  | 1.15 | Km
191 | JANDAHA | Mahipura | Ward No | 7 |  | 1.7 | Km
192 | JANDAHA | Said Mohammad Urf Salaha | Ward No | 9 |  | 1.8 | Km
193 | JANDAHA | Chandsarai | Ward No | 12 |  | 0.95 | Km
194 | JANDAHA | Dih Bichauli | Ward No | 8&1 |  | 0.955 | Km
195 | JANDAHA | Khopi | Ward No | 3 |  | 1.5 | Km
196 | JANDAHA | Rasulpur Purushottam | Ward No | 4,5,6 |  | 1.1 | Km
197 | JANDAHA | Laxmipur Barbatta | Ward No | 8 |  | 0.85 | Km
198 | JANDAHA | Harprasad | Ward No | 10 |  | 1.4 | Km
199 | JANDAHA | Harprasad | Ward No | 3 |  | 1.32 | Km
| Total Km = |  |  |  | Per Km | 287.886 | 7500 | 2159145
| TOTAL = | [6 empty] | 454137790.8754
| Add difference of GST (18%-12%) i.e 0.0536 | [6 empty] | 24341785.5909
| TOTAL A = | [6 empty] | 478479576.4663
| Add 1% Contigency upto 1 crore and 0.5% above 1 crore on DB | [6 empty] | 2392397.8823
| SUB TOTAL A | [6 empty] | 480871974.3486
Analysis for (1) Electric Bill, (2) Chlorination & chemical charges in TRC for 3-Months (Including 18% GST )
S.N. | Description |  |  | No.of Schemes | Quantity |  | Rate | Amount
IX | Cost of Applying for Taking Electricity connection including installation of Electric Meter on the scheme. |  |  | 199 | 199 | Nos. | 200 | 39800
X | Cost for Electricity charges for a period of 3 months ( TRC) (As per sub Estimate no.-A-1) @ Rs.2.45/unit [ FOR 3hp] |  |  | 199 | 199 | Nos. | 4860 | 967140
XI | For 2 PPM & 30% Chlorine solution of { Total population served ( say = 400 nos. (avg.) / scheme )} *81*2/1000000)*(100/30)*3months*30* No.of schemes |  |  | 199 | 19.44 | per lit. | 150 | 580284
| SAB TOTAL B = | [6 empty] | 1587224
| GRAND TOTAL | [6 empty] | 482459198.3486
| Say | [6 empty] | 482459198
|  | JE |  | AE |  |  | Executive Engineer
P. H. Division, Hajipur.

## Abstract (2) (hidden)
GOVERNMENT OF BIHAR
Public Health Engineering Department
ABSTRACT OF COST
NAME OF WORK:- CONSTRUCTION OF RURAL PIPED WATER SUPPLY SCHEME FOR THE LEFT OUT HABITATIONS
IN, PANCHAYAT- |  | PAHETIYA |  | UNDER THE WARDS | 02B CHAKBHATANDI |  |  | TOTAL 01 NO
SCHEMES, BLOCK- |  |  | HAJIPUR | OF VAISHALI DISTRICT HAVING | 75 | HOUSE HOLDS & 8 M STEEL STAGING
S.N. | Description |  |  |  | Quantity | Unit | Rate | Total Amount
PART - A
1 | Construction of 150mm X100mmx 125m deep T/W etc. all complete and as per direction of E/I.(As per sub Estimate no.- 1) |  |  |  | 1 | Each | 279342 | 279342
2 | Constructing masonry Chamber 100x100x75 cm inside, in brick work in cement mortar 1:4 (1 cement : 4 coarse sand) for Tube Well, and RCC top slab 1:1.5:3 mix (1 cement : 1.5 coarse sand : 3 graded stone aggregate 20mm nominal size ) , necessary excavation, foundation concrete 1:2:4(1 cement : 2 fine sand : 4 graded stone aggregate 20 mm nominal size) and inside plastering with cement mortar 1:3 (1 cement : 3coarse sand) 12 mm thick with 5% cico fnished with a floating coat of neat cement, out side plastering with cement mortar 1:4 (1 cement : 4coarse sand) 12 mm thick complete as per standard specifications & direction of E/I. (As per sub Estimate no.- 2) |  |  |  | 1 | Each | 14535 | 14535
3 | Providing and Laying Distrbution network of High Density Polyethyene pipe (HDPE pipe) including 10000 liter PVC tank installed at 8M high MS staging etc all complete as per direction of E/I. (As per sub Estimate no.- 3 ) |  |  |  | 1 | Unit | 976399.6088 | 976399.6088
4 | Providing house connection for each house hold including supplying all materials, labours, tools and making ferrule connection with 20 mm dia MDPE and 15mm CPVC Pipes with all fittings etc all complete. (As per sub Estimate no.- 4) |  |  |  | 75 | Each | 2490 | 186750
5 | Provision of safe waste water disposal etc. all complete work. (As per sub Estimate no.- 6) |  |  |  | 0 | Each | 23551 | 0
5 | Providing and erecting 8M high staging with ladder of ISA65x65x6 and 16mm dia MS bar as trade @ 400mm c/c and GI enclosure to house electric switch panel & treatment unit (where required) of suitably designed MS section of angle, channel, etc. as per drawing attached. (As per sub Estimate no.- 5) |  |  |  | 1 | Each | 697000 | 697000
6 | Surveying and levelling using Total Station/DGPS or auto level instruments of the project area including transfer of relevant bench mark to establish the levels of strategic points at the selected position of the T/Well, pumping station & attach the surveying data sheet with design & drawing of pipe line, map of location of HYDT & Steel structure etc. all complete work.As per Direction of E/I |  |  |  | 1.55 | pKM | 7500 | 11625
7 a | Supply Installation, commissioning and testing of single phase 3 H.P submersible pump set having discharging capacity 3.35 lps at a total head of 35 meter(approx) of different capacity of KSB/ Kirloskar or equivalent make with all accessories & fittings etc including loading unloading and transportation of the pump set to the work site with all required labour, materials, tools and tackles installation, testing & commissioning as per standards specifications and direction of E/I. (As per sub Estimate no.- 6A) |  |  |  | 1 | Each | 105000 | 105000
8 | Installation of Electronically Regulated Doser type chlorinator using Sodium Hypo Chlorite (Hypo NaOCl) (As per sub Estimate no.- 7) |  |  |  | 1 | Each | 23515 | 23515 | 2097223.0638
10 | Design, supply, erection, installation, testing and commissioning of Iron removal plant based on aeration/ filteration/ activated carbon treatemnt units or any other suitable treatmnet process of ISO 9001 certified reputed make housed in MS/FRP vessel suitable for required flow rate with iron concentration upto 10 ppm in raw water to deliver treated water quality confirming to IS 10500( latest revision) including all necessary civil works, accessories,taxes and duties etc. all complete as per directions of Engineer-in-Charge.
| 8 KLPH Capacity(As per sub Estimate no.- 9A) |  |  |  | 0 | Each | 489605 | 0
| 12 KLPH Capacity(As per sub Estimate no.- 9B) |  |  |  | 0 | Each | 545245 | 0
| 16 KLPH Capacity(As per sub Estimate no.- 9C) |  |  |  | 0 | Each | 600880 | 0
| Total | [6 empty] | 2294166.6088
| For additional 6% GST to make 18% GST Instead of 12% (Multiplying By 0.0536 of A) | [6 empty] | 122967.3302
| Sub Total = | [6 empty] | 2417133.939
| Add 1% Contigency on DB | [6 empty] | 24171.3394
Grand Total= | [7 empty] | 2441305.2784
Say= | [7 empty] | 2441305
Executive Engineer,
P. H. Division, Hajipur.

## Cover (hidden)
NAME OF WORK:- CONSTRUCTION OF RURAL PIPED WATER SUPPLY SCHEME FOR
IN, PANCHAYAT- |  | PAHETIYA | UNDER THE WARDS |  | 02B CHAKBHATANDI
TOTAL 01 NO SCHEMES, BLOCK- |  |  |  | HAJIPUR | OF VAISHALI DISTRICT
HAVING | 75 | HOUSE HOLDS & 8 MTR. STEEL STAGING
|  | Block | :- | HAJIPUR
|  | Panchayat | :- | PAHETIYA
| Habitation |  | :- | CHAKBHATANDI
| No of Schemes |  | :- | 1 |  | HAJIPUR PAHETIYA 02B CHAKBHATANDI
| Estimated Cost |  | Rs | 24.4131 | Lacs
Year : 2024 - 25
UNDER
P.H DIVISION HAJIPUR
GOVERNMENT OF BIHAR
fcgkj ljdkj
PUBLIC HEALTH ENGINEERING DEPARTMENT
P.H. DIVISION, HAJIPUR
ESTIMATE FOR TECHNICAL APPROVAL

## Report (hidden)
GOVERNMENT OF BIHAR PUBLIC HEALTH ENGINEERING DEPARTMENT PUBLIC HEALTH DIVISION, HAJIPUR.
NAME OF WORK:- CONSTRUCTION OF RURAL PIPED WATER SUPPLY SCHEME FOR THE LEFT OUT
HABITATIONS OF PRD IN, PANCHAYAT- |  |  | PAHETIYA |  | UNDER THE WARDS |  |  | 02B CHAKBHATANDI
TOTAL 01 NO'S SCHEMES, BLOCK - |  |  |  | HAJIPUR |  | OF VAISHALI DISTRICT HAVING |  |  | 75
HOUSE HOLDS WITH & 8 MTR. STEEL STAGING
REPORT
This estimate has been framed by Executive Engineer, P.H. Division, Hajpur for construction of rural piped water
Supply Scheme in Leftout Habitations of Panchayat- |  |  |  |  | PAHETIYA |  | A Total of 1 No of Schems are
included in this Estimate under the panchayat, Block- |  |  |  |  | HAJIPUR |  | This estimate has been framed as per
guideline of “Har Ghar Nal Ka Jal”and as per direction of Engineer in Chief-cum-Special Secretary, P.H.E.D., Bihar,
Patna vide his No.- 14@fo01&103@2024&156 Dated 25-07-2024 .for the habitations of Vaishali district under
P.H Division, Hajipur .This is PRD Ward.
Below said habitations are situated either far away from the source of nearest existing water supply schemes or
obstructed through rivers/depressions/railway lines/NH etc. Hence there is a need of one Piped Water Supply Scheme
for saturation of each of the habitations. We have made provision of T/well, Motor pump, Steel Structure, Distrubtion
of pipe line, house connection etc. in the estimate.
Details provision made for this habitation with proposed house connection is as tabulated below : -
Sl. No. | Block | Panchayat | Proposed T/well | Ward no. Covered | House Hold Covered | Proposed length of diff. dia. Pipe line |  |  | Estimated Cost (in lacs)
1 | HAJIPUR | PAHETIYA | 1 | 1 | 75 | Dia mm | Length (m) | Rate
[6 empty] | 110 | 0 | 646.25
[6 empty] | 90 | 150 | 437.96 | 24.4131
[6 empty] | 75 | 300 | 306.31
[6 empty] | 63 | 400 | 218.62
[6 empty] | 50 | 350 | 116.25
[6 empty] | 40 | 350 | 76.53
[6 empty] | Total | 1550
Specification :- The standard specification of P.H.E.D. and PWD will be followed during the Execution of work
Time of completion: - This work will be completed in six (6)month after the fund is made available.
Estimated | cost :The estimated cost |  |  |  | 24.4131 | Lacs
Executive Engineer,
P. H. Division, Hajipur.

## Quantity (hidden)
P. H. DIVISION, HAJIPUR
WORK DETAIL Of Quantity For Distribution System
DETAILS OF Pipeline Distribution System Of Different Schemes
Sl. No. | Ward No | Scheme Name | Different Size Of HDPE pipe (In Mtrs.) | [6 empty] | PVC Tank in Liter | Brass gate valve with C.I. wheel |  |  | Nos. of connections
|  |  | 110 mm | 90 mm | 75 mm | 63 mm | 50 mm | 40 mm | Total |  | 80 mm | 65 mm | 50 mm
1 | 02B | 02B CHAKBHATANDI | 0 | 150 | 250 | 250 | 200 | 150 | 1000 | 10000 | 2 | 2 | 1 | 75 |  |  | ( | )
| Total |  | 0 | 150 | 250 | 250 | 200 | 150 | 1000 | 10000 | 2 | 2 | 1 | 75
item No 7 | Providing and fixing G.I.Pipes complete with G.I. Fittings including trenching and refilling etc | [8 empty] | No Of Scheme | Quantity |  | Unit | Total
7.1 | 50mm dia G.I.Pipe from T/well to PVC Tank | [8 empty] | 1 | 14 | m | P/M | 14
7.2 | 80mm dia G.I.Pipe from PVC Tank to Distribution main | [8 empty] | 1 | 14 | m | P/M | 14 | Districk | VAISHALI
7.3 | 65mm dia G.I.Pipe for wash out | [8 empty] | 1 | 12 | m | P/M | 12 | Block | HAJIPUR
[15 empty] | Panchayat | PAHETIYA
Item No 12 | G.I pipe for using as filling station | [8 empty] | No Of Scheme | Quantity |  | Unit | Total | Habitation | CHAKBHATANDI
| 50mm dia. Pipe from distribution main | [8 empty] | 1 | 3.5 | m | p/m | 3.5
| Providing and fixing G.I fittings | [8 empty] | 1 | 1 | each | Each | 1
| 80mmx80mmx50mm dia Tee | [8 empty] | 1 | 3 | each | Each | 3
| 50mm dia bend | [8 empty] | 1 | 1 | each | Each | 1
Item No 13 | Providing and fixing PTMT extension nipple for water tank pipe, fittings of approved quality and colour. | [8 empty] | No Of Scheme | Quantity |  | Unit | Total
13.1 | 50mm dia | [8 empty] | 1 | 2 | No's | Each | 2
13.2 | 63mm dia | [8 empty] | 1 | 1 | No's | Each | 1
13.3 | 80 mm dia | [8 empty] | 1 | 1 | No's | Each | 1
Executive Engineer
P. H. Division, Hajipur.

## Quantityof IRP MOTOR (hidden)
P. H. DIVISION, HAJIPUR
WORK DETAIL Of Quantity For Population Forcast Motor Pump Design
DETAILS OF Motor pump Of Different Schemes
Sl. No. | Ward No | Scheme Name | Different Size of Iron Treatment Unit Required in Schemes |  |  | Motor Pump Required
|  |  | 16KLPH | 12KLPH | 8KLPH | 2HP | 3HP
1 | 02B | 02B CHAKBHATANDI | 0 | 0 | 0 | 0 | 1
| Total |  | 0 | 0 | 0 | 0 | 1
Executive Engineer
P. H. Division, Hajipur.

## Motor Design (hidden)
DESIGN OF MOTOR PUMP
1 | #REF! | #REF! | #REF! | PAHETIYA | Scheme | 02B CHAKBHATANDI
Water demand in Intermediate year | [6 empty] | 40.2887 | KLD
Duration of Pumping | [6 empty] | 8 | Hrs.
Hence the rate of pumping | [6 empty] | 5.0361 | Kl/Hr
[7 empty] | 0.0013989 | Kl/Sec
[7 empty] | 1.3989 | LPS
Now calculation of Head
| (a) | Sub Soil Water Level |  |  |  |  | 11 | M
| (b) | Draw down created during pumping |  |  |  |  | 2 | M
| (c) | Frictional Loss in pipe and Treatment Unit |  |  |  |  | 5 | M
| (d) | Residual Head required to the pump |  |  |  |  | 12 | M
[7 empty] | 30 | M
Taking efficiency of Motor Pump --- 80%
|  | B.H.P. of Motor Pump |  | = | WQH
75 n
|  |  |  | = | 1.3989 | x | 30
[5 empty] | 75 | x | 0.7
[5 empty] | 0.79938 | HP
|  |  |  | Say | 2 | HP
| Considering life of Motor Pump :- |  |  |  | 15 Years
| Hence one no. of Subemersible Pump of |  |  |  | 2 | H.P.
| For Discharging |  | 1.3989 | LPS
| Capacity acting against a total head of |  |  | 30 | M Head
will be provide in both the present and intermediate stage.
| Hence we shall provide one nos |  |  | 2 | H.P. Submersible Pump
Executive Engineer P.H. Division, Hajipur

## IRP DESIGN (hidden)
CALCULATION OF CAPACITY OF IRON TREATMENT PLANT
1 | #REF! | #REF! | #REF! | PAHETIYA |  | Scheme | 02B CHAKBHATANDI
As per CPHEEO monual on Water Supply and Treatment published by the Ministry of Urban Development Department, Government of India in May 1999, the design period of Water Treatment Unit is 15 years only.
Hence, Capacity of proposed Iron Treatment Plant (IRP) has been calculated for Intermediate Year requirement.
| In Intermediate year Water Demand |  |  | = | 0.040289 | MLD
| Pumping Hour |  |  | = | 8 | Hours
|  |  |  | = | 0.040289 | x 103 | KL
|  |  |  | = | 40.2887 | /8
|  |  |  | = | 5.0361 | KLPH
|  |  |  | Say: | 8 | KLPH
|  |  | Hence, | 8 | KLPH | Capacity of IRP may be provided
Executive Engineer P.H. Division, Hajipur

## Energy Charge (hidden)
Sub Estimate No.-10B
COST OF ENERGY CHARGES
1 | Cost of Energy charges
| HP of pump =3HP |  | 3
| 3 | HP | = | 2.238 | KW
| Oprating Hour Average running |  |  | 6 | Hours/Day
| Unit Expenditure per year |  |  | 5440.3542 | Unit
| Energy Charges @ |  |  | 8.31 | per Unit | 45209.3434
| Fixed charges (3HPx100x365/30) |  | 1 | 100 | Per HP per month | 3650 | 3650
| Duty charges @ 6% of energy charges |  |  |  |  | 2712.5606
| Total |  |  |  |  | 0
2 | Cost of Energy charges
| HP of pump =2HP |  | 2
| 2 | HP | = | 1.492 | KW
| Oprating Hour Average running |  |  | 6 | Hours/Day
| Unit Expenditure per year |  |  | 3626.9028 | Unit
| Energy Charges @ |  |  | 8.31 | per Unit | 30139.5623
| Fixed charges (2HPx100x365/30) |  | 1 | 100 | Per HP per month | 2433.3333
| Duty charges @ 6% of energy charges |  |  |  |  | 1808.3737
| Total |  |  |  |  | 0
Executive Engineer
P.H. Division, Hajipur

## Boring (hidden)
Sub Estimate no.- 1
CONSTRUCTION OF 150MM X 100MM DIA & 125M DEEP TUBE WELL
S.No. | Description | Qty. |  | Unit | Rate | Amount
1 | Boring/drilling bore well of required dia for casing/strainer pipe, by suitable method prescribed in IS: 2800 (part I), including collecting samples from different strata, preparing and submitting strata chart/ bore log, including hire & running charges of all equipments, tools, plants & machineries required for the job, all complete as per direction of Engineer -in-charge, upto 90 metre depth below ground level. (All types of soil)
24.1.1.2 | (a) 350mm dia bore from G.L. to 30.0M | 30 | M | P/M | 532.4 | 15972
24.1.1.1 | (b) 300mm dia bore from 30.0 m to 60.0M | 30 | M | P/M | 486.8 | 14604
| (c) 300mm dia bore from 60M to 90.0M | 30 | M | P/M | 486.8 | 14604
24.2.1 | (d) 300mm dia bore from 90.0M to 150.0M | 35 | M | P/M | 567.9 | 19876.5
2A | Supplying, assembling, lowering and fixing in vertical position in bore well, unplasticized PVC (UPVC) medium well casing (CM) pipe of required dia, conforming to IS: 12818, including required hire and labour charges, fittings & accessories etc. all complete, for all depths, as per direction of Engineer -in-charge.
24.3.2 | (a) 150 mm nominal size dia | 30 | M | P/M | 660.1 | 19803 | 246165 | 1969.32 | 177238.8
24.3.1 | (b) 100 mm nominal size dia | 60 | M | P/M | 546.1 | 32766
2B | Supplying, assembling, lowering and fixing in vertical position in bore well unplasticized PVC (UPVC) medium well screen (RMS) pipes with ribs, conforming to IS: 12818, including hire & labour charges, fittings & accessories etc. all complete, for all depths, as per direction of Engineer-in-charge.
24.4.1 | 100 mm nominal size dia | 30 | M | P/M | 573.1 | 17193
3 | Supplying the following fittings & fixing the same in position as per approved lowering assembly and strata chart including providing all equipments and welding the same on process of lowering the assay etc. all complete as per S/D of E/I.
24.13.2 | (a) 150 mm dia well cap | 1 | No. | Each | 210.7 | 210.7
24.14.2 | (b) 150 mm dia M.S. Clamp 1.6 M long (one Pair) | 1 | No. | Each | 1531.4 | 1531.4
| (c) 150 mm dia center guide | 4 | Nos. | Each | 150 | 600
| (d) 100 mm dia center guide | 6 | Nos. | Each | 100 | 600
| (e) 150 mm x 100 mm dia 6mm wall thickness MS reducer | 1 | No. | Each | 500 | 500
24.15.1 | (f) 100mm dia & 6mm thick M.S. well shoe plug | 1 | No. | Each | 228.3 | 228.3
4a 24.6 | Providing all materials, labours, & equipments for fixing tube well with pea gravel of Dalbhumigarh to size 4mm to 8mm approx. as suitable for strata including carriage washing, placing and packing the same in position around the tube well etc. all complete as per direction of E/I. | 9 | M3 | P/M3 | 1343.2 | 12088.8
4b | Carriage of Pea Gravel from Dhalbhumigarh (taken av distance 400km.) | 9 | M3 | P/M3 | 0 | 0
5 24.12 | Development of tube well in accordance with IS : 2800 (part I) and IS: 11189, to establish maximum rate of usable water yield without sand content (beyond permissible limit), with required capacity air compressor, running the compressor for required time till well is fully develo ped, measuring yield of well by "V" notch method or any other approved method, measuring static level & draw down etc. by step draw down method, collecting water sampl &getting tested in approved laboratory, disinfection of tubewell, all complete,including hire & labour charges of air compressor, tools & accessories etc., all as per requirement and direction of Engineer-in-charge. | 24 | Hrs. | P/H | 916.8 | 22003.2
6 | Transportation of drilling plants, developing equipments & all other required tools and M/c by and suitable mechanical means including all cost of loading, unloading, placing at work site and back after completion of work as per S/D of E/I | 1 | No. | Each | 9200 | 9200
7 | Supplying all materials and labours for arrangement for additional water required during the drilling period for 70 Hrs & site clearance & leveling etc. And providing the soap duster etc. to staff engaged in drilling etc. all complete work as per specification & direction of E.I. | 1 | No. | Each | 7000 | 7000
| TOTAL |  |  |  |  | 0
| Say |  |  |  |  | 0 |  |  | #REF!
188780.9
Executive Engineer,
P. H. Division, Hajipur.

## Abstract (hidden)
GOVERNMENT OF BIHAR
Public Health Engineering Department
ABSTRACT OF COST
NAME OF WORK:- CONSTRUCTION OF RURAL PIPED WATER SUPPLY SCHEME FOR THE LEFT OUT HABITATIONS
IN, PANCHAYAT- |  | PAHETIYA |  | UNDER THE WARDS | 02B CHAKBHATANDI |  |  | TOTAL 01 NO
SCHEMES, BLOCK- |  |  | HAJIPUR | OF VAISHALI DISTRICT HAVING | 75 | HOUSE HOLDS & 8 M STEEL STAGING
S.N. | Description |  |  |  | Quantity | Unit | Rate | Total Amount
PART - A
1 | Construction of 150mm X100mmx 125m deep T/W etc. all complete and as per direction of E/I.(As per sub Estimate no.- 1) |  |  |  | 1 | Each | 279342 | 279342
2 | Constructing masonry Chamber 100x100x75 cm inside, in brick work in cement mortar 1:4 (1 cement : 4 coarse sand) for Tube Well, and RCC top slab 1:1.5:3 mix (1 cement : 1.5 coarse sand : 3 graded stone aggregate 20mm nominal size ) , necessary excavation, foundation concrete 1:2:4(1 cement : 2 fine sand : 4 graded stone aggregate 20 mm nominal size) and inside plastering with cement mortar 1:3 (1 cement : 3coarse sand) 12 mm thick with 5% cico fnished with a floating coat of neat cement, out side plastering with cement mortar 1:4 (1 cement : 4coarse sand) 12 mm thick complete as per standard specifications & direction of E/I. (As per sub Estimate no.- 2) |  |  |  | 1 | Each | 14535 | 14535
3 | Providing and Laying Distrbution network of High Density Polyethyene pipe (HDPE pipe) including 10000 liter PVC tank installed at 8M high MS staging etc all complete as per direction of E/I. (As per sub Estimate no.- 3 ) |  |  |  | 1 | Unit | 976399.6088 | 976399.6088
4 | Providing house connection for each house hold including supplying all materials, labours, tools and making ferrule connection with 20 mm dia MDPE and 15mm CPVC Pipes with all fittings etc all complete. (As per sub Estimate no.- 4) |  |  |  | 75 | Each | 2490 | 186750
5 | Provision of safe waste water disposal etc. all complete work. (As per sub Estimate no.- 6) |  |  |  | 0 | Each | 23551 | 0
5 | Providing and erecting 8M high staging with ladder of ISA65x65x6 and 16mm dia MS bar as trade @ 400mm c/c and GI enclosure to house electric switch panel & treatment unit (where required) of suitably designed MS section of angle, channel, etc. as per drawing attached. (As per sub Estimate no.- 5) |  |  |  | 1 | Each | 697000 | 697000
6 | Surveying and levelling using Total Station/DGPS or auto level instruments of the project area including transfer of relevant bench mark to establish the levels of strategic points at the selected position of the T/Well, pumping station & attach the surveying data sheet with design & drawing of pipe line, map of location of HYDT & Steel structure etc. all complete work.As per Direction of E/I |  |  |  | 1.55 | pKM | 7500 | 11625
7 a | Supply Installation, commissioning and testing of single phase 3 H.P submersible pump set having discharging capacity 3.35 lps at a total head of 35 meter(approx) of different capacity of KSB/ Kirloskar or equivalent make with all accessories & fittings etc including loading unloading and transportation of the pump set to the work site with all required labour, materials, tools and tackles installation, testing & commissioning as per standards specifications and direction of E/I. (As per sub Estimate no.- 6A) |  |  |  | 1 | Each | 105000 | 105000
8 | Installation of Electronically Regulated Doser type chlorinator using Sodium Hypo Chlorite (Hypo NaOCl) (As per sub Estimate no.- 7) |  |  |  | 1 | Each | 23515 | 23515 | 2097223.0638
10 | Design, supply, erection, installation, testing and commissioning of Iron removal plant based on aeration/ filteration/ activated carbon treatemnt units or any other suitable treatmnet process of ISO 9001 certified reputed make housed in MS/FRP vessel suitable for required flow rate with iron concentration upto 10 ppm in raw water to deliver treated water quality confirming to IS 10500( latest revision) including all necessary civil works, accessories,taxes and duties etc. all complete as per directions of Engineer-in-Charge.
| 8 KLPH Capacity(As per sub Estimate no.- 9A) |  |  |  | 0 | Each | 489605 | 0
| 12 KLPH Capacity(As per sub Estimate no.- 9B) |  |  |  | 0 | Each | 545245 | 0
| 16 KLPH Capacity(As per sub Estimate no.- 9C) |  |  |  | 0 | Each | 600880 | 0
| Total | [6 empty] | 2294166.6088
| For additional 6% GST to make 18% GST Instead of 12% (Multiplying By 0.0536 of A) | [6 empty] | 122967.3302
| Sub Total = | [6 empty] | 2417133.939
| Add 1% Contigency on DB | [6 empty] | 24171.3394
Grand Total= | [7 empty] | 2441305.2784
Say= | [7 empty] | 2441305
Executive Engineer,
P. H. Division, Hajipur.

## COM Quantity .
yksd LokLF; iz'kk[k] gkthiqj
PRD NqVk gqvk Vksyk u;k ;kstuk fy;s tkus fd vko';drk
P. H. DIVISION, HAJIPUR
WORK DETAIL Of Quantity For Distribution System
DETAILS OF Pipeline Distribution System Of Different Schemes
Sl. No. | BLOCK | PANCHYAT | WARD NO. |  | Nos. of connections | Different Size Of HDPE pipe (In Mtrs.) | [5 empty] | Distribution Cost | Estimating Cost
|  |  |  | Habitation |  | 90mm | 75mm | 63mm | 50mm | 40mm | Total
1 | MAHUA | RASULPUR MUBARAK | 13 |  | 55 | 150 | 300 | 300 | 250 | 200 | 1200 | 824719.2378 | 2238523.4282 | 1.2
2 | MAHUA | FULWARIYA | 4 |  | 150 | 100 | 300 | 350 | 450 | 400 | 1600 | 971546.5924 | 2660801.7019 | 1.6
3 | MAHUA | MADHUL | 15 |  | 80 | 100 | 200 | 200 | 300 | 400 | 1200 | 768783.1128 | 2248168.6238 | 1.2
4 | MAHUA | MADHUL | 3 |  | 60 | 100 | 170 | 150 | 250 | 330 | 1000 | 676999.2655 | 2093566.8517 | 1
5 | MAHUA | GOVINDPUR | 14 |  | 60 | 100 | 200 | 150 | 250 | 300 | 1000 | 684237.3355 | 2101269.1426 | 1
6 | MAHUA | KANULI DHANRAJ | 3 |  | 40 | 100 | 200 | 200 | 300 | 400 | 1200 | 768783.1128 | 2137498.4798 | 1.2
7 | MAHUA | JAHAGIRPUR SALKHANNI | 5 | PASWAN TOLA | 100 | 200 | 400 | 250 | 450 | 500 | 1800 | 1093704.9446 | 2654053.3263 | 1.8
8 | MAHUA | HASANPUR OSTI | 8 | RAM TOLA | 100 | 300 | 250 | 250 | 450 | 400 | 1650 | 1039214.1804 | 2594870.5894 | 1.65
9 | MAHUA | HASANPUR OSTI | 3 | MUSLIM TOLA | 65 | 350 | 400 | 400 | 800 | 500 | 2450 | 1431358.8896 | 2921714.3316 | 2.45
10 | MAHUA | KANHAULI DHANRAJ | 2 | RAM TOLA | 95 | 350 | 400 | 500 | 600 | 550 | 2400 | 1419186.9515 | 2991365.2911 | 2.4
11 | MAHUA | JAHAGIRPUR SALKHANNI | 6 | RAM TOLA | 70 | 100 | 300 | 200 | 100 | 100 | 800 | 634567.3082 | 2074484.8104 | 0.8
12 | MAHUA | GAUSPUR CHKMJAHID | 12 | SHARMA TOLA | 90 | 150 | 100 | 100 | 400 | 400 | 1150 | 734132.2497 | 2238563.878 | 1.15
13 | MAHUA | RASULPUR MOBARK | 8 | MUSLIM TOLA | 80 | 200 | 350 | 300 | 700 | 600 | 2150 | 1230779.0361 | 2747377.0867 | 2.15
14 | MAHUA | SHERPUR MANIKPUR | 3&5 | PASWAN TOLA | 70 | 250 | 500 | 200 | 200 | 100 | 1250 | 912668.6259 | 2374013.8932 | 1.25
15 | MAHUA | TAJPUR BUZURAG | 5 | PASWAN TOLA | 50 | 250 | 200 | 500 | 500 | 200 | 1650 | 1047559.5804 | 2465413.55 | 1.65
16 | MAHUA | RAMPUR CHANDRABHAN URF DAGARU | 14 | YADAV TOLA | 80 | 150 | 200 | 200 | 100 | 100 | 750 | 610665.2952 | 2076318.3029 | 0.75
17 | MAHUA | RAMPUR CHANDRABHAN URF DAGARU | 11 | PASWAN TOLA | 70 | 100 | 500 | 500 | 250 | 100 | 1450 | 977587.8032 | 2444692.9308 | 1.45
18 | MAHUA | RAMPUR CHANDRABHAN URF DAGARU | 12 | GIRI TOLA | 80 | 250 | 300 | 300 | 250 | 250 | 1350 | 918919.952 | 2409131.7924 | 1.35
19 | MAHUA | SHERPUR MANIKPUR | 5 | NUNIYA TOLA | 60 | 300 | 250 | 250 | 300 | 300 | 1400 | 939207.3401 | 2375784.3114 | 1.4
20 | MAHUA | BISUNPUR HIRARAM URF PAHARPUR | 7 | PASWAN TOLA | 60 | 200 | 300 | 250 | 200 | 200 | 1150 | 815399.0997 | 2242040.2507 | 1.15
21 | MAHUA | BISUNPUR HIRARAM URF PAHARPUR | 8 | SHARMA TOLA | 60 | 350 | 400 | 500 | 350 | 250 | 1850 | 1202508.3827 | 2659563.8887 | 1.85
22 | MAHUA | MANGURAHI | 12 | YADAV TOLA | 30 | 200 | 200 | 250 | 300 | 300 | 1250 | 832943.1759 | 832943.1759 | 1.25
23 | MAHUA | MANGURAHI | 1 | PASWAN TOLA | 60 | 150 | 200 | 200 | 300 | 400 | 1250 | 806508.3759 | 2233377.4134 | 1.25
24 | MAHUA | LAXMINARAYANPUR | 3 | YADAV TOLA | 60 | 200 | 400 | 100 | 100 | 300 | 1100 | 794226.0367 | 2219110.1811 | 1.1
25 | MAHUA | MIRJANAGAR | 4 | KUSHWAHA TOLA | 60 | 150 | 200 | 150 | 200 | 200 | 900 | 663626.7344 | 2078538.5579 | 0.9
26 | MAHUA | MIRJANAGAR | 2 | YADAV TOLA | 60 | 200 | 300 | 250 | 250 | 300 | 1300 | 873734.9639 | 2305314.6969 | 1.3
27 | MAHUA | SAMASPURA | 7 | PASWAN TOLA | 100 | 250 | 300 | 250 | 200 | 200 | 1200 | 881194.6889 | 2230250.2508 | 1.2
28 | CHEHRAKALA | BASTI SARSIKAN | 8B |  | 45 | 90 | 150 | 100 | 250 | 200 | 790 | 582168.3556 | 1949476.5484 | 0.79
29 | CHEHRAKALA | AKHTIYARPUR | 14B |  | 40 | 90 | 100 | 120 | 250 | 200 | 760 | 561838.6828 | 1913769.8131 | 0.76
30 | CHEHRAKALA | RASULPUR FATAH | 3B |  | 70 | 100 | 200 | 300 | 350 | 300 | 1250 | 804538.0509 | 2258948.2556 | 1.25
31 | CHEHRAKALA | RASULPUR FATAH | 4B |  | 80 | 100 | 220 | 330 | 300 | 250 | 1200 | 793003.7778 | 2273942.7054 | 1.2
32 | CHEHRAKALA | SAHPUR KHURD | 4,5 |  | 60 | 90 | 180 | 210 | 180 | 200 | 860 | 629148.6639 | 2041529.9612 | 0.86
33 | CHEHRAKALA | BASTI SARSIKAN | 7 |  | 55 | 70 | 100 | 120 | 250 | 100 | 640 | 509248.2014 | 1898349.9702 | 0.64
34 | CHEHRAKALA | BASTI SARSIKAN | 14 |  | 37 | 70 | 100 | 120 | 250 | 100 | 640 | 509248.2014 | 1848548.4054 | 0.64
35 | CHEHRAKALA | BASTI SARSIKAN | 15 |  | 47 | 75 | 100 | 130 | 250 | 100 | 655 | 518262.7103 | 1885928.3201 | 0.655
36 | CHEHRAKALA | ABABAKARPUR | 3 |  | 42 | 80 | 100 | 120 | 250 | 100 | 650 | 516793.254 | 1870490.9457 | 0.65 | BASTI SARSIKAN | 9
37 | CHEHRAKALA | KARAHATIYA BUZURG | 2B |  | 32 | 75 | 100 | 110 | 250 | 100 | 635 | 507778.7451 | 1833111.0309 | 0.635
38 | CHEHRAKALA | BISUNPUR ARRA | 5,7 |  | 48 | 75 | 100 | 120 | 250 | 100 | 645 | 513020.7277 | 1883037.0811 | 0.645
39 | CHEHRAKALA | BISUNPUR ARRA | 8,14 |  | 28 | 80 | 100 | 110 | 250 | 100 | 640 | 511551.2714 | 1826098.4027 | 0.64 | BISUNPUR ARRA | 13
40 | CHEHRAKALA | RASULPUR FATAH | 14,12 |  | 45 | 70 | 100 | 120 | 250 | 100 | 640 | 509248.2014 | 1870682.4342 | 0.64
41 | CHEHRAKALA | RASULPUR FATAH | 9 |  | 38 | 70 | 100 | 130 | 250 | 100 | 650 | 514490.184 | 1856973.1516 | 0.65 | CHHAURAHI | 11B
42 | HAJIPUR | Daulatpur Chandi | 2 | Paswan Tola | 105 | 300 | 700 | 600 | 500 | 400 | 2500 | 1520841.8026 | 3128005.5158 | 2.5
43 | HAJIPUR | Daulatpur Chandi | 4 | Mahto Tola | 65 | 150 | 300 | 370 | 350 | 250 | 1420 | 921834.2803 | 2371290.4014 | 1.42
44 | HAJIPUR | Daulatpur Chandi | 8 | Yadav Tola | 60 | 150 | 300 | 300 | 200 | 150 | 1100 | 785133.5617 | 2209434.5511 | 1.1
45 | HAJIPUR | Daulatpur Chandi | 11 | Kumhar Tola | 50 | 150 | 350 | 350 | 250 | 150 | 1250 | 862992.6009 | 2265816.7746 | 1.25
46 | HAJIPUR | Daulatpur Chandi | 3 | Bhumiyar Tola | 100 | 150 | 300 | 300 | 300 | 250 | 1300 | 864304.9139 | 2405949.9852 | 1.3
47 | HAJIPUR | Daulatpur Dewariya | 5 | Yadav Tola | 55 | 150 | 300 | 300 | 250 | 200 | 1200 | 824719.2378 | 2238523.4282 | 1.2
48 | HAJIPUR | Gadai Sarai | 7 | Yadav Tola | 95 | 150 | 250 | 250 | 200 | 150 | 1000 | 728110.0105 | 2244792.0115 | 1
49 | HAJIPUR | Gadai Sarai | 8 | Yadav Tola | 60 | 100 | 250 | 303 | 150 | 150 | 953 | 697133 | 2147955.6355 | 1
50 | HAJIPUR | Gadai Sarai | 9 | Yadav Tola | 45 | 150 | 300 | 250 | 200 | 150 | 1050 | 758923.6486 | 2139643.284 | 1.05
51 | HAJIPUR | Gadai Sarai | 12 | Paswan Tola | 95 | 200 | 400 | 500 | 250 | 250 | 1600 | 1047661.6174 | 2589626.9922 | 1.6
52 | HAJIPUR | Bisunpur Baladhari | 5 | Paswan Tola | 120 | 200 | 400 | 400 | 350 | 300 | 1650 | 1055662.9554 | 2667709.3951 | 1.65
53 | HAJIPUR | Bisunpur Baladhari | 6 | Hajam Tola | 45 | 150 | 350 | 300 | 400 | 350 | 1550 | 974289.9043 | 2372812.7799 | 1.55
54 | HAJIPUR | Bisunpur Baladhari | 8 | Yadav Tola | 105 | 300 | 700 | 600 | 500 | 400 | 2500 | 1520841.8026 | 3128005.5158 | 2.5
55 | HAJIPUR | Gadai Sarai | 11 | Yadav Tola | 115 | 200 | 400 | 500 | 400 | 300 | 1800 | 1128918.2696 | 2733026.3971 | 1.8
56 | HAJIPUR | Ismailpur | 1&2 | Paswan Tola | 160 | 200 | 500 | 400 | 350 | 300 | 1750 | 1117290.2316 | 2844757.4442 | 1.75
57 | HAJIPUR | Ismailpur | 3 | Teli Tola | 55 | 200 | 300 | 300 | 400 | 400 | 1600 | 999951.7174 | 2428187.026 | 1.6
58 | HAJIPUR | Ismailpur | 4 | Yadav Tola | 45 | 150 | 300 | 350 | 400 | 300 | 1500 | 950935.9912 | 2347561.9893 | 1.5
59 | HAJIPUR | Ismailpur | 6 | Paswan Tola | 50 | 150 | 300 | 350 | 400 | 300 | 1500 | 950935.9912 | 2361395.7573 | 1.5
60 | HAJIPUR | Ismailpur | 15 | Bhumiyar Tola | 100 | 150 | 300 | 300 | 300 | 250 | 1300 | 864304.9139 | 2405949.9852 | 1.3
61 | HAJIPUR | Manua | 6 | KOIRI TOLA | 85 | 200 | 350 | 350 | 300 | 300 | 1500 | 977803.9162 | 2486823.2595 | 1.5
62 | HAJIPUR | Manua | 7 | Ravidas tola | 155 | 150 | 300 | 350 | 400 | 350 | 1550 | 969686.1793 | 2672256.6864 | 1.55
63 | HAJIPUR | Manua | 8 | Ravidas tola | 75 | 200 | 400 | 450 | 500 | 450 | 2000 | 1200629.8969 | 2700263.3813 | 2
64 | HAJIPUR | Thathan Buzurg | 13 | PASWAN TOLA | 65 | 150 | 350 | 350 | 200 | 150 | 1200 | 842157.1128 | 2284747.2347 | 1.2
65 | HAJIPUR | Pahetiya | 4 | Sahani Tola | 145 | 200 | 400 | 400 | 300 | 200 | 1500 | 997327.0912 | 2673603.7889 | 1.5
66 | HAJIPUR | Pahetiya | 10 | Yadav Tola | 90 | 150 | 300 | 350 | 350 | 250 | 1400 | 911350.3151 | 2429143.2562 | 1.4
67 | HAJIPUR | Pahetiya | 5 | Mahto Tola | 95 | 150 | 350 | 350 | 300 | 200 | 1350 | 902578.277 | 2433243.3317 | 1.35
68 | HAJIPUR | Pahetiya | 8 | Sahani Tola | 85 | 300 | 600 | 500 | 450 | 464 | 2314 | 1409959.453 | 2953192.0741 | 2.314
69 | HAJIPUR | Pahetiya | 14 | Yadav Tola | 95 | 250 | 350 | 350 | 300 | 250 | 1500 | 996778.9912 | 2534682.8559 | 1.5
70 | HAJIPUR | Afjalpur Dhobaghatti | 1 | Yadav Tola | 70 | 100 | 250 | 300 | 150 | 150 | 950 | 695759.1725 | 2140798.4291 | 0.95
71 | HAJIPUR | Afjalpur Dhobaghatti | 7 | Mahadalit Tola | 85 | 300 | 600 | 500 | 450 | 464 | 2314 | 1409959.453 | 2953192.0741 | 2.314
72 | HAJIPUR | Afjalpur Dhobaghatti | 8 | Paswan Tola | 85 | 150 | 350 | 300 | 250 | 200 | 1250 | 855532.8759 | 2354714.9887 | 1.25
73 | HAJIPUR | Afjalpur Dhobaghatti | 4 | Paswan Tola | 75 | 150 | 300 | 350 | 400 | 350 | 1550 | 969686.1793 | 2450916.3984 | 1.55
74 | HAJIPUR | Afjalpur Dhobaghatti | 11 | Pandit Tola | 95 | 150 | 300 | 300 | 200 | 250 | 1200 | 822633.9378 | 2291639.4574 | 1.2
75 | HAJIPUR | Afjalpur Dhobaghatti | 12 & 13 | Bhumiyar Tola | 85 | 150 | 300 | 350 | 400 | 400 | 1600 | 988436.3674 | 2498935.7355 | 1.6
76 | HAJIPUR | Senduari | 14 | Bhumiyar Tola | 185 | 250 | 500 | 500 | 400 | 300 | 1950 | 1228270.8089 | 3033620.9158 | 1.95
77 | HAJIPUR | Bisunpur Basant | 3 | Saw tola | 150 | 150 | 350 | 400 | 300 | 300 | 1500 | 966288.5662 | 2654408.345 | 1.5
78 | HAJIPUR | Bisunpur Basant | 4 | Yadav Tola | 60 | 150 | 300 | 300 | 250 | 200 | 1200 | 824719.2378 | 2252357.1962 | 1.2
79 | HAJIPUR | Bisunpur Basant | 12 | Bhumiyar Tola | 55 | 150 | 300 | 300 | 200 | 200 | 1150 | 803883.7497 | 2215952.5842 | 1.15
80 | HAJIPUR | Bisunpur Basant | 10 | Paswan Tola | 145 | 200 | 400 | 400 | 350 | 250 | 1600 | 1036912.7674 | 2716526.4339 | 1.6
81 | HAJIPUR | Bishunpur Basant | 14 | Yadav Tola | 85 | 300 | 600 | 500 | 450 | 464 | 2314 | 1409959.453 | 2953192.0741 | 2.314
82 | HAJIPUR | Panapur Langa | 1 | Kumhar Tola | 35 | 150 | 250 | 250 | 200 | 150 | 1000 | 728110.0105 | 2078786.7955 | 1
83 | HAJIPUR | Panapur Langa | 2 | Yadav Tola | 65 | 150 | 300 | 300 | 200 | 200 | 1150 | 803883.7497 | 2243620.1202 | 1.15
84 | HAJIPUR | Panapur Langa | 8 | Mali Tola | 135 | 200 | 500 | 400 | 400 | 300 | 1800 | 1138125.7196 | 2798159.4481 | 1.8
85 | HAJIPUR | Panapur Langa | 9 | Yadav Tola | 95 | 200 | 500 | 400 | 350 | 250 | 1700 | 1098540.0435 | 2644566.659 | 1.7
86 | HAJIPUR | Chankunda urf Milki | 5 | Paswan Tola | 65 | 200 | 500 | 500 | 300 | 250 | 1750 | 1130124.3816 | 2595573.1332 | 1.75
87 | HAJIPUR | Chankunda urf Milki | 4 | Paswan Tola | 50 | 150 | 400 | 400 | 250 | 250 | 1450 | 957516.5282 | 2367999.2925 | 1.45
88 | HAJIPUR | Chankunda urf Milki | 3 | Yadav Tola | 55 | 150 | 300 | 350 | 400 | 350 | 1550 | 969686.1793 | 2395581.3264 | 1.55
89 | HAJIPUR | Kashipur chakbibi | 12 | Yadav Tola | 75 | 150 | 350 | 400 | 250 | 200 | 1350 | 907952.702 | 2383627.3788 | 1.35
90 | HAJIPUR | Kashipur chakbibi | 7 | Paswan Tola | 65 | 200 | 350 | 300 | 300 | 300 | 1450 | 951594.0032 | 2403198.2245 | 1.45
91 | HAJIPUR | Kasipur Chakbibi | 8 | Yadav Tola | 60 | 100 | 250 | 250 | 200 | 150 | 950 | 690384.7475 | 2107411.7739 | 0.95
92 | HAJIPUR | Bahuara | 1 | Yadav Tola | 65 | 200 | 400 | 450 | 350 | 400 | 1800 | 1119373.2446 | 2584531.5124 | 1.8
93 | HAJIPUR | Bahuara | 10 | Yadav Tola | 115 | 200 | 400 | 500 | 400 | 300 | 1800 | 1128918.2696 | 2733026.3971 | 1.8
94 | HAJIPUR | Bahuara | 14 | Yadav Tola | 65 | 100 | 250 | 350 | 136 | 100 | 936 | 697000 | 2155254.6241 | 1
95 | HAJIPUR | Andharbara | 2 | Muslim Tola | 50 | 100 | 200 | 200 | 150 | 100 | 750 | 593775.5202 | 1975342.6772 | 0.75
96 | HAJIPUR | Andharbara | 3 | Yadav Tola | 75 | 150 | 400 | 400 | 250 | 200 | 1400 | 938766.3401 | 2416816.3314 | 1.4
97 | HAJIPUR | Andharbara | 4 | Bhumiyar Tola | 75 | 150 | 400 | 400 | 250 | 200 | 1400 | 938766.3401 | 2416816.3314 | 1.4
98 | HAJIPUR | Andharbara | 9 | Bhumiyar Tola | 100 | 150 | 350 | 350 | 200 | 200 | 1250 | 860907.3009 | 2401935.4118 | 1.25
99 | HAJIPUR | Andharbara | 10 | Paswan Tola | 70 | 150 | 300 | 250 | 150 | 150 | 1000 | 738088.1605 | 2186241.2801 | 1
100 | HAJIPUR | Andharbara | 11 | Barka Tola | 115 | 200 | 400 | 500 | 400 | 300 | 1800 | 1128918.2696 | 2733026.3971 | 1.8
101 | HAJIPUR | Andharbara | 13 | Paswan Tola | 95 | 200 | 400 | 400 | 300 | 300 | 1600 | 1034827.4674 | 2575969.7111 | 1.6
102 | HAJIPUR | Hilalpur | 1 | Yadav Tola | 55 | 150 | 300 | 300 | 200 | 150 | 1100 | 785133.5617 | 2195600.7831 | 1.1
103 | HAJIPUR | Hilalpur | 9 & 10 | Yadav Tola | 95 | 200 | 500 | 400 | 450 | 400 | 1950 | 1196461.5839 | 2750763.7503 | 1.95
104 | HAJIPUR | Hilalpur | 8 | Paswan Tola | 100 | 150 | 300 | 350 | 400 | 350 | 1550 | 969686.1793 | 2520085.2384 | 1.55
105 | HAJIPUR | Sultanpur | 3 | Paswan Tola | 95 | 200 | 300 | 400 | 200 | 250 | 1350 | 912779.027 | 2444098.317 | 1.35
106 | HAJIPUR | Sultanpur | 9 | Paswan Tola | 60 | 150 | 300 | 350 | 200 | 200 | 1200 | 830093.6628 | 2258076.3153 | 1.2
107 | HAJIPUR | Hilalpur | 5 | Yadav Tola | 115 | 200 | 400 | 500 | 400 | 300 | 1800 | 1128918.2696 | 2733026.3971 | 1.8
108 | BIDUPUR | Bidupur | 12 | Rajput Tola | 150 | 100 | 250 | 300 | 400 | 500 | 1550 | 931187.9293 | 2617455.5446 | 1.55
109 | BIDUPUR | Dilawarpur Govardhan | 13,12 | Yadav Tola | 180 | 150 | 100 | 100 | 400 | 400 | 1150 | 734132.2497 | 2238563.878 | 1.15
110 | BIDUPUR | Sahdulapur Dhobauli | 9 | Yadav Tola | 80 | 200 | 350 | 300 | 700 | 600 | 2150 | 1230779.0361 | 2747377.0867 | 2.15
111 | BIDUPUR | Sahdulapur Dhobauli | 15A | Yadav Tola | 70 | 250 | 500 | 200 | 200 | 100 | 1250 | 912668.6259 | 2374013.8932 | 1.25
112 | BIDUPUR | Amer | 8,13 | Rajput Tola | 80 | 150 | 200 | 200 | 100 | 100 | 750 | 610665.2952 | 2076318.3029 | 0.75
113 | BIDUPUR | Khanpur Pakri | 6 | DALIT TOLA | 70 | 100 | 500 | 500 | 250 | 100 | 1450 | 977587.8032 | 2444692.9308 | 1.45
114 | BIDUPUR | Kathuliya | 7 | Rajput Tola | 80 | 250 | 300 | 300 | 250 | 250 | 1350 | 918919.952 | 2409131.7924 | 1.35
115 | BIDUPUR | Chakatkurshi | 8 | Pandit Tola | 60 | 300 | 250 | 250 | 300 | 300 | 1400 | 939207.3401 | 2375784.3114 | 1.4
116 | BIDUPUR | Saidpur Ganesh | 6 | Yadav Tola | 60 | 350 | 400 | 500 | 350 | 250 | 1850 | 1202508.3827 | 2659563.8887 | 1.85
117 | BIDUPUR | Mail | 12 | Muslim Tola | 60 | 150 | 200 | 200 | 300 | 400 | 1250 | 806508.3759 | 2233377.4134 | 1.25
118 | BIDUPUR | Dilawarpur Govardhan | 13 |  | 115 | 110 | 220 | 340 | 470 | 560 | 1700 | 992882.6385 | 2587467.8827 | 1.7
119 | BIDUPUR | Bidupur | 10 |  | 100 | 150 | 260 | 380 | 460 | 550 | 1800 | 1060764.5546 | 2619000.2714 | 1.8
120 | BIDUPUR | Rahimapur | 6&7 |  | 125 | 10 | 250 | 170 | 290 | 230 | 950 | 648047.5925 | 2242198.2672 | 0.95
121 | BIDUPUR | Kanchanpur | 4 |  | 80 | 50 | 160 | 190 | 245 | 310 | 955 | 644495.5813 | 2113954.4373 | 0.955
122 | BIDUPUR | Rahimapur | 9& 10 |  | 150 | 150 | 220 | 320 | 340 | 470 | 1500 | 924656.2762 | 2610105.9265 | 1.5
123 | BIDUPUR | Khanpur Pakri | 15&16 |  | 125 | 100 | 160 | 230 | 440 | 570 | 1500 | 881948.1562 | 2495489.8385 | 1.5
124 | BIDUPUR | Kathuliya | 11&12 |  | 85 | 100 | 150 | 190 | 280 | 380 | 1100 | 716893.2217 | 2109150.0126 | 1.1
125 | BIDUPUR | Saidpur Ganesh | 9B |  | 45 | 150 | 200 | 200 | 250 | 200 | 1000 | 710672.1355 | 2087898.0609 | 1
126 | RAJAPAKAR | JAFARPATTI | 10 |  | 50 | 100 | 200 | 300 | 400 | 400 | 1400 | 1419186.9515 | 2991365.2911 | 2.4
127 | RAJAPAKAR | BAIKUNTHPUR | 7,9 |  | 115 | 100 | 300 | 400 | 500 | 500 | 1800 | 1056092.3696 | 2531025.8232 | 1.8
128 | RAJAPAKAR | Bakhari bari | 11B, 8 |  | 105 | 300 | 700 | 600 | 500 | 400 | 2500 | 1520841.8026 | 3128005.5158 | 2.5
129 | RAJAPAKAR | RAMPUR RATNAKAR | 08,11 & 16B |  | 205 | 300 | 700 | 600 | 500 | 400 | 2500 | 1520841.8026 | 3128005.5158 | 2.5
130 | RAJAPAKAR | BARAI | 9,6 |  | 100 | 200 | 400 | 250 | 450 | 500 | 1800 | 1093704.9446 | 2654053.3263 | 1.8
131 | RAJAPAKAR | MIRPUR PATHAD | 1,6,5 |  | 195 | 350 | 400 | 500 | 600 | 550 | 2400 | 1419186.9515 | 2991365.2911 | 2.4
132 | RAJAPAKAR | BAIKUNTPUR | 1,2,11 |  | 80 | 200 | 350 | 300 | 700 | 600 | 2150 | 1230779.0361 | 2747377.0867 | 2.15
133 | RAJAPAKAR | Bakarpur | 11,13 |  | 100 | 200 | 400 | 250 | 450 | 500 | 1800 | 1093704.9446 | 2654053.3263 | 1.8
134 | RAJAPAKAR | Narayanpur Bujurg | 11,14 |  | 165 | 350 | 400 | 400 | 800 | 500 | 2450 | 1431358.8896 | 2921714.3316 | 2.45
135 | RAJAPAKAR | Jafarpatti | 3 |  | 195 | 350 | 400 | 500 | 600 | 550 | 2400 | 862873.9151 | 2266887.6298 | 1.4 | 50 | 100 | 200 | 300 | 400 | 400 | 1400
136 | RAJAPAKAR | Gauspur | 2,4 |  | 105 | 300 | 700 | 600 | 500 | 400 | 2500 | 1520841.8026 | 3128005.5158 | 2.5
137 | RAJAPAKAR | Bakarpur | 3 |  | 65 | 150 | 300 | 370 | 350 | 250 | 1420 | 921834.2803 | 2371290.4014 | 1.42
138 | RAJAPAKAR | Rajapakar Uttari | 3 |  | 50 | 150 | 350 | 350 | 250 | 150 | 1250 | 862992.6009 | 2265816.7746 | 1.25
139 | RAGHOPUR | RUSTAMPUR | 4 | Yadav Tola | 80 | 150 | 200 | 200 | 100 | 100 | 750 | 610665.2952 | 2076318.3029 | 0.75
140 | RAGHOPUR | CHANDPURA | 1 | Rajput Tola | 80 | 250 | 200 | 500 | 500 | 200 | 1650 | 1047559.5804 | 2548416.158 | 1.65
141 | RAGHOPUR | CHANDPURA | 6 | Yadav Tola | 70 | 100 | 500 | 500 | 250 | 100 | 1450 | 977587.8032 | 2444692.9308 | 1.45
142 | RAGHOPUR | CHANDPURA | 11 | Yadav Tola | 85 | 250 | 300 | 300 | 250 | 250 | 1350 | 918919.952 | 2422965.5604 | 1.35
143 | RAGHOPUR | CHANDPURA | 5 | Rajput Tola | 60 | 300 | 250 | 250 | 300 | 300 | 1400 | 939207.3401 | 2375784.3114 | 1.4
144 | RAGHOPUR | RUSTAMPUR | 5B,20 |  | 195 | 350 | 400 | 500 | 600 | 550 | 2400 | 1419186.9515 | 2991365.2911 | 2.4
145 | RAGHOPUR | JAHAGIRPUR | 1 |  | 80 | 250 | 200 | 500 | 500 | 200 | 1650 | 1047559.5804 | 2548416.158 | 1.65
146 | RAGHOPUR | JAHAGIRPUR | 7 |  | 225 | 200 | 400 | 250 | 450 | 500 | 1800 | 1093704.9446 | 2654053.3263 | 1.8
147 | RAGHOPUR | JAHAGIRPUR | 5 |  | 150 | 300 | 250 | 250 | 450 | 400 | 1650 | 1039214.1804 | 2594870.5894 | 1.65
148 | RAGHOPUR | JAHAGIRPUR | 4 |  | 200 | 350 | 400 | 400 | 800 | 500 | 2450 | 1431358.8896 | 2921714.3316 | 2.45
149 | RAGHOPUR | SARAIPUR | 5 | Rajput Tola | 70 | 350 | 400 | 500 | 600 | 550 | 2400 | 1419186.9515 | 2991365.2911 | 2.4
150 | RAGHOPUR | TERASIYA | 11 | Rajput Tola | 60 | 300 | 250 | 250 | 300 | 300 | 1400 | 939207.3401 | 2375784.3114 | 1.4
151 | RAGHOPUR | TERASIYA | 12 | Rajput Tola | 60 | 300 | 250 | 250 | 300 | 300 | 1400 | 939207.3401 | 2375784.3114 | 1.4
152 | RAGHOPUR | RAMPUR SHAYAMCHAND | 13 | Yadav Tola | 75 | 200 | 300 | 250 | 200 | 200 | 1150 | 815399.0997 | 2283541.5547 | 1.15
153 | RAGHOPUR | RAGHOPUR EAST | 7 | Rajput Tola | 60 | 350 | 400 | 500 | 350 | 250 | 1850 | 1202508.3827 | 2659563.8887 | 1.85
154 | RAGHOPUR | BAHARAMAPUR | 2,3 | Yadav Tola | 65 | 200 | 200 | 250 | 300 | 300 | 1250 | 832943.1759 | 2275341.4037 | 1.25
155 | RAGHOPUR | BAHARAMAPUR | 13 | Yadav Tola | 70 | 150 | 200 | 200 | 300 | 400 | 1250 | 806508.3759 | 2261044.9494 | 1.25
156 | RAGHOPUR | BAHARAMAPUR | 10 | Rajput Tola | 60 | 200 | 400 | 100 | 100 | 300 | 1100 | 794226.0367 | 2219110.1811 | 1.1
157 | VAISHALI | Amritpur | 8 | Yadav Tola | 50 | 100 | 200 | 300 | 300 | 400 | 1300 | 821202.9389 | 2221745.9419 | 1.3
158 | VAISHALI | Majhauli | 8 | Paswan Tola | 115 | 200 | 400 | 500 | 400 | 300 | 1800 | 1128918.2696 | 2733026.3971 | 1.8
159 | PATEDHI BELSAR | Nagawan | 10 |  | 100 | 200 | 400 | 250 | 450 | 500 | 1800 | 1093704.9446 | 2654053.3263 | 1.8
160 | PATEDHI BELSAR | Nagawan | 1 |  | 100 | 300 | 250 | 250 | 450 | 400 | 1650 | 1039214.1804 | 2594870.5894 | 1.65
161 | PATEDHI BELSAR | Sain | 1 |  | 65 | 350 | 400 | 400 | 800 | 500 | 2450 | 1431358.8896 | 2921714.3316 | 2.45
162 | PATEDHI BELSAR | Sain | 4 |  | 95 | 350 | 400 | 500 | 600 | 550 | 2400 | 1419186.9515 | 2991365.2911 | 2.4
163 | PATEDHI BELSAR | Sorahattha | 1 |  | 80 | 200 | 350 | 300 | 700 | 600 | 2150 | 1230779.0361 | 2747377.0867 | 2.15
164 | PATEDHI BELSAR | Manora | 13 |  | 70 | 250 | 500 | 200 | 200 | 100 | 1250 | 912668.6259 | 2374013.8932 | 1.25
165 | PATEDHI BELSAR | Mishrauliya | 8 |  | 60 | 300 | 250 | 250 | 300 | 300 | 1400 | 939207.3401 | 2375784.3114 | 1.4
166 | PATEDHI BELSAR | Manora | 1 |  | 60 | 350 | 400 | 500 | 350 | 250 | 1850 | 1202508.3827 | 2659563.8887 | 1.85
167 | PATEDHI BELSAR | Chakgulamuddin | 2 |  | 60 | 150 | 200 | 200 | 300 | 400 | 1250 | 806508.3759 | 2233377.4134 | 1.25
168 | PATEDHI BELSAR | Chakgulamuddin | 1 |  | 60 | 200 | 400 | 100 | 100 | 300 | 1100 | 794226.0367 | 2219110.1811 | 1.1
169 | PATEDHI BELSAR | Mishrauliya | 10 |  | 50 | 150 | 200 | 100 | 200 | 250 | 900 | 656167.0094 | 2042932.86 | 0.9
170 | PATEDHI BELSAR | Karneji | 5 |  | 100 | 20 | 140 | 170 | 220 | 550 | 1100 | 678634.1617 | 2206774.8496 | 1.1
171 | GORAUL | Katarmala | 2 | PRD | 25 | 50 | 100 | 150 | 200 | 200 | 700 | 526548.9321 | 1834236.5537 | 0.7
172 | GORAUL | ISMAILPUR | 11&12 |  | 50 | 100 | 100 | 250 | 300 | 450 | 1200 | 752115.9378 | 2147429.8749 | 1.2
173 | GORAUL | ISMAILPUR | 4B |  | 70 | 100 | 200 | 350 | 400 | 450 | 1500 | 907834.0162 | 2370864.466 | 1.5
174 | GORAUL | BHUALPUR UF BAHADURPUR | 7&8 |  | 80 | 50 | 100 | 100 | 200 | 150 | 600 | 481588.831 | 1937766.2375 | 0.6
175 | GORAUL | LODIPUR | 6 |  | 105 | 300 | 700 | 600 | 500 | 400 | 2500 | 1520841.8026 | 3128005.5158 | 2.5
176 | GORAUL | BAKSAMA | 13 |  | 65 | 150 | 300 | 370 | 350 | 250 | 1420 | 921834.2803 | 2371290.4014 | 1.42
177 | LALGANJ | Atwarpur Sisaula | 02&03 | Tanra par | 125 | 100 | 160 | 230 | 440 | 570 | 1500 | 881948.1562 | 2495489.8385 | 1.5
178 | LALGANJ | Yusufpur | 5 | YADAV TOLA | 40 | 300 | 250 | 250 | 450 | 400 | 1650 | 1039214.1804 | 2428865.3734 | 1.65
179 | LALGANJ | Bhatuli Bhagwan | 10,11,12 |  | 60 | 150 | 300 | 300 | 200 | 150 | 1100 | 785133.5617 | 2209434.5511 | 1.1
180 | LALGANJ | Shital Bhakurahar | 3 |  | 55 | 150 | 300 | 300 | 250 | 200 | 1200 | 824719.2378 | 2238523.4282 | 1.2
181 | LALGANJ | Yusufpur | 3 |  | 80 | 250 | 300 | 300 | 250 | 250 | 1350 | 918919.952 | 2409131.7924 | 1.35
182 | BHAGWANPUR | Sahmia Rahua | 1 |  | 65 | 200 | 400 | 250 | 450 | 500 | 1800 | 1093704.9446 | 2654053.3263 | 1.8
183 | BHAGWANPUR | MAGANPUR | 6 |  | 100 | 300 | 250 | 250 | 450 | 400 | 1650 | 1039214.1804 | 2594870.5894 | 1.65
184 | BHAGWANPUR | SAHTHA | 2 |  | 65 | 350 | 400 | 400 | 800 | 500 | 2450 | 1431358.8896 | 2921714.3316 | 2.45
185 | SAHDEI BUZURG | Naya Gaow West | 11 | KUSHWAHA TOLA | 110 | 50 | 250 | 300 | 250 | 280 | 1130 | 748455.3745 | 2308981.0823 | 1.13
186 | SAHDEI BUZURG | Sultanpur | 9 | YADAV TOLA | 70 | 200 | 400 | 250 | 450 | 500 | 1800 | 1093704.9446 | 2571050.7183 | 1.8
187 | MAHNAR | Gorigama | 9 | Ravidas tola | 85 | 50 | 250 | 300 | 250 | 280 | 1130 | 748455.3745 | 2239812.2423 | 1.13
188 | PATEPUR | Malpur | 2 | PRD | 70 | 50 | 150 | 250 | 300 | 450 | 1200 | 745204.3128 | 2167742.5019 | 1.2
189 | PATEPUR | Govindpur Bela | 6 | PRD | 102 | 100 | 100 | 200 | 300 | 450 | 1150 | 725906.0247 | 2160641.2158 | 1.15
190 | PATEPUR | Harlochanpur Sukki | 3 | PRD | 80 | 100 | 100 | 200 | 300 | 450 | 1150 | 725906.0247 | 2160641.2158 | 1.75
191 | JANDAHA | Mahipura | 7 | Paswan Tola | 115 | 110 | 220 | 340 | 470 | 560 | 1700 | 992882.6385 | 2587467.8827 | 1.7
192 | JANDAHA | Said Mohammad Urf Salaha | 9 | Ram Tola | 100 | 150 | 260 | 380 | 460 | 550 | 1800 | 1060764.5546 | 2619000.2714 | 1.8
193 | JANDAHA | Chandsarai | 12 | Yadav +Paswan Tola | 125 | 10 | 250 | 170 | 290 | 230 | 950 | 648047.5925 | 2242198.2672 | 0.95
194 | JANDAHA | Dih Bichauli | 8&1 | Pasi + Lohar Tola | 80 | 50 | 160 | 190 | 245 | 310 | 955 | 644495.5813 | 2113954.4373 | 0.955
195 | JANDAHA | Khopi | 3 | Mushahari Tola | 150 | 150 | 220 | 320 | 340 | 470 | 1500 | 924656.2762 | 2610105.9265 | 1.5
196 | JANDAHA | Rasulpur Purushottam | 4,5,6 | Dhanuk & Pandit Tola | 50 | 100 | 150 | 190 | 280 | 380 | 1100 | 716893.2217 | 2109150.0126 | 1.1
197 | JANDAHA | Laxmipur Barbatta | 8 | Hajjam + Kushwaha Tola | 45 | 50 | 100 | 180 | 240 | 280 | 850 | 588943.5713 | 1957165.1605 | 0.85
198 | JANDAHA | Harprasad | 10 | Paswan + muslim tola | 60 | 100 | 200 | 220 | 370 | 510 | 1400 | 849687.1751 | 2280522.6811 | 1.4
199 | JANDAHA | Harprasad | 3 | Kushwaha + Sahni Tola | 60 | 100 | 170 | 230 | 360 | 460 | 1320 | 813523.6892 | 2241401.3322 | 1.32
| TOTAL |  |  |  | 16589 | 35495 | 60920 | 62093 | 67506 | 61872 | 287886 | 186088237.8754 | 480601292.77

## COM Quantity (hidden)
P. H. DIVISION, HAJIPUR
WORK DETAIL Of Quantity For Distribution System
DETAILS OF Pipeline Distribution System Of Different Schemes
Block :- Bidupur
Sl. No. | Panchayat | Ward No | Scheme Name | Different Size Of HDPE pipe (In Mtrs.) | [6 empty] | PVC Tank in Liter | Brass gate valve with C.I. wheel |  |  | Nos. of connections
|  |  |  | 110 mm | 90 mm | 75 mm | 63 mm | 50 mm | 40 mm | Total |  | 80 mm | 65 mm | 50 mm
1 | Bajitpur Saidat | 03B | (Kushwaha Tola) | 0 | 150 | 300 | 400 | 350 | 350 | 1550 | 10000 | 2 | 2 | 1 | 95 |  | ( | )
2 | Bajitpur Saidat | 05B | (Kahar Tola ) | 0 | 100 | 250 | 250 | 200 | 350 | 1150 | 10000 | 2 | 2 | 2 | 60 |  | ( | )
3 | Bajitpur Saidat | 09B&13B | (DalitTola) | 0 | 100 | 250 | 250 | 200 | 200 | 1000 | 10000 | 2 | 2 | 2 | 100 |  | ( | )
4 | Chakat Kursi Kushyari | 02B | (Dalit Tola) | 0 | 100 | 250 | 250 | 300 | 300 | 1200 | 10000 | 2 | 2 | 1 | 75 |  | ( | )
5 | Chakat Kursi Kushyari | 10B | (Yadav Tola ) | 0 | 200 | 500 | 550 | 450 | 350 | 2050 | 10000 | 2 | 2 | 2 | 120 |  | ( | )
6 | Chakat Kursi Kushyari | 11B | (DalitTola) | 0 | 150 | 300 | 400 | 350 | 350 | 1550 | 10000 | 2 | 2 | 2 | 130 |  | ( | )
7 | Chechar | 10B & 11B | (Yadav Tola) | 0 | 100 | 300 | 400 | 350 | 350 | 1500 | 10000 | 2 | 2 | 1 | 105 |  | ( | )
8 | Chechar | 12B & 13B | (Dalit Tola) | 0 | 100 | 300 | 400 | 350 | 350 | 1500 | 10000 | 2 | 2 | 1 | 55 |  | ( | )
9 | DAUDNAGAR | 09B | DAUDNAGAR | 0 | 150 | 400 | 300 | 350 | 200 | 1400 |  |  |  |  | 75
10 | Dilawarpur Govardhan | 02B &6 | Dalit Tola | 0 | 150 | 450 | 400 | 300 | 300 | 1600 | 10000 | 2 | 2 | 1 | 75 | 02B &6 | ( | )
11 | Dilawarpur Govardhan | 03B & 8 | Rajput Tola | 0 | 150 | 450 | 550 | 350 | 300 | 1800 | 10000 | 2 | 2 | 1 | 95 | 03B & 8 | ( | )
12 | Dilawarpur Govardhan | 04B | Kushwaha Tola | 0 | 200 | 500 | 550 | 450 | 400 | 2100 | 10000 | 2 | 2 | 1 | 95 | 04B | ( | )
13 | Dilawarpur Govardhan | 05B &6 | Rajput Tola | 0 | 150 | 450 | 550 | 350 | 350 | 1850 | 10000 | 2 | 2 | 1 | 105 | 05B &6 | ( | )
14 | Dilawarpur Govardhan | 7B & 6 | Pashwan Tola | 0 | 150 | 450 | 400 | 300 | 300 | 1600 | 10000 | 2 | 2 | 2 | 95 | 7B & 6 | ( | )
15 | Dilawarpur Govardhan | 14B &15 | Kumhar Tola | 0 | 150 | 450 | 400 | 300 | 300 | 1600 | 10000 | 2 | 2 | 1 | 80 | 14B &15 | ( | )
16 | Kanchanpur | 09B | YADAV TOLA |  | 100 | 300 | 350 | 250 | 200 | 1200 |  |  |  |  | 80 | 09B
17 | KATHAULIYA | 07B | DALIT TOLA |  | 200 | 500 | 550 | 500 | 450 | 2200 |  |  |  |  | 150 | 07B
18 | Khanpur Pakri | 02&04 | (Dalit Tola) | 0 | 100 | 200 | 200 | 250 | 300 | 1050 | 10000 | 2 | 2 | 1 | 75 |  | ( | )
19 | Khanpur Pakri | 04B | (Yadav Tola ) | 0 | 100 | 200 | 250 | 250 | 200 | 1000 | 10000 | 2 | 2 | 2 | 50 |  | ( | )
20 | Khanpur Pakri | 10B | (Yadav & Dalit Tola ) | 0 | 150 | 500 | 550 | 450 | 350 | 2000 | 10000 | 2 | 2 | 2 | 120 |  | ( | )
21 | Khilwat | 01B | Khilwat (Yadav Tola) | 0 | 150 | 450 | 550 | 350 | 300 | 1800 | 10000 | 2 | 2 | 1 | 95 |  | ( | )
22 | Khilwat | 02B | Yadav Tola | 0 | 100 | 200 | 300 | 300 | 300 | 1200 | 10000 | 2 | 2 | 1 | 75 |  | ( | )
23 | Khilwat | 9B | Khilwat (Tatama Tola ) | 0 | 150 | 350 | 300 | 200 | 200 | 1200 | 10000 | 2 | 2 | 2 | 75 |  | ( | )
24 | Khilwat | 12B&13B | Khilwat (Yadav Tola) | 0 | 150 | 350 | 300 | 200 | 200 | 1200 | 10000 | 2 | 2 | 2 | 70 |  | ( | )
25 | Kutubpur | 12B&11B | (Kahar Tola) | 0 | 250 | 700 | 800 | 400 | 400 | 2550 | 10000 | 2 | 2 | 1 | 75 |  | ( | )
26 | Kutubpur | 13B | (Yadav Tola) | 0 | 150 | 450 | 400 | 300 | 300 | 1600 | 10000 | 2 | 2 | 1 | 95 |  | ( | )
27 | Mail Pakri | 14B&7B | (Yadav Tola) | 0 | 150 | 450 | 550 | 350 | 300 | 1800 | 10000 | 2 | 2 | 1 | 110 |  | ( | )
28 | Mail Pakri | 10B & 11B | (Mahadalit Tola) | 0 | 150 | 450 | 550 | 350 | 300 | 1800 | 10000 | 2 | 2 | 1 | 100 |  | ( | )
29 | Nawanagar | 03B | (Yadav Tola) |  | 100 | 200 | 250 | 250 | 200 | 1000 |  |  |  |  | 50
30 | Rahimapur | 09B&08B | (Yadav Tola) | 0 | 150 | 300 | 350 | 350 | 300 | 1450 | 10000 | 2 | 2 | 1 | 95 |  | ( | )
31 | Rahimapur | 02B | (Mahadalit Tola ) | 0 | 150 | 500 | 550 | 350 | 300 | 1850 | 10000 | 2 | 2 | 2 | 120 |  | ( | )
32 | Rahimapur | 10B&11B | (Mahadalit Tola ) | 0 | 100 | 300 | 250 | 200 | 250 | 1100 | 10000 | 2 | 2 | 2 | 65 |  | ( | )
33 | Sahdullahpur Dhabaul | 11B | (Mahadalit Tola) | 0 | 100 | 200 | 300 | 350 | 250 | 1200 | 10000 | 2 | 2 | 1 | 70 |  | ( | )
34 | Sahdullahpur Dhabaul & Majhauli Siman | 5B&5B | (Yadav Tola) | 0 | 100 | 200 | 250 | 250 | 200 | 1000 | 10000 | 2 | 2 | 1 | 50 |  | ( | )
35 | Majlispur | 05B | (Yadav Tola) |  | 100 | 200 | 300 | 300 | 300 | 1200 | 10000 | 2 | 2 | 1 | 150 |  | ( | )
36 | Jurawanpur | 10B | (Yadav Tola) |  | 200 | 400 | 500 | 450 | 450 | 2000 | 10000 | 2 | 2 | 1 | 165 |  | ( | )
37 | Jurawanpur | 12B | (Yadav Tola) |  | 200 | 400 | 500 | 450 | 450 | 2000 | 10000 | 2 | 2 | 1 | 160 |  | ( | )
38 | Jurawanpur | 13B | (Yadav Tola) |  | 200 | 500 | 600 | 450 | 450 | 2200 | 10000 | 2 | 2 | 1 | 160 |  | ( | )
TOTAL |  |  |  | 0 | 5400 | 13900 | 15550 | 12500 | 11700 | 59050 | 340000 | 68 | 68 | 45 | 3615
JE |  |  |  |  | AE | [9 empty] | EE

## Bajitpur Saidat 03B (hidden)
Sub Estimate no. - 3A
Bajitpur Saidat Ward No. :-03B
WATER SUPPLY DISTRIBUTION SYSTEM
S.N. | Particulars |  |  |  |  | Quantity |  | Unit | Rate | Amount
1/ 2.8 | Earthwork in excavation over areas (exceeding 30 cm in depth 1.5 in width as well as 10 sqm on plan) including disposal of excavated earth lead upto 50m and lift upto 1.5m, disposal earth to be levelled and neatly dressed.
| 110mm dia Pipe | 0 | 0.3 | 1.1 | = | 0 | [6 empty] | 152000
| 90mm dia Pipe | 150 | 0.3 | 1.1 | = | 49.5 | [6 empty] | 152000
| 75mm dia Pipe | 300 | 0.3 | 1.1 | = | 99
| 63mm dia Pipe | 400 | 0.3 | 1.1 | = | 132 | [6 empty] | 152000
| 50 mm dia Pipe | 350 | 0.3 | 1.1 | = | 115.5
| 40mm dia Pipe | 350 | 0.3 | 1.1 | = | 115.5
|  | 1550 |  |  |  | 511.5 | M3
| Add 5% extra for fittings = |  |  |  |  | 25.575 | M3
[6 empty] | 537.075 | M3 | P/M3 | 360.7 | 193722.9525
2/ 2.26 | Filling available excavated earth (excluding rock) in trenches, plinth, sides of foundations etc. in layers not exceeding 20cm in depth, consolidating each deposited layer by ramming and watering, lead up to 50 m and lift upto 1.5 m. |  |  |  |  | 526.3335 | M3 | P/M3 | 123.9 | 65212.7207
3/ 15.2.1 | Demolishing cement concrete manually/by mechanical means including disposal of material within 50 metres lead as per direction of Engineer - in - charge. | [8 empty] | 20316.0825
1:3:6 or richer mix
|  | 465 | 0.3 | 0.15 | = | 20.925 | M3 | P/M3 | 970.9
4/ 4.1.3 | Providing and laying in position cement concrete of specified grade excluding the cost of centering and shuttering all work upto plinth |  |  |  |  | 20.925 | M3 | P/M3 | 3998.1 | 83660.2425 | 4969
1:2:4 (1 cement: 2 coarse sand : 4 graded stone aggregate 40mm nominal size)
5 | Carriage of the following materials from quarry to work site including loading, unloading and staking at work site as per specification & direction of E/I.
| Coarse Sand (44Km Pucca & 1Km Kaccha Carriage) |  |  |  |  | 9.6255 | M3 | P/M3 | 1160.62 | 11171.5478
| Stone chips (195Km Pucca & 5Km unsurafced Carriage) |  |  |  |  | 19.251 | M3 | P/M3 | 4291.17 | 82609.3137
6A/ 18.12 | Providing and fixing G.I.Pipes complete with G.I. Fittings including trenching and refilling etc.
18.12.6 | 50mm dia G.I.Pipe from T/well to PVC Tank |  |  |  |  | 14 | M | P/M | 572.6 | 8016.4 |  |  |  | 611.3975
18.12.8 | 80mm dia G.I.Pipe from PVC Tank to Distribution main |  |  |  |  | 14 | M | P/M | 818.2 | 11454.8
18.12.7 | 65mm dia G.I.Pipe for wash out |  |  |  |  | 12 | M | P/M | 667.7 | 8012.4
7A/ 18.31.1.1 | P/F C.I sluice Valve (with Cap) complete with bolts,nuts,rubber insertions etc
6B/ | Providing and fixing brass gate valve with C.I. wheel of approved quality (screwed end).
| 80mm dia Pipe |  |  |  |  | 2 | Nos. | Each | 2227.6 | 4455.2
| 65mm dia Pipe |  |  |  |  | 2 | Nos. | Each | 1490.7 | 2981.4
| 50mm dia Pipe |  |  |  |  | 1 | Nos. | Each | 878.2 | 878.2
7/ 18.33 | Constructing masonry Chamber 60x60x75 cm inside, in brick work in cement mortar 1:4 (1 cement : 4 coarse sand) for sluice valve,with C.I. surface box 100mm top diameter, 160 mm bottom diameter and 180 mm deep ( inside) with chained lid and RCC top slab 1:2:4 mix (1 cement : 2 coarse sand : 4 graded stone aggregate 20mm nominal size ) , necessary excavation, foundation concrete 1:5:10(1 cement : 5 fine sand : 10 graded stone aggregate 40 mm nominalsize) and inside plastering with cement mortar 1:3 (1 cement : 3coarse sand) 12 mm thick, finished with a floating coat of neat cement complete as per standard specifications & direction of E/I. |  |  |  |  | 5 | Nos. | Each | 7210.6 | 36053
| Work for additional depth | [10 empty] | 4.9933
Brick work (1:4) in foundation
| 2 | 1.1 | 0.25 | 0.35 | 0.1925
| 2 | 0.6 | 0.25 | 0.35 | 0.105
6.1.12 |  |  |  |  | 0.2975 | 1.4875 | M3 | P/M3 | 5017.9 | 7464.1262
13.11.1 | Plaster (1:3)
| 8 | 1.1 |  | 0.35 | 3.08 | 15.4 | M2 | P/M2 | 164.3 | 2530.22
8 | Carriage 10% of item 9 | [8 empty] | 4604.7346
9A/ 18.48 | Providing and placing on terrace (at all floor levels) polyethylene water storage tank, ISI : 12701 marked, with cover and suitable locking arrangement and making necessary holes for inlet, outlet and overflow pipes but without fittings and the base support for tank. |  |  |  |  | 10000 | Ltrs. | P/Ltr. | 9.7 | 97000
9B | Providing and fixing MS clamp consisting of 32mm X 5mm thick two no. rings spaced suitably distance apart. | [7 empty] | LS | 3000
10A | Supplying all materials labours & fixing 50mm dia. G.I pipe for using as filling station etc. All as per direction of E/I
| 50mm dia. Pipe from distribution main |  |  |  |  | 3.5 | M | P/M | 572.6 | 2004.1
10B | Providing and fixing G.I fittings
| 80mmx80mmx50mm dia Tee |  |  |  |  | 1 | No | Each | 225 | 225
| 50mm dia bend |  |  |  |  | 3 | No | Each | 175 | 525
| Providing and fixing gun metal gate valve with C.I. wheel of approved quality (screwed end) :50mm nominal dia. |  |  |  |  | 1 | N | Each | 811.4 | 811.4
10C | Providing designation of 100 A brick Flat soling joints filled with local sand including cost of watering, taxes & royalty all complete as per specification & direction of E/I.
|  | 1 | 0.45 | 0.45 |  | 0.2025 | m2 | p/m2 | 283.3 | 57.3683
11 | Providing and fixing PTMT extension nipple for water tank pipe, fittings of approved quality and colour.
| 50mm dia |  |  |  |  | 2 | Nos. | each | 300 | 600
| 63mm dia |  |  |  |  | 1 | No. | each | 350 | 350
| 80 mm dia |  |  |  |  | 1 | No. | each | 550 | 550
| Sub Total of Part - I | [8 empty] | 0
Part - II
12 | Providing and laying High Density Polyethyene pipe (HDPE pipe) of 20 mm to 225 mm OD and pressure 6.0 Kg/cm2 and 10 Kg/cm2 sutable for water supply which is available in all standard, like ISI-4984/1995 and various grades like PE-80, PE-100 including required specials. Rates are inclusive of , all taxes and duties (Exise duty @12.50% &CST @2% against Form 'C'), labour cess, contractor profit and overhead charges all complete as per direction of Engineer-in-charge.
12A | HDPE pipe of materials grade PE100- PN10 (dia in mm)
| 110mm dia Pipe |  |  |  |  | 0 | M | P/M | 646.25 | 0
| 90mm dia Pipe |  |  |  |  | 150 | M | P/M | 437.96 | 65694
| 75mm dia Pipe |  |  |  |  | 300 | M | P/M | 306.31 | 91893
| 63mm dia Pipe |  |  |  |  | 400 | M | P/M | 218.62 | 87448
13B | HDPE pipe of materials grade PE100- PN8 (dia in mm)
| 50 mm dia Pipe |  |  |  |  | 350 | M | P/M | 116.25 | 40687.5
| 40mm dia Pipe |  |  |  |  | 350 | M | P/M | 76.53 | 26785.5
13C | Providing all materials labours tools, fittings , specials and tackles for fitting, jointing and connecting HDPE pipes. (5% of the cost of the HDPE pipe .) | [8 empty] | 15625.4
| Sub Total Of Part (II) | [8 empty] | 0
| Grand Total | [8 empty] | 976399.6088
JE |  |  |  | AE |  |  |  |  | Executive Engineer
P. H. Division, Hajipur.

## O & M (F2) (hidden)
Sub Estimate No.- 8A
Bajitpur Saidat Ward No. :-03B
Operation & maintance cost based on PHED compendium guidelines
Sl No | Description | Unit | Cost as DPR | As per yard stick publised in compendium page 203-205 dept(2001) | % annual Depreciation | Base year (After Trial ) cost | Quantity | Rate | Total Amount
1 | 2 | 3 | 4 | 5 |  | 6 | 7 | 8 | 9
Formula |  | Rt=[ 1+(r/100)]^t x (Base year O&M cost) |  | t= | 5 | Years | Proposal is for 5 years O & M
Total House Connection in Scheme |  |  |  | 75 |  | Total Population Surveyed |  | 375
A | Honorarium of pump operator 1 Nos. for 12 Month | per month |  |  |  |  | 12 | 4000 | 48000
| Sub Total(A) | [7 empty] | 48000 | (Final Rate)
B | Infrastruture Maintance
Formula 2 (With 5 years interval and constant component wise annual variable component wise depreciation rate:
| Masonary Chamber | per year | 14535 | 1% | 2 | 145.35 | 160.4781 |  | 160.4781
| Steel Staging | per year | 697000 | 0.5% | 1.5 | 3485 | 3754.3348 |  | 3754.3348
| Distrubution line | per year | 976399.6088 | 0.25% | 2 | 2440.999 | 2695.0602 |  | 2695.0602 |  | Masonary chamber+distribution+waste disposal pit
| House conection | per year | 186750 | 1% | 5 | 1867.5 | 2383.4558 |  | 2383.4558
| Chloronation/WTP | per year | 23515 | 0.5% | 2.5 | 117.575 | 133.0253 |  | 133.0253
[5 empty] | Sub Total | 8056.424 | 9126.3542 |  | 9126.3542 | civil work
| Pump Motar | per year | 105000 | 2.5% | 5 | 2625 | 3350.2391 |  | 3350.2391 | Elect. & Mech.
| Sub Total B | [7 empty] | 12476.5933
|  |  | 2003199.6088 |  | Sub Total B= | 10681.424 | 12476.5933 |  | 12476.5933
C | Cost of Chemical For 2PPM& 30% CL Solution
| (Total Population*81*2/1000000)*(100/30)*365 | Per litre |  |  |  |  | 73.9125 | 150 | 11086.875 |  |  | 16984.35 | 3057.183 | 13927.167 | 13927.167
| Sub Total C | [7 empty] | 11086.875
D | Cleaning of OHT including at an interval of 6 months and regular cleaning of campus | Job |  |  |  |  | 1 | 1000 | 1000
| Sub Total(D) | [7 empty] | 1000
[9 empty] | 12086.875 | (Including 18% GST)
| Total A+B+C+D | [7 empty] | 72563.4683 |  | 128419.738
E | Provision for water charges, 18% GST, 15% CPOH and 1 % Labour Cess (multiplying factor 1.4226 of Base Rate)=1.4226*(A+B+C+D) | [7 empty] | 103228.79
| Operation & Maintenance for One Year | [7 empty] | 103228.79
F | Operation & Maintenance for Five Year | [7 empty] | 516143.95
Executive Engineer
P.H. Division, Hajipur

## Bajitpur Saidat 03B (2) (hidden)
Sub Estimate no. - 3A
Bajitpur Saidat Ward No. :-03B
WATER SUPPLY DISTRIBUTION SYSTEM
S.N. | Particulars |  |  |  |  | Quantity |  | Unit | Rate | Amount
1/ 2.8 | Earthwork in excavation over areas (exceeding 30 cm in depth 1.5 in width as well as 10 sqm on plan) including disposal of excavated earth lead upto 50m and lift upto 1.5m, disposal earth to be levelled and neatly dressed.
| 110mm dia Pipe | 0 | 0.3 | 1.1 | = | 0 | [6 empty] | 152000
| 90mm dia Pipe | 150 | 0.3 | 1.1 | = | 49.5 | [6 empty] | 152000
| 75mm dia Pipe | 300 | 0.3 | 1.1 | = | 99
| 63mm dia Pipe | 400 | 0.3 | 1.1 | = | 132 | [6 empty] | 152000
| 50 mm dia Pipe | 350 | 0.3 | 1.1 | = | 115.5
| 40mm dia Pipe | 350 | 0.3 | 1.1 | = | 115.5
|  | 1550 |  |  |  | 511.5 | M3
| Add 5% extra for fittings = |  |  |  |  | 25.575 | M3
[6 empty] | 537.075 | M3 | P/M3 | 360.7 | 193722.9525
2/ 2.26 | Filling available excavated earth (excluding rock) in trenches, plinth, sides of foundations etc. in layers not exceeding 20cm in depth, consolidating each deposited layer by ramming and watering, lead up to 50 m and lift upto 1.5 m. |  |  |  |  | 526.3335 | M3 | P/M3 | 123.9 | 65212.7207
3/ 15.2.1 | Demolishing cement concrete manually/by mechanical means including disposal of material within 50 metres lead as per direction of Engineer - in - charge. | [8 empty] | 20316.0825
1:3:6 or richer mix
|  | 465 | 0.3 | 0.15 | = | 20.925 | M3 | P/M3 | 970.9
4/ 4.1.3 | Providing and laying in position cement concrete of specified grade excluding the cost of centering and shuttering all work upto plinth |  |  |  |  | 20.925 | M3 | P/M3 | 3998.1 | 83660.2425 | 4969
1:2:4 (1 cement: 2 coarse sand : 4 graded stone aggregate 40mm nominal size)
5 | Carriage of the following materials from quarry to work site including loading, unloading and staking at work site as per specification & direction of E/I.
| Coarse Sand (44Km Pucca & 1Km Kaccha Carriage) |  |  |  |  | 9.6255 | M3 | P/M3 | 1160.62 | 11171.5478
| Stone chips (195Km Pucca & 5Km unsurafced Carriage) |  |  |  |  | 19.251 | M3 | P/M3 | 4291.17 | 82609.3137
6A/ 18.12 | Providing and fixing G.I.Pipes complete with G.I. Fittings including trenching and refilling etc.
18.12.6 | 50mm dia G.I.Pipe from T/well to PVC Tank |  |  |  |  | 14 | M | P/M | 572.6 | 8016.4 |  |  |  | 611.3975
18.12.8 | 80mm dia G.I.Pipe from PVC Tank to Distribution main |  |  |  |  | 14 | M | P/M | 818.2 | 11454.8
18.12.7 | 65mm dia G.I.Pipe for wash out |  |  |  |  | 12 | M | P/M | 667.7 | 8012.4
7A/ 18.31.1.1 | P/F C.I sluice Valve (with Cap) complete with bolts,nuts,rubber insertions etc
6B/ | Providing and fixing brass gate valve with C.I. wheel of approved quality (screwed end).
| 80mm dia Pipe |  |  |  |  | 2 | Nos. | Each | 2227.6 | 4455.2
| 65mm dia Pipe |  |  |  |  | 2 | Nos. | Each | 1490.7 | 2981.4
| 50mm dia Pipe |  |  |  |  | 1 | Nos. | Each | 878.2 | 878.2
7/ 18.33 | Constructing masonry Chamber 60x60x75 cm inside, in brick work in cement mortar 1:4 (1 cement : 4 coarse sand) for sluice valve,with C.I. surface box 100mm top diameter, 160 mm bottom diameter and 180 mm deep ( inside) with chained lid and RCC top slab 1:2:4 mix (1 cement : 2 coarse sand : 4 graded stone aggregate 20mm nominal size ) , necessary excavation, foundation concrete 1:5:10(1 cement : 5 fine sand : 10 graded stone aggregate 40 mm nominalsize) and inside plastering with cement mortar 1:3 (1 cement : 3coarse sand) 12 mm thick, finished with a floating coat of neat cement complete as per standard specifications & direction of E/I. |  |  |  |  | 5 | Nos. | Each | 7210.6 | 36053
| Work for additional depth | [10 empty] | 4.9933
Brick work (1:4) in foundation
| 2 | 1.1 | 0.25 | 0.35 | 0.1925
| 2 | 0.6 | 0.25 | 0.35 | 0.105
6.1.12 |  |  |  |  | 0.2975 | 1.4875 | M3 | P/M3 | 5017.9 | 7464.1262
13.11.1 | Plaster (1:3)
| 8 | 1.1 |  | 0.35 | 3.08 | 15.4 | M2 | P/M2 | 164.3 | 2530.22
8 | Carriage 10% of item 9 | [8 empty] | 4604.7346
9A/ 18.48 | Providing and placing on terrace (at all floor levels) polyethylene water storage tank, ISI : 12701 marked, with cover and suitable locking arrangement and making necessary holes for inlet, outlet and overflow pipes but without fittings and the base support for tank. |  |  |  |  | 10000 | Ltrs. | P/Ltr. | 9.7 | 97000
9B | Providing and fixing MS clamp consisting of 32mm X 5mm thick two no. rings spaced suitably distance apart. | [7 empty] | LS | 3000
10A | Supplying all materials labours & fixing 50mm dia. G.I pipe for using as filling station etc. All as per direction of E/I
| 50mm dia. Pipe from distribution main |  |  |  |  | 3.5 | M | P/M | 572.6 | 2004.1
10B | Providing and fixing G.I fittings
| 80mmx80mmx50mm dia Tee |  |  |  |  | 1 | No | Each | 225 | 225
| 50mm dia bend |  |  |  |  | 3 | No | Each | 175 | 525
| Providing and fixing gun metal gate valve with C.I. wheel of approved quality (screwed end) :50mm nominal dia. |  |  |  |  | 1 | N | Each | 811.4 | 811.4
10C | Providing designation of 100 A brick Flat soling joints filled with local sand including cost of watering, taxes & royalty all complete as per specification & direction of E/I.
|  | 1 | 0.45 | 0.45 |  | 0.2025 | m2 | p/m2 | 283.3 | 57.3683
11 | Providing and fixing PTMT extension nipple for water tank pipe, fittings of approved quality and colour.
| 50mm dia |  |  |  |  | 2 | Nos. | each | 300 | 600
| 63mm dia |  |  |  |  | 1 | No. | each | 350 | 350
| 80 mm dia |  |  |  |  | 1 | No. | each | 550 | 550
| Sub Total of Part - I | [8 empty] | 0
Part - II
12 | Providing and laying High Density Polyethyene pipe (HDPE pipe) of 20 mm to 225 mm OD and pressure 6.0 Kg/cm2 and 10 Kg/cm2 sutable for water supply which is available in all standard, like ISI-4984/1995 and various grades like PE-80, PE-100 including required specials. Rates are inclusive of , all taxes and duties (Exise duty @12.50% &CST @2% against Form 'C'), labour cess, contractor profit and overhead charges all complete as per direction of Engineer-in-charge.
12A | HDPE pipe of materials grade PE100- PN10 (dia in mm)
| 110mm dia Pipe |  |  |  |  | 0 | M | P/M | 646.25 | 0
| 90mm dia Pipe |  |  |  |  | 150 | M | P/M | 437.96 | 65694
| 75mm dia Pipe |  |  |  |  | 300 | M | P/M | 306.31 | 91893
| 63mm dia Pipe |  |  |  |  | 400 | M | P/M | 218.62 | 87448
13B | HDPE pipe of materials grade PE100- PN8 (dia in mm)
| 50 mm dia Pipe |  |  |  |  | 350 | M | P/M | 116.25 | 40687.5
| 40mm dia Pipe |  |  |  |  | 350 | M | P/M | 76.53 | 26785.5
13C | Providing all materials labours tools, fittings , specials and tackles for fitting, jointing and connecting HDPE pipes. (5% of the cost of the HDPE pipe .) | [8 empty] | 15625.4
| Sub Total Of Part (II) | [8 empty] | 0
| Grand Total | [8 empty] | 976399.6088
JE |  |  |  | AE |  |  |  |  | Executive Engineer
P. H. Division, Hajipur.

## Bajitpur Saidat 05B (hidden)
Sub Estimate no. - 3B
Bajitpur Saidat Ward No. :-05B
WATER SUPPLY DISTRIBUTION SYSTEM
S.N. | Particulars |  |  |  |  | Quantity |  | Unit | Rate | Amount
1/ 2.8 | Earthwork in excavation over areas (exceeding 30 cm in depth 1.5 in width as well as 10 sqm on plan) including disposal of excavated earth lead upto 50m and lift upto 1.5m, disposal earth to be levelled and neatly dressed.
| 110mm dia Pipe | 0 | 0.3 | 1.1 | = | 0 | [6 empty] | 152000
| 90mm dia Pipe | 100 | 0.3 | 1.1 | = | 33 | [6 empty] | 152000
| 75mm dia Pipe | 250 | 0.3 | 1.1 | = | 82.5
| 63mm dia Pipe | 250 | 0.3 | 1.1 | = | 82.5 | [6 empty] | 152000
| 50 mm dia Pipe | 200 | 0.3 | 1.1 | = | 66
| 40mm dia Pipe | 350 | 0.3 | 1.1 | = | 115.5
|  | 1150 |  |  |  | 379.5 | M3
| Add 5% extra for fittings = |  |  |  |  | 18.975 | M3
[6 empty] | 398.475 | M3 | P/M3 | 360.7 | 143729.9325
2/ 2.26 | Filling available excavated earth (excluding rock) in trenches, plinth, sides of foundations etc. in layers not exceeding 20cm in depth, consolidating each deposited layer by ramming and watering, lead up to 50 m and lift upto 1.5 m. |  |  |  |  | 390.5055 | M3 | P/M3 | 123.9 | 48383.6315
3/ 15.2.1 | Demolishing cement concrete manually/by mechanical means including disposal of material within 50 metres lead as per direction of Engineer - in - charge. | [8 empty] | 15073.2225
1:3:6 or richer mix
|  | 345 | 0.3 | 0.15 | = | 15.525 | M3 | P/M3 | 970.9
4/ 4.1.3 | Providing and laying in position cement concrete of specified grade excluding the cost of centering and shuttering all work upto plinth |  |  |  |  | 15.525 | M3 | P/M3 | 3998.1 | 62070.5025 | 4969
1:2:4 (1 cement: 2 coarse sand : 4 graded stone aggregate 40mm nominal size)
5 | Carriage of the following materials from quarry to work site including loading, unloading and staking at work site as per specification & direction of E/I.
| Coarse Sand (44Km Pucca & 1Km Kaccha Carriage) |  |  |  |  | 7.1415 | M3 | P/M3 | 1160.62 | 8288.5677
| Stone chips (195Km Pucca & 5Km unsurafced Carriage) |  |  |  |  | 14.283 | M3 | P/M3 | 4291.17 | 61290.7811
6A/ 18.12 | Providing and fixing G.I.Pipes complete with G.I. Fittings including trenching and refilling etc.
18.12.6 | 50mm dia G.I.Pipe from T/well to PVC Tank |  |  |  |  | 14 | M | P/M | 572.6 | 8016.4 |  |  |  | 611.3975
18.12.8 | 80mm dia G.I.Pipe from PVC Tank to Distribution main |  |  |  |  | 14 | M | P/M | 818.2 | 11454.8
18.12.7 | 65mm dia G.I.Pipe for wash out |  |  |  |  | 12 | M | P/M | 667.7 | 8012.4
7A/ 18.31.1.1 | P/F C.I sluice Valve (with Cap) complete with bolts,nuts,rubber insertions etc
6B/ | Providing and fixing brass gate valve with C.I. wheel of approved quality (screwed end).
| 80mm dia Pipe |  |  |  |  | 2 | Nos. | Each | 2227.6 | 4455.2
| 65mm dia Pipe |  |  |  |  | 2 | Nos. | Each | 1490.7 | 2981.4
| 50mm dia Pipe |  |  |  |  | 2 | Nos. | Each | 878.2 | 1756.4
7/ 18.33 | Constructing masonry Chamber 60x60x75 cm inside, in brick work in cement mortar 1:4 (1 cement : 4 coarse sand) for sluice valve,with C.I. surface box 100mm top diameter, 160 mm bottom diameter and 180 mm deep ( inside) with chained lid and RCC top slab 1:2:4 mix (1 cement : 2 coarse sand : 4 graded stone aggregate 20mm nominal size ) , necessary excavation, foundation concrete 1:5:10(1 cement : 5 fine sand : 10 graded stone aggregate 40 mm nominalsize) and inside plastering with cement mortar 1:3 (1 cement : 3coarse sand) 12 mm thick, finished with a floating coat of neat cement complete as per standard specifications & direction of E/I. |  |  |  |  | 6 | Nos. | Each | 7210.6 | 43263.6
| Work for additional depth | [10 empty] | 4.9933
Brick work (1:4) in foundation
| 2 | 1.1 | 0.25 | 0.35 | 0.1925
| 2 | 0.6 | 0.25 | 0.35 | 0.105
6.1.12 |  |  |  |  | 0.2975 | 1.785 | M3 | P/M3 | 5017.9 | 8956.9515
13.11.1 | Plaster (1:3)
| 8 | 1.1 |  | 0.35 | 3.08 | 18.48 | M2 | P/M2 | 164.3 | 3036.264
8 | Carriage 10% of item 9 | [8 empty] | 5525.6816
9A/ 18.48 | Providing and placing on terrace (at all floor levels) polyethylene water storage tank, ISI : 12701 marked, with cover and suitable locking arrangement and making necessary holes for inlet, outlet and overflow pipes but without fittings and the base support for tank. |  |  |  |  | 10000 | Ltrs. | P/Ltr. | 9.7 | 97000
9B | Providing and fixing MS clamp consisting of 32mm X 5mm thick two no. rings spaced suitably distance apart. | [7 empty] | LS | 3000
10A | Supplying all materials labours & fixing 50mm dia. G.I pipe for using as filling station etc. All as per direction of E/I
| 50mm dia. Pipe from distribution main |  |  |  |  | 3.5 | M | P/M | 572.6 | 2004.1
10B | Providing and fixing G.I fittings
| 80mmx80mmx50mm dia Tee |  |  |  |  | 1 | No | Each | 225 | 225
| 50mm dia bend |  |  |  |  | 3 | No | Each | 175 | 525
| Providing and fixing gun metal gate valve with C.I. wheel of approved quality (screwed end) :50mm nominal dia. |  |  |  |  | 1 | N | Each | 811.4 | 811.4
10C | Providing designation of 100 A brick Flat soling joints filled with local sand including cost of watering, taxes & royalty all complete as per specification & direction of E/I.
|  | 1 | 0.45 | 0.45 |  | 0.2025 | m2 | p/m2 | 283.3 | 57.3683
11 | Providing and fixing PTMT extension nipple for water tank pipe, fittings of approved quality and colour.
| 50mm dia |  |  |  |  | 2 | Nos. | each | 300 | 600
| 63mm dia |  |  |  |  | 1 | No. | each | 350 | 350
| 80 mm dia |  |  |  |  | 1 | No. | each | 550 | 550
| Sub Total of Part - I | [8 empty] | 0
Part - II
12 | Providing and laying High Density Polyethyene pipe (HDPE pipe) of 20 mm to 225 mm OD and pressure 6.0 Kg/cm2 and 10 Kg/cm2 sutable for water supply which is available in all standard, like ISI-4984/1995 and various grades like PE-80, PE-100 including required specials. Rates are inclusive of , all taxes and duties (Exise duty @12.50% &CST @2% against Form 'C'), labour cess, contractor profit and overhead charges all complete as per direction of Engineer-in-charge.
12A | HDPE pipe of materials grade PE100- PN10 (dia in mm)
| 110mm dia Pipe |  |  |  |  | 0 | M | P/M | 646.25 | 0
| 90mm dia Pipe |  |  |  |  | 100 | M | P/M | 437.96 | 43796
| 75mm dia Pipe |  |  |  |  | 250 | M | P/M | 306.31 | 76577.5
| 63mm dia Pipe |  |  |  |  | 250 | M | P/M | 218.62 | 54655
13B | HDPE pipe of materials grade PE100- PN8 (dia in mm)
| 50 mm dia Pipe |  |  |  |  | 200 | M | P/M | 116.25 | 23250
| 40mm dia Pipe |  |  |  |  | 350 | M | P/M | 76.53 | 26785.5
13C | Providing all materials labours tools, fittings , specials and tackles for fitting, jointing and connecting HDPE pipes. (5% of the cost of the HDPE pipe .) | [8 empty] | 11253.2
| Sub Total Of Part (II) | [8 empty] | 0
| Grand Total | [8 empty] | 777735.8031
JE |  |  |  | AE |  |  |  |  | Executive Engineer
P. H. Division, Hajipur.

## Bajitpur Saidat 09B&13B (2) (hidden)
Sub Estimate no. - 3C
Bajitpur Saidat Ward No. :-09B&13B
WATER SUPPLY DISTRIBUTION SYSTEM
S.N. | Particulars |  |  |  |  | Quantity |  | Unit | Rate | Amount
1/ 2.8 | Earthwork in excavation over areas (exceeding 30 cm in depth 1.5 in width as well as 10 sqm on plan) including disposal of excavated earth lead upto 50m and lift upto 1.5m, disposal earth to be levelled and neatly dressed.
| 110mm dia Pipe | 0 | 0.3 | 1.1 | = | 0 | [6 empty] | 152000
| 90mm dia Pipe | 100 | 0.3 | 1.1 | = | 33 | [6 empty] | 152000
| 75mm dia Pipe | 250 | 0.3 | 1.1 | = | 82.5
| 63mm dia Pipe | 250 | 0.3 | 1.1 | = | 82.5 | [6 empty] | 152000
| 50 mm dia Pipe | 200 | 0.3 | 1.1 | = | 66
| 40mm dia Pipe | 200 | 0.3 | 1.1 | = | 66
|  | 1000 |  |  |  | 330 | M3
| Add 5% extra for fittings = |  |  |  |  | 16.5 | M3
[6 empty] | 346.5 | M3 | P/M3 | 360.7 | 124982.55
2/ 2.26 | Filling available excavated earth (excluding rock) in trenches, plinth, sides of foundations etc. in layers not exceeding 20cm in depth, consolidating each deposited layer by ramming and watering, lead up to 50 m and lift upto 1.5 m. |  |  |  |  | 339.57 | M3 | P/M3 | 123.9 | 42072.723
3/ 15.2.1 | Demolishing cement concrete manually/by mechanical means including disposal of material within 50 metres lead as per direction of Engineer - in - charge. | [8 empty] | 13107.15
1:3:6 or richer mix
|  | 300 | 0.3 | 0.15 | = | 13.5 | M3 | P/M3 | 970.9
4/ 4.1.3 | Providing and laying in position cement concrete of specified grade excluding the cost of centering and shuttering all work upto plinth |  |  |  |  | 13.5 | M3 | P/M3 | 3998.1 | 53974.35 | 4969
1:2:4 (1 cement: 2 coarse sand : 4 graded stone aggregate 40mm nominal size)
5 | Carriage of the following materials from quarry to work site including loading, unloading and staking at work site as per specification & direction of E/I.
| Coarse Sand (44Km Pucca & 1Km Kaccha Carriage) |  |  |  |  | 6.21 | M3 | P/M3 | 1160.62 | 7207.4502
| Stone chips (195Km Pucca & 5Km unsurafced Carriage) |  |  |  |  | 12.42 | M3 | P/M3 | 4291.17 | 53296.3314
6A/ 18.12 | Providing and fixing G.I.Pipes complete with G.I. Fittings including trenching and refilling etc.
18.12.6 | 50mm dia G.I.Pipe from T/well to PVC Tank |  |  |  |  | 14 | M | P/M | 572.6 | 8016.4 |  |  |  | 611.3975
18.12.8 | 80mm dia G.I.Pipe from PVC Tank to Distribution main |  |  |  |  | 14 | M | P/M | 818.2 | 11454.8
18.12.7 | 65mm dia G.I.Pipe for wash out |  |  |  |  | 12 | M | P/M | 667.7 | 8012.4
7A/ 18.31.1.1 | P/F C.I sluice Valve (with Cap) complete with bolts,nuts,rubber insertions etc
6B/ | Providing and fixing brass gate valve with C.I. wheel of approved quality (screwed end).
| 80mm dia Pipe |  |  |  |  | 2 | Nos. | Each | 2227.6 | 4455.2
| 65mm dia Pipe |  |  |  |  | 1 | Nos. | Each | 1490.7 | 1490.7
| 50mm dia Pipe |  |  |  |  | 1 | Nos. | Each | 878.2 | 878.2
7/ 18.33 | Constructing masonry Chamber 60x60x75 cm inside, in brick work in cement mortar 1:4 (1 cement : 4 coarse sand) for sluice valve,with C.I. surface box 100mm top diameter, 160 mm bottom diameter and 180 mm deep ( inside) with chained lid and RCC top slab 1:2:4 mix (1 cement : 2 coarse sand : 4 graded stone aggregate 20mm nominal size ) , necessary excavation, foundation concrete 1:5:10(1 cement : 5 fine sand : 10 graded stone aggregate 40 mm nominalsize) and inside plastering with cement mortar 1:3 (1 cement : 3coarse sand) 12 mm thick, finished with a floating coat of neat cement complete as per standard specifications & direction of E/I. |  |  |  |  | 4 | Nos. | Each | 7210.6 | 28842.4
| Work for additional depth | [10 empty] | 4.9933
Brick work (1:4) in foundation
| 2 | 1.1 | 0.25 | 0.35 | 0.1925
| 2 | 0.6 | 0.25 | 0.35 | 0.105
6.1.12 |  |  |  |  | 0.2975 | 1.19 | M3 | P/M3 | 5017.9 | 5971.301
13.11.1 | Plaster (1:3)
| 8 | 1.1 |  | 0.35 | 3.08 | 12.32 | M2 | P/M2 | 164.3 | 2024.176
8 | Carriage 10% of item 9 | [8 empty] | 3683.7877
9A/ 18.48 | Providing and placing on terrace (at all floor levels) polyethylene water storage tank, ISI : 12701 marked, with cover and suitable locking arrangement and making necessary holes for inlet, outlet and overflow pipes but without fittings and the base support for tank. |  |  |  |  | 10000 | Ltrs. | P/Ltr. | 9.7 | 97000
9B | Providing and fixing MS clamp consisting of 32mm X 5mm thick two no. rings spaced suitably distance apart. | [7 empty] | LS | 3000
10A | Supplying all materials labours & fixing 50mm dia. G.I pipe for using as filling station etc. All as per direction of E/I
| 50mm dia. Pipe from distribution main |  |  |  |  | 3.5 | M | P/M | 572.6 | 2004.1
10B | Providing and fixing G.I fittings
| 80mmx80mmx50mm dia Tee |  |  |  |  | 1 | No | Each | 225 | 225
| 50mm dia bend |  |  |  |  | 3 | No | Each | 175 | 525
| Providing and fixing gun metal gate valve with C.I. wheel of approved quality (screwed end) :50mm nominal dia. |  |  |  |  | 1 | N | Each | 811.4 | 811.4
10C | Providing designation of 100 A brick Flat soling joints filled with local sand including cost of watering, taxes & royalty all complete as per specification & direction of E/I.
|  | 1 | 0.45 | 0.45 |  | 0.2025 | m2 | p/m2 | 283.3 | 57.3683
11 | Providing and fixing PTMT extension nipple for water tank pipe, fittings of approved quality and colour.
| 50mm dia |  |  |  |  | 2 | Nos. | each | 300 | 600
| 63mm dia |  |  |  |  | 1 | No. | each | 350 | 350
| 80 mm dia |  |  |  |  | 1 | No. | each | 550 | 550
| Sub Total of Part - I | [8 empty] | 0
Part - II
12 | Providing and laying High Density Polyethyene pipe (HDPE pipe) of 20 mm to 225 mm OD and pressure 6.0 Kg/cm2 and 10 Kg/cm2 sutable for water supply which is available in all standard, like ISI-4984/1995 and various grades like PE-80, PE-100 including required specials. Rates are inclusive of , all taxes and duties (Exise duty @12.50% &CST @2% against Form 'C'), labour cess, contractor profit and overhead charges all complete as per direction of Engineer-in-charge.
12A | HDPE pipe of materials grade PE100- PN10 (dia in mm)
| 110mm dia Pipe |  |  |  |  | 0 | M | P/M | 646.25 | 0
| 90mm dia Pipe |  |  |  |  | 100 | M | P/M | 437.96 | 43796
| 75mm dia Pipe |  |  |  |  | 250 | M | P/M | 306.31 | 76577.5
| 63mm dia Pipe |  |  |  |  | 250 | M | P/M | 218.62 | 54655
13B | HDPE pipe of materials grade PE100- PN8 (dia in mm)
| 50 mm dia Pipe |  |  |  |  | 200 | M | P/M | 116.25 | 23250
| 40mm dia Pipe |  |  |  |  | 200 | M | P/M | 76.53 | 15306
13C | Providing all materials labours tools, fittings , specials and tackles for fitting, jointing and connecting HDPE pipes. (5% of the cost of the HDPE pipe .) | [8 empty] | 10679.225
| Sub Total Of Part (II) | [8 empty] | 0
| Grand Total | [8 empty] | 698856.5125
JE |  |  |  | AE |  |  |  |  | Executive Engineer
P. H. Division, Hajipur.

## Bidupur (hidden)
Sub Estimate no. - 3
BIDUPUR BIDUPUR 12B YADAV TOLA
WATER SUPPLY DISTRIBUTION SYSTEM
S.N. | Particulars |  |  |  |  | Quantity |  | Unit | Rate | Amount
1/ 2.8 | Earthwork in excavation over areas (exceeding 30 cm in depth 1.5 in width as well as 10 sqm on plan) including disposal of excavated earth lead upto 50m and lift upto 1.5m, disposal earth to be levelled and neatly dressed.
| 110mm dia Pipe | 0 | 0.3 | 1.1 | = | 0 | [6 empty] | 152000
| 90mm dia Pipe | 100 | 0.3 | 1.1 | = | 33 | [6 empty] | 152000
| 75mm dia Pipe | 200 | 0.3 | 1.1 | = | 66
| 63mm dia Pipe | 250 | 0.3 | 1.1 | = | 82.5 | [6 empty] | 152000
| 50 mm dia Pipe | 250 | 0.3 | 1.1 | = | 82.5
| 40mm dia Pipe | 200 | 0.3 | 1.1 | = | 66
|  | 1000 |  |  |  | 330 | M3
| Add 5% extra for fittings = |  |  |  |  | 16.5 | M3
[6 empty] | 346.5 | M3 | P/M3 | 360.7 | 124982.55
2/ 2.26 | Filling available excavated earth (excluding rock) in trenches, plinth, sides of foundations etc. in layers not exceeding 20cm in depth, consolidating each deposited layer by ramming and watering, lead up to 50 m and lift upto 1.5 m. |  |  |  |  | 339.57 | M3 | P/M3 | 123.9 | 42072.723
3/ 15.2.1 | Demolishing cement concrete manually/by mechanical means including disposal of material within 50 metres lead as per direction of Engineer - in - charge. | [8 empty] | 13107.15
1:3:6 or richer mix
|  | 300 | 0.3 | 0.15 | = | 13.5 | M3 | P/M3 | 970.9
4/ 4.1.3 | Providing and laying in position cement concrete of specified grade excluding the cost of centering and shuttering all work upto plinth |  |  |  |  | 13.5 | M3 | P/M3 | 3998.1 | 53974.35 | 4969
1:2:4 (1 cement: 2 coarse sand : 4 graded stone aggregate 40mm nominal size)
5 | Carriage of the following materials from quarry to work site including loading, unloading and staking at work site as per specification & direction of E/I.
| Coarse Sand (44Km Pucca & 1Km Kaccha Carriage) |  |  |  |  | 6.21 | M3 | P/M3 | 1160.62 | 7207.4502
| Stone chips (195Km Pucca & 5Km unsurafced Carriage) |  |  |  |  | 12.42 | M3 | P/M3 | 4291.17 | 53296.3314
6A/ 18.12 | Providing and fixing G.I.Pipes complete with G.I. Fittings including trenching and refilling etc.
18.12.6 | 50mm dia G.I.Pipe from T/well to PVC Tank |  |  |  |  | 14 | M | P/M | 572.6 | 8016.4 |  |  |  | 611.3975
18.12.8 | 80mm dia G.I.Pipe from PVC Tank to Distribution main |  |  |  |  | 14 | M | P/M | 818.2 | 11454.8
18.12.7 | 65mm dia G.I.Pipe for wash out |  |  |  |  | 12 | M | P/M | 667.7 | 8012.4
7A/ 18.31.1.1 | P/F C.I sluice Valve (with Cap) complete with bolts,nuts,rubber insertions etc
6B/ | Providing and fixing brass gate valve with C.I. wheel of approved quality (screwed end).
| 80mm dia Pipe |  |  |  |  | 2 | Nos. | Each | 2227.6 | 4455.2
| 65mm dia Pipe |  |  |  |  | 2 | Nos. | Each | 1490.7 | 2981.4
| 50mm dia Pipe |  |  |  |  | 2 | Nos. | Each | 878.2 | 1756.4
7/ 18.33 | Constructing masonry Chamber 60x60x75 cm inside, in brick work in cement mortar 1:4 (1 cement : 4 coarse sand) for sluice valve,with C.I. surface box 100mm top diameter, 160 mm bottom diameter and 180 mm deep ( inside) with chained lid and RCC top slab 1:2:4 mix (1 cement : 2 coarse sand : 4 graded stone aggregate 20mm nominal size ) , necessary excavation, foundation concrete 1:5:10(1 cement : 5 fine sand : 10 graded stone aggregate 40 mm nominalsize) and inside plastering with cement mortar 1:3 (1 cement : 3coarse sand) 12 mm thick, finished with a floating coat of neat cement complete as per standard specifications & direction of E/I. |  |  |  |  | 6 | Nos. | Each | 7210.6 | 43263.6
| Work for additional depth | [10 empty] | 4.9933
Brick work (1:4) in foundation
| 2 | 1.1 | 0.25 | 0.35 | 0.1925
| 2 | 0.6 | 0.25 | 0.35 | 0.105
6.1.12 |  |  |  |  | 0.2975 | 1.785 | M3 | P/M3 | 5017.9 | 8956.9515
13.11.1 | Plaster (1:3)
| 8 | 1.1 |  | 0.35 | 3.08 | 18.48 | M2 | P/M2 | 164.3 | 3036.264
8 | Carriage 10% of item 9 | [8 empty] | 5525.6816
9A/ 18.48 | Providing and placing on terrace (at all floor levels) polyethylene water storage tank, ISI : 12701 marked, with cover and suitable locking arrangement and making necessary holes for inlet, outlet and overflow pipes but without fittings and the base support for tank. |  |  |  |  | 10000 | Ltrs. | P/Ltr. | 9.7 | 97000
9B | Providing and fixing MS clamp consisting of 32mm X 5mm thick two no. rings spaced suitably distance apart. | [7 empty] | LS | 3000
10A | Supplying all materials labours & fixing 50mm dia. G.I pipe for using as filling station etc. All as per direction of E/I
| 50mm dia. Pipe from distribution main |  |  |  |  | 3.5 | M | P/M | 572.6 | 2004.1
10B | Providing and fixing G.I fittings
| 80mmx80mmx50mm dia Tee |  |  |  |  | 1 | No | Each | 225 | 225
| 50mm dia bend |  |  |  |  | 3 | No | Each | 175 | 525
| Providing and fixing gun metal gate valve with C.I. wheel of approved quality (screwed end) :50mm nominal dia. |  |  |  |  | 1 | N | Each | 811.4 | 811.4
10C | Providing designation of 100 A brick Flat soling joints filled with local sand including cost of watering, taxes & royalty all complete as per specification & direction of E/I.
|  | 1 | 0.45 | 0.45 |  | 0.2025 | m2 | p/m2 | 283.3 | 57.3683
11 | Providing and fixing PTMT extension nipple for water tank pipe, fittings of approved quality and colour.
| 50mm dia |  |  |  |  | 2 | Nos. | each | 300 | 600
| 63mm dia |  |  |  |  | 1 | No. | each | 350 | 350
| 80 mm dia |  |  |  |  | 1 | No. | each | 550 | 550
| Sub Total of Part - I | [8 empty] | 0
Part - II
12 | Providing and laying High Density Polyethyene pipe (HDPE pipe) of 20 mm to 225 mm OD and pressure 6.0 Kg/cm2 and 10 Kg/cm2 sutable for water supply which is available in all standard, like ISI-4984/1995 and various grades like PE-80, PE-100 including required specials. Rates are inclusive of , all taxes and duties (Exise duty @12.50% &CST @2% against Form 'C'), labour cess, contractor profit and overhead charges all complete as per direction of Engineer-in-charge.
12A | HDPE pipe of materials grade PE100- PN10 (dia in mm)
| 110mm dia Pipe |  |  |  |  | 0 | M | P/M | 646.25 | 0
| 90mm dia Pipe |  |  |  |  | 100 | M | P/M | 437.96 | 43796
| 75mm dia Pipe |  |  |  |  | 200 | M | P/M | 306.31 | 61262
| 63mm dia Pipe |  |  |  |  | 250 | M | P/M | 218.62 | 54655
13B | HDPE pipe of materials grade PE100- PN8 (dia in mm)
| 50 mm dia Pipe |  |  |  |  | 250 | M | P/M | 116.25 | 29062.5
| 40mm dia Pipe |  |  |  |  | 200 | M | P/M | 76.53 | 15306
13C | Providing all materials labours tools, fittings , specials and tackles for fitting, jointing and connecting HDPE pipes. (5% of the cost of the HDPE pipe .) | [8 empty] | 10204.075
| Sub Total Of Part (II) | [8 empty] | 0
| Grand Total | [8 empty] | 711508.0949
Executive Engineer
P. H. Division, Hajipur.

## Chakat Kursi Kushyari 02B (hidden)
Sub Estimate no. - 3A
Chakat Kursi Kushyari Ward No. :-02B
WATER SUPPLY DISTRIBUTION SYSTEM
S.N. | Particulars |  |  |  |  | Quantity |  | Unit | Rate | Amount
1/ 2.8 | Earthwork in excavation over areas (exceeding 30 cm in depth 1.5 in width as well as 10 sqm on plan) including disposal of excavated earth lead upto 50m and lift upto 1.5m, disposal earth to be levelled and neatly dressed.
| 110mm dia Pipe | 0 | 0.3 | 1.1 | = | 0 | [6 empty] | 152000
| 90mm dia Pipe | 100 | 0.3 | 1.1 | = | 33 | [6 empty] | 152000
| 75mm dia Pipe | 250 | 0.3 | 1.1 | = | 82.5
| 63mm dia Pipe | 250 | 0.3 | 1.1 | = | 82.5 | [6 empty] | 152000
| 50 mm dia Pipe | 300 | 0.3 | 1.1 | = | 99
| 40mm dia Pipe | 300 | 0.3 | 1.1 | = | 99
|  | 1200 |  |  |  | 396 | M3
| Add 5% extra for fittings = |  |  |  |  | 19.8 | M3
[6 empty] | 415.8 | M3 | P/M3 | 360.7 | 149979.06
2/ 2.26 | Filling available excavated earth (excluding rock) in trenches, plinth, sides of foundations etc. in layers not exceeding 20cm in depth, consolidating each deposited layer by ramming and watering, lead up to 50 m and lift upto 1.5 m. |  |  |  |  | 407.484 | M3 | P/M3 | 123.9 | 50487.2676
3/ 15.2.1 | Demolishing cement concrete manually/by mechanical means including disposal of material within 50 metres lead as per direction of Engineer - in - charge. | [8 empty] | 15728.58
1:3:6 or richer mix
|  | 360 | 0.3 | 0.15 | = | 16.2 | M3 | P/M3 | 970.9
4/ 4.1.3 | Providing and laying in position cement concrete of specified grade excluding the cost of centering and shuttering all work upto plinth |  |  |  |  | 16.2 | M3 | P/M3 | 3998.1 | 64769.22 | 4969
1:2:4 (1 cement: 2 coarse sand : 4 graded stone aggregate 40mm nominal size)
5 | Carriage of the following materials from quarry to work site including loading, unloading and staking at work site as per specification & direction of E/I.
| Coarse Sand (44Km Pucca & 1Km Kaccha Carriage) |  |  |  |  | 7.452 | M3 | P/M3 | 1160.62 | 8648.9402
| Stone chips (195Km Pucca & 5Km unsurafced Carriage) |  |  |  |  | 14.904 | M3 | P/M3 | 4291.17 | 63955.5977
6A/ 18.12 | Providing and fixing G.I.Pipes complete with G.I. Fittings including trenching and refilling etc.
18.12.6 | 50mm dia G.I.Pipe from T/well to PVC Tank |  |  |  |  | 14 | M | P/M | 572.6 | 8016.4 |  |  |  | 611.3975
18.12.8 | 80mm dia G.I.Pipe from PVC Tank to Distribution main |  |  |  |  | 14 | M | P/M | 818.2 | 11454.8
18.12.7 | 65mm dia G.I.Pipe for wash out |  |  |  |  | 12 | M | P/M | 667.7 | 8012.4
7A/ 18.31.1.1 | P/F C.I sluice Valve (with Cap) complete with bolts,nuts,rubber insertions etc
6B/ | Providing and fixing brass gate valve with C.I. wheel of approved quality (screwed end).
| 80mm dia Pipe |  |  |  |  | 2 | Nos. | Each | 2227.6 | 4455.2
| 65mm dia Pipe |  |  |  |  | 2 | Nos. | Each | 1490.7 | 2981.4
| 50mm dia Pipe |  |  |  |  | 1 | Nos. | Each | 878.2 | 878.2
7/ 18.33 | Constructing masonry Chamber 60x60x75 cm inside, in brick work in cement mortar 1:4 (1 cement : 4 coarse sand) for sluice valve,with C.I. surface box 100mm top diameter, 160 mm bottom diameter and 180 mm deep ( inside) with chained lid and RCC top slab 1:2:4 mix (1 cement : 2 coarse sand : 4 graded stone aggregate 20mm nominal size ) , necessary excavation, foundation concrete 1:5:10(1 cement : 5 fine sand : 10 graded stone aggregate 40 mm nominalsize) and inside plastering with cement mortar 1:3 (1 cement : 3coarse sand) 12 mm thick, finished with a floating coat of neat cement complete as per standard specifications & direction of E/I. |  |  |  |  | 5 | Nos. | Each | 7210.6 | 36053
| Work for additional depth | [10 empty] | 4.9933
Brick work (1:4) in foundation
| 2 | 1.1 | 0.25 | 0.35 | 0.1925
| 2 | 0.6 | 0.25 | 0.35 | 0.105
6.1.12 |  |  |  |  | 0.2975 | 1.4875 | M3 | P/M3 | 5017.9 | 7464.1262
13.11.1 | Plaster (1:3)
| 8 | 1.1 |  | 0.35 | 3.08 | 15.4 | M2 | P/M2 | 164.3 | 2530.22
8 | Carriage 10% of item 9 | [8 empty] | 4604.7346
9A/ 18.48 | Providing and placing on terrace (at all floor levels) polyethylene water storage tank, ISI : 12701 marked, with cover and suitable locking arrangement and making necessary holes for inlet, outlet and overflow pipes but without fittings and the base support for tank. |  |  |  |  | 10000 | Ltrs. | P/Ltr. | 9.7 | 97000
9B | Providing and fixing MS clamp consisting of 32mm X 5mm thick two no. rings spaced suitably distance apart. | [7 empty] | LS | 3000
10A | Supplying all materials labours & fixing 50mm dia. G.I pipe for using as filling station etc. All as per direction of E/I
| 50mm dia. Pipe from distribution main |  |  |  |  | 3.5 | M | P/M | 572.6 | 2004.1
10B | Providing and fixing G.I fittings
| 80mmx80mmx50mm dia Tee |  |  |  |  | 1 | No | Each | 225 | 225
| 50mm dia bend |  |  |  |  | 3 | No | Each | 175 | 525
| Providing and fixing gun metal gate valve with C.I. wheel of approved quality (screwed end) :50mm nominal dia. |  |  |  |  | 1 | N | Each | 811.4 | 811.4
10C | Providing designation of 100 A brick Flat soling joints filled with local sand including cost of watering, taxes & royalty all complete as per specification & direction of E/I.
|  | 1 | 0.45 | 0.45 |  | 0.2025 | m2 | p/m2 | 283.3 | 57.3683
11 | Providing and fixing PTMT extension nipple for water tank pipe, fittings of approved quality and colour.
| 50mm dia |  |  |  |  | 2 | Nos. | each | 300 | 600
| 63mm dia |  |  |  |  | 1 | No. | each | 350 | 350
| 80 mm dia |  |  |  |  | 1 | No. | each | 550 | 550
| Sub Total of Part - I | [8 empty] | 0
Part - II
12 | Providing and laying High Density Polyethyene pipe (HDPE pipe) of 20 mm to 225 mm OD and pressure 6.0 Kg/cm2 and 10 Kg/cm2 sutable for water supply which is available in all standard, like ISI-4984/1995 and various grades like PE-80, PE-100 including required specials. Rates are inclusive of , all taxes and duties (Exise duty @12.50% &CST @2% against Form 'C'), labour cess, contractor profit and overhead charges all complete as per direction of Engineer-in-charge.
12A | HDPE pipe of materials grade PE100- PN10 (dia in mm)
| 110mm dia Pipe |  |  |  |  | 0 | M | P/M | 646.25 | 0
| 90mm dia Pipe |  |  |  |  | 100 | M | P/M | 437.96 | 43796
| 75mm dia Pipe |  |  |  |  | 250 | M | P/M | 306.31 | 76577.5
| 63mm dia Pipe |  |  |  |  | 250 | M | P/M | 218.62 | 54655
13B | HDPE pipe of materials grade PE100- PN8 (dia in mm)
| 50 mm dia Pipe |  |  |  |  | 300 | M | P/M | 116.25 | 34875
| 40mm dia Pipe |  |  |  |  | 300 | M | P/M | 76.53 | 22959
13C | Providing all materials labours tools, fittings , specials and tackles for fitting, jointing and connecting HDPE pipes. (5% of the cost of the HDPE pipe .) | [8 empty] | 11643.125
| Sub Total Of Part (II) | [8 empty] | 0
| Grand Total | [8 empty] | 789647.6396
JE |  |  |  | AE |  |  |  |  | Executive Engineer
P. H. Division, Hajipur.

## Chakat Kursi Kushyari 10B (hidden)
Sub Estimate no. - 3B
Chakat Kursi Kushyari Ward No. :-10B
WATER SUPPLY DISTRIBUTION SYSTEM
S.N. | Particulars |  |  |  |  | Quantity |  | Unit | Rate | Amount
1/ 2.8 | Earthwork in excavation over areas (exceeding 30 cm in depth 1.5 in width as well as 10 sqm on plan) including disposal of excavated earth lead upto 50m and lift upto 1.5m, disposal earth to be levelled and neatly dressed.
| 110mm dia Pipe | 0 | 0.3 | 1.1 | = | 0 | [6 empty] | 152000
| 90mm dia Pipe | 200 | 0.3 | 1.1 | = | 66 | [6 empty] | 152000
| 75mm dia Pipe | 500 | 0.3 | 1.1 | = | 165
| 63mm dia Pipe | 550 | 0.3 | 1.1 | = | 181.5 | [6 empty] | 152000
| 50 mm dia Pipe | 450 | 0.3 | 1.1 | = | 148.5
| 40mm dia Pipe | 350 | 0.3 | 1.1 | = | 115.5
|  | 2050 |  |  |  | 676.5 | M3
| Add 5% extra for fittings = |  |  |  |  | 33.825 | M3
[6 empty] | 710.325 | M3 | P/M3 | 360.7 | 256214.2275
2/ 2.26 | Filling available excavated earth (excluding rock) in trenches, plinth, sides of foundations etc. in layers not exceeding 20cm in depth, consolidating each deposited layer by ramming and watering, lead up to 50 m and lift upto 1.5 m. |  |  |  |  | 696.1185 | M3 | P/M3 | 123.9 | 86249.0822
3/ 15.2.1 | Demolishing cement concrete manually/by mechanical means including disposal of material within 50 metres lead as per direction of Engineer - in - charge. | [8 empty] | 26869.6575
1:3:6 or richer mix
|  | 615 | 0.3 | 0.15 | = | 27.675 | M3 | P/M3 | 970.9
4/ 4.1.3 | Providing and laying in position cement concrete of specified grade excluding the cost of centering and shuttering all work upto plinth |  |  |  |  | 27.675 | M3 | P/M3 | 3998.1 | 110647.4175 | 4969
1:2:4 (1 cement: 2 coarse sand : 4 graded stone aggregate 40mm nominal size)
5 | Carriage of the following materials from quarry to work site including loading, unloading and staking at work site as per specification & direction of E/I.
| Coarse Sand (44Km Pucca & 1Km Kaccha Carriage) |  |  |  |  | 12.7305 | M3 | P/M3 | 1160.62 | 14775.2729
| Stone chips (195Km Pucca & 5Km unsurafced Carriage) |  |  |  |  | 25.461 | M3 | P/M3 | 4291.17 | 109257.4794
6A/ 18.12 | Providing and fixing G.I.Pipes complete with G.I. Fittings including trenching and refilling etc.
18.12.6 | 50mm dia G.I.Pipe from T/well to PVC Tank |  |  |  |  | 14 | M | P/M | 572.6 | 8016.4 |  |  |  | 611.3975
18.12.8 | 80mm dia G.I.Pipe from PVC Tank to Distribution main |  |  |  |  | 14 | M | P/M | 818.2 | 11454.8
18.12.7 | 65mm dia G.I.Pipe for wash out |  |  |  |  | 12 | M | P/M | 667.7 | 8012.4
7A/ 18.31.1.1 | P/F C.I sluice Valve (with Cap) complete with bolts,nuts,rubber insertions etc
6B/ | Providing and fixing brass gate valve with C.I. wheel of approved quality (screwed end).
| 80mm dia Pipe |  |  |  |  | 2 | Nos. | Each | 2227.6 | 4455.2
| 65mm dia Pipe |  |  |  |  | 1 | Nos. | Each | 1490.7 | 1490.7
| 50mm dia Pipe |  |  |  |  | 1 | Nos. | Each | 878.2 | 878.2
7/ 18.33 | Constructing masonry Chamber 60x60x75 cm inside, in brick work in cement mortar 1:4 (1 cement : 4 coarse sand) for sluice valve,with C.I. surface box 100mm top diameter, 160 mm bottom diameter and 180 mm deep ( inside) with chained lid and RCC top slab 1:2:4 mix (1 cement : 2 coarse sand : 4 graded stone aggregate 20mm nominal size ) , necessary excavation, foundation concrete 1:5:10(1 cement : 5 fine sand : 10 graded stone aggregate 40 mm nominalsize) and inside plastering with cement mortar 1:3 (1 cement : 3coarse sand) 12 mm thick, finished with a floating coat of neat cement complete as per standard specifications & direction of E/I. |  |  |  |  | 4 | Nos. | Each | 7210.6 | 28842.4
| Work for additional depth | [10 empty] | 4.9933
Brick work (1:4) in foundation
| 2 | 1.1 | 0.25 | 0.35 | 0.1925
| 2 | 0.6 | 0.25 | 0.35 | 0.105
6.1.12 |  |  |  |  | 0.2975 | 1.19 | M3 | P/M3 | 5017.9 | 5971.301
13.11.1 | Plaster (1:3)
| 8 | 1.1 |  | 0.35 | 3.08 | 12.32 | M2 | P/M2 | 164.3 | 2024.176
8 | Carriage 10% of item 9 | [8 empty] | 3683.7877
9A/ 18.48 | Providing and placing on terrace (at all floor levels) polyethylene water storage tank, ISI : 12701 marked, with cover and suitable locking arrangement and making necessary holes for inlet, outlet and overflow pipes but without fittings and the base support for tank. |  |  |  |  | 10000 | Ltrs. | P/Ltr. | 9.7 | 97000
9B | Providing and fixing MS clamp consisting of 32mm X 5mm thick two no. rings spaced suitably distance apart. | [7 empty] | LS | 3000
10A | Supplying all materials labours & fixing 50mm dia. G.I pipe for using as filling station etc. All as per direction of E/I
| 50mm dia. Pipe from distribution main |  |  |  |  | 3.5 | M | P/M | 572.6 | 2004.1
10B | Providing and fixing G.I fittings
| 80mmx80mmx50mm dia Tee |  |  |  |  | 1 | No | Each | 225 | 225
| 50mm dia bend |  |  |  |  | 3 | No | Each | 175 | 525
| Providing and fixing gun metal gate valve with C.I. wheel of approved quality (screwed end) :50mm nominal dia. |  |  |  |  | 1 | N | Each | 811.4 | 811.4
10C | Providing designation of 100 A brick Flat soling joints filled with local sand including cost of watering, taxes & royalty all complete as per specification & direction of E/I.
|  | 1 | 0.45 | 0.45 |  | 0.2025 | m2 | p/m2 | 283.3 | 57.3683
11 | Providing and fixing PTMT extension nipple for water tank pipe, fittings of approved quality and colour.
| 50mm dia |  |  |  |  | 2 | Nos. | each | 300 | 600
| 63mm dia |  |  |  |  | 1 | No. | each | 350 | 350
| 80 mm dia |  |  |  |  | 1 | No. | each | 550 | 550
| Sub Total of Part - I | [8 empty] | 0
Part - II
12 | Providing and laying High Density Polyethyene pipe (HDPE pipe) of 20 mm to 225 mm OD and pressure 6.0 Kg/cm2 and 10 Kg/cm2 sutable for water supply which is available in all standard, like ISI-4984/1995 and various grades like PE-80, PE-100 including required specials. Rates are inclusive of , all taxes and duties (Exise duty @12.50% &CST @2% against Form 'C'), labour cess, contractor profit and overhead charges all complete as per direction of Engineer-in-charge.
12A | HDPE pipe of materials grade PE100- PN10 (dia in mm)
| 110mm dia Pipe |  |  |  |  | 0 | M | P/M | 646.25 | 0
| 90mm dia Pipe |  |  |  |  | 200 | M | P/M | 437.96 | 87592
| 75mm dia Pipe |  |  |  |  | 500 | M | P/M | 306.31 | 153155
| 63mm dia Pipe |  |  |  |  | 550 | M | P/M | 218.62 | 120241
13B | HDPE pipe of materials grade PE100- PN8 (dia in mm)
| 50 mm dia Pipe |  |  |  |  | 450 | M | P/M | 116.25 | 52312.5
| 40mm dia Pipe |  |  |  |  | 350 | M | P/M | 76.53 | 26785.5
13C | Providing all materials labours tools, fittings , specials and tackles for fitting, jointing and connecting HDPE pipes. (5% of the cost of the HDPE pipe .) | [8 empty] | 22004.3
| Sub Total Of Part (II) | [8 empty] | 0
| Grand Total | [8 empty] | 1246055.6699
JE |  |  |  | AE |  |  |  |  | Executive Engineer
P. H. Division, Hajipur.

## Chakat Kursi Kushyari 11B (hidden)
Sub Estimate no. - 3C
Chakat Kursi Kushyari Ward No. :-11B
WATER SUPPLY DISTRIBUTION SYSTEM
S.N. | Particulars |  |  |  |  | Quantity |  | Unit | Rate | Amount
1/ 2.8 | Earthwork in excavation over areas (exceeding 30 cm in depth 1.5 in width as well as 10 sqm on plan) including disposal of excavated earth lead upto 50m and lift upto 1.5m, disposal earth to be levelled and neatly dressed.
| 110mm dia Pipe | 0 | 0.3 | 1.1 | = | 0 | [6 empty] | 152000
| 90mm dia Pipe | 150 | 0.3 | 1.1 | = | 49.5 | [6 empty] | 152000
| 75mm dia Pipe | 300 | 0.3 | 1.1 | = | 99
| 63mm dia Pipe | 400 | 0.3 | 1.1 | = | 132 | [6 empty] | 152000
| 50 mm dia Pipe | 350 | 0.3 | 1.1 | = | 115.5
| 40mm dia Pipe | 350 | 0.3 | 1.1 | = | 115.5
|  | 1550 |  |  |  | 511.5 | M3
| Add 5% extra for fittings = |  |  |  |  | 25.575 | M3
[6 empty] | 537.075 | M3 | P/M3 | 360.7 | 193722.9525
2/ 2.26 | Filling available excavated earth (excluding rock) in trenches, plinth, sides of foundations etc. in layers not exceeding 20cm in depth, consolidating each deposited layer by ramming and watering, lead up to 50 m and lift upto 1.5 m. |  |  |  |  | 526.3335 | M3 | P/M3 | 123.9 | 65212.7207
3/ 15.2.1 | Demolishing cement concrete manually/by mechanical means including disposal of material within 50 metres lead as per direction of Engineer - in - charge. | [8 empty] | 20316.0825
1:3:6 or richer mix
|  | 465 | 0.3 | 0.15 | = | 20.925 | M3 | P/M3 | 970.9
4/ 4.1.3 | Providing and laying in position cement concrete of specified grade excluding the cost of centering and shuttering all work upto plinth |  |  |  |  | 20.925 | M3 | P/M3 | 3998.1 | 83660.2425 | 4969
1:2:4 (1 cement: 2 coarse sand : 4 graded stone aggregate 40mm nominal size)
5 | Carriage of the following materials from quarry to work site including loading, unloading and staking at work site as per specification & direction of E/I.
| Coarse Sand (44Km Pucca & 1Km Kaccha Carriage) |  |  |  |  | 9.6255 | M3 | P/M3 | 1160.62 | 11171.5478
| Stone chips (195Km Pucca & 5Km unsurafced Carriage) |  |  |  |  | 19.251 | M3 | P/M3 | 4291.17 | 82609.3137
6A/ 18.12 | Providing and fixing G.I.Pipes complete with G.I. Fittings including trenching and refilling etc.
18.12.6 | 50mm dia G.I.Pipe from T/well to PVC Tank |  |  |  |  | 14 | M | P/M | 572.6 | 8016.4 |  |  |  | 611.3975
18.12.8 | 80mm dia G.I.Pipe from PVC Tank to Distribution main |  |  |  |  | 14 | M | P/M | 818.2 | 11454.8
18.12.7 | 65mm dia G.I.Pipe for wash out |  |  |  |  | 12 | M | P/M | 667.7 | 8012.4
7A/ 18.31.1.1 | P/F C.I sluice Valve (with Cap) complete with bolts,nuts,rubber insertions etc
6B/ | Providing and fixing brass gate valve with C.I. wheel of approved quality (screwed end).
| 80mm dia Pipe |  |  |  |  | 2 | Nos. | Each | 2227.6 | 4455.2
| 65mm dia Pipe |  |  |  |  | 1 | Nos. | Each | 1490.7 | 1490.7
| 50mm dia Pipe |  |  |  |  | 1 | Nos. | Each | 878.2 | 878.2
7/ 18.33 | Constructing masonry Chamber 60x60x75 cm inside, in brick work in cement mortar 1:4 (1 cement : 4 coarse sand) for sluice valve,with C.I. surface box 100mm top diameter, 160 mm bottom diameter and 180 mm deep ( inside) with chained lid and RCC top slab 1:2:4 mix (1 cement : 2 coarse sand : 4 graded stone aggregate 20mm nominal size ) , necessary excavation, foundation concrete 1:5:10(1 cement : 5 fine sand : 10 graded stone aggregate 40 mm nominalsize) and inside plastering with cement mortar 1:3 (1 cement : 3coarse sand) 12 mm thick, finished with a floating coat of neat cement complete as per standard specifications & direction of E/I. |  |  |  |  | 4 | Nos. | Each | 7210.6 | 28842.4
| Work for additional depth | [10 empty] | 4.9933
Brick work (1:4) in foundation
| 2 | 1.1 | 0.25 | 0.35 | 0.1925
| 2 | 0.6 | 0.25 | 0.35 | 0.105
6.1.12 |  |  |  |  | 0.2975 | 1.19 | M3 | P/M3 | 5017.9 | 5971.301
13.11.1 | Plaster (1:3)
| 8 | 1.1 |  | 0.35 | 3.08 | 12.32 | M2 | P/M2 | 164.3 | 2024.176
8 | Carriage 10% of item 9 | [8 empty] | 3683.7877
9A/ 18.48 | Providing and placing on terrace (at all floor levels) polyethylene water storage tank, ISI : 12701 marked, with cover and suitable locking arrangement and making necessary holes for inlet, outlet and overflow pipes but without fittings and the base support for tank. |  |  |  |  | 10000 | Ltrs. | P/Ltr. | 9.7 | 97000
9B | Providing and fixing MS clamp consisting of 32mm X 5mm thick two no. rings spaced suitably distance apart. | [7 empty] | LS | 3000
10A | Supplying all materials labours & fixing 50mm dia. G.I pipe for using as filling station etc. All as per direction of E/I
| 50mm dia. Pipe from distribution main |  |  |  |  | 3.5 | M | P/M | 572.6 | 2004.1
10B | Providing and fixing G.I fittings
| 80mmx80mmx50mm dia Tee |  |  |  |  | 1 | No | Each | 225 | 225
| 50mm dia bend |  |  |  |  | 3 | No | Each | 175 | 525
| Providing and fixing gun metal gate valve with C.I. wheel of approved quality (screwed end) :50mm nominal dia. |  |  |  |  | 1 | N | Each | 811.4 | 811.4
10C | Providing designation of 100 A brick Flat soling joints filled with local sand including cost of watering, taxes & royalty all complete as per specification & direction of E/I.
|  | 1 | 0.45 | 0.45 |  | 0.2025 | m2 | p/m2 | 283.3 | 57.3683
11 | Providing and fixing PTMT extension nipple for water tank pipe, fittings of approved quality and colour.
| 50mm dia |  |  |  |  | 2 | Nos. | each | 300 | 600
| 63mm dia |  |  |  |  | 1 | No. | each | 350 | 350
| 80 mm dia |  |  |  |  | 1 | No. | each | 550 | 550
| Sub Total of Part - I | [8 empty] | 0
Part - II
12 | Providing and laying High Density Polyethyene pipe (HDPE pipe) of 20 mm to 225 mm OD and pressure 6.0 Kg/cm2 and 10 Kg/cm2 sutable for water supply which is available in all standard, like ISI-4984/1995 and various grades like PE-80, PE-100 including required specials. Rates are inclusive of , all taxes and duties (Exise duty @12.50% &CST @2% against Form 'C'), labour cess, contractor profit and overhead charges all complete as per direction of Engineer-in-charge.
12A | HDPE pipe of materials grade PE100- PN10 (dia in mm)
| 110mm dia Pipe |  |  |  |  | 0 | M | P/M | 646.25 | 0
| 90mm dia Pipe |  |  |  |  | 150 | M | P/M | 437.96 | 65694
| 75mm dia Pipe |  |  |  |  | 300 | M | P/M | 306.31 | 91893
| 63mm dia Pipe |  |  |  |  | 400 | M | P/M | 218.62 | 87448
13B | HDPE pipe of materials grade PE100- PN8 (dia in mm)
| 50 mm dia Pipe |  |  |  |  | 350 | M | P/M | 116.25 | 40687.5
| 40mm dia Pipe |  |  |  |  | 350 | M | P/M | 76.53 | 26785.5
13C | Providing all materials labours tools, fittings , specials and tackles for fitting, jointing and connecting HDPE pipes. (5% of the cost of the HDPE pipe .) | [8 empty] | 15625.4
| Sub Total Of Part (II) | [8 empty] | 0
| Grand Total | [8 empty] | 964778.4926
JE |  |  |  | AE |  |  |  |  | Executive Engineer
P. H. Division, Hajipur.

## CHECHAR 10B&11B (hidden)
Sub Estimate no. - 3A
Chechar Ward no. :- 10B&11B
WATER SUPPLY DISTRIBUTION SYSTEM
S.N. | Particulars |  |  |  |  | Quantity |  | Unit | Rate | Amount
1/ 2.8 | Earthwork in excavation over areas (exceeding 30 cm in depth 1.5 in width as well as 10 sqm on plan) including disposal of excavated earth lead upto 50m and lift upto 1.5m, disposal earth to be levelled and neatly dressed.
| 110mm dia Pipe | 0 | 0.3 | 1.1 | = | 0 | [6 empty] | 152000
| 90mm dia Pipe | 100 | 0.3 | 1.1 | = | 33 | [6 empty] | 152000
| 75mm dia Pipe | 300 | 0.3 | 1.1 | = | 99
| 63mm dia Pipe | 400 | 0.3 | 1.1 | = | 132 | [6 empty] | 152000
| 50 mm dia Pipe | 350 | 0.3 | 1.1 | = | 115.5
| 40mm dia Pipe | 350 | 0.3 | 1.1 | = | 115.5
|  | 1500 |  |  |  | 495 | M3
| Add 5% extra for fittings = |  |  |  |  | 24.75 | M3
[6 empty] | 519.75 | M3 | P/M3 | 360.7 | 187473.825
2/ 2.26 | Filling available excavated earth (excluding rock) in trenches, plinth, sides of foundations etc. in layers not exceeding 20cm in depth, consolidating each deposited layer by ramming and watering, lead up to 50 m and lift upto 1.5 m. |  |  |  |  | 509.355 | M3 | P/M3 | 123.9 | 63109.0845
3/ 15.2.1 | Demolishing cement concrete manually/by mechanical means including disposal of material within 50 metres lead as per direction of Engineer - in - charge. | [8 empty] | 19660.725
1:3:6 or richer mix
|  | 450 | 0.3 | 0.15 | = | 20.25 | M3 | P/M3 | 970.9
4/ 4.1.3 | Providing and laying in position cement concrete of specified grade excluding the cost of centering and shuttering all work upto plinth |  |  |  |  | 20.25 | M3 | P/M3 | 3998.1 | 80961.525 | 4969
1:2:4 (1 cement: 2 coarse sand : 4 graded stone aggregate 40mm nominal size)
5 | Carriage of the following materials from quarry to work site including loading, unloading and staking at work site as per specification & direction of E/I.
| Coarse Sand (44Km Pucca & 1Km Kaccha Carriage) |  |  |  |  | 9.315 | M3 | P/M3 | 1160.62 | 10811.1753
| Stone chips (195Km Pucca & 5Km unsurafced Carriage) |  |  |  |  | 18.63 | M3 | P/M3 | 4291.17 | 79944.4971
6A/ 18.12 | Providing and fixing G.I.Pipes complete with G.I. Fittings including trenching and refilling etc.
18.12.6 | 50mm dia G.I.Pipe from T/well to PVC Tank |  |  |  |  | 14 | M | P/M | 572.6 | 8016.4 |  |  |  | 611.3975
18.12.8 | 80mm dia G.I.Pipe from PVC Tank to Distribution main |  |  |  |  | 14 | M | P/M | 818.2 | 11454.8
18.12.7 | 65mm dia G.I.Pipe for wash out |  |  |  |  | 12 | M | P/M | 667.7 | 8012.4
7A/ 18.31.1.1 | P/F C.I sluice Valve (with Cap) complete with bolts,nuts,rubber insertions etc
6B/ | Providing and fixing brass gate valve with C.I. wheel of approved quality (screwed end).
| 80mm dia Pipe |  |  |  |  | 2 | Nos. | Each | 2227.6 | 4455.2
| 65mm dia Pipe |  |  |  |  | 1 | Nos. | Each | 1490.7 | 1490.7
| 50mm dia Pipe |  |  |  |  | 1 | Nos. | Each | 878.2 | 878.2
7/ 18.33 | Constructing masonry Chamber 60x60x75 cm inside, in brick work in cement mortar 1:4 (1 cement : 4 coarse sand) for sluice valve,with C.I. surface box 100mm top diameter, 160 mm bottom diameter and 180 mm deep ( inside) with chained lid and RCC top slab 1:2:4 mix (1 cement : 2 coarse sand : 4 graded stone aggregate 20mm nominal size ) , necessary excavation, foundation concrete 1:5:10(1 cement : 5 fine sand : 10 graded stone aggregate 40 mm nominalsize) and inside plastering with cement mortar 1:3 (1 cement : 3coarse sand) 12 mm thick, finished with a floating coat of neat cement complete as per standard specifications & direction of E/I. |  |  |  |  | 4 | Nos. | Each | 7210.6 | 28842.4
| Work for additional depth | [10 empty] | 4.9933
Brick work (1:4) in foundation
| 2 | 1.1 | 0.25 | 0.35 | 0.1925
| 2 | 0.6 | 0.25 | 0.35 | 0.105
6.1.12 |  |  |  |  | 0.2975 | 1.19 | M3 | P/M3 | 5017.9 | 5971.301
13.11.1 | Plaster (1:3)
| 8 | 1.1 |  | 0.35 | 3.08 | 12.32 | M2 | P/M2 | 164.3 | 2024.176
8 | Carriage 10% of item 9 | [8 empty] | 3683.7877
9A/ 18.48 | Providing and placing on terrace (at all floor levels) polyethylene water storage tank, ISI : 12701 marked, with cover and suitable locking arrangement and making necessary holes for inlet, outlet and overflow pipes but without fittings and the base support for tank. |  |  |  |  | 10000 | Ltrs. | P/Ltr. | 9.7 | 97000
9B | Providing and fixing MS clamp consisting of 32mm X 5mm thick two no. rings spaced suitably distance apart. | [7 empty] | LS | 3000
10A | Supplying all materials labours & fixing 50mm dia. G.I pipe for using as filling station etc. All as per direction of E/I
| 50mm dia. Pipe from distribution main |  |  |  |  | 3.5 | M | P/M | 572.6 | 2004.1
10B | Providing and fixing G.I fittings
| 80mmx80mmx50mm dia Tee |  |  |  |  | 1 | No | Each | 225 | 225
| 50mm dia bend |  |  |  |  | 3 | No | Each | 175 | 525
| Providing and fixing gun metal gate valve with C.I. wheel of approved quality (screwed end) :50mm nominal dia. |  |  |  |  | 1 | N | Each | 811.4 | 811.4
10C | Providing designation of 100 A brick Flat soling joints filled with local sand including cost of watering, taxes & royalty all complete as per specification & direction of E/I.
|  | 1 | 0.45 | 0.45 |  | 0.2025 | m2 | p/m2 | 283.3 | 57.3683
11 | Providing and fixing PTMT extension nipple for water tank pipe, fittings of approved quality and colour.
| 50mm dia |  |  |  |  | 2 | Nos. | each | 300 | 600
| 63mm dia |  |  |  |  | 1 | No. | each | 350 | 350
| 80 mm dia |  |  |  |  | 1 | No. | each | 550 | 550
| Sub Total of Part - I | [8 empty] | 0
Part - II
12 | Providing and laying High Density Polyethyene pipe (HDPE pipe) of 20 mm to 225 mm OD and pressure 6.0 Kg/cm2 and 10 Kg/cm2 sutable for water supply which is available in all standard, like ISI-4984/1995 and various grades like PE-80, PE-100 including required specials. Rates are inclusive of , all taxes and duties (Exise duty @12.50% &CST @2% against Form 'C'), labour cess, contractor profit and overhead charges all complete as per direction of Engineer-in-charge.
12A | HDPE pipe of materials grade PE100- PN10 (dia in mm)
| 110mm dia Pipe |  |  |  |  | 0 | M | P/M | 646.25 | 0
| 90mm dia Pipe |  |  |  |  | 100 | M | P/M | 437.96 | 43796
| 75mm dia Pipe |  |  |  |  | 300 | M | P/M | 306.31 | 91893
| 63mm dia Pipe |  |  |  |  | 400 | M | P/M | 218.62 | 87448
13B | HDPE pipe of materials grade PE100- PN8 (dia in mm)
| 50 mm dia Pipe |  |  |  |  | 350 | M | P/M | 116.25 | 40687.5
| 40mm dia Pipe |  |  |  |  | 350 | M | P/M | 76.53 | 26785.5
13C | Providing all materials labours tools, fittings , specials and tackles for fitting, jointing and connecting HDPE pipes. (5% of the cost of the HDPE pipe .) | [8 empty] | 14530.5
| Sub Total Of Part (II) | [8 empty] | 0
| Grand Total | [8 empty] | 927053.5649
JE |  |  |  | AE |  |  |  |  | Executive Engineer
P. H. Division, Hajipur.

## CHECHAR 12B&13B (hidden)
Sub Estimate no. - 3B
Chechar Ward no. :- 12B&13B
WATER SUPPLY DISTRIBUTION SYSTEM
S.N. | Particulars |  |  |  |  | Quantity |  | Unit | Rate | Amount
1/ 2.8 | Earthwork in excavation over areas (exceeding 30 cm in depth 1.5 in width as well as 10 sqm on plan) including disposal of excavated earth lead upto 50m and lift upto 1.5m, disposal earth to be levelled and neatly dressed.
| 110mm dia Pipe | 0 | 0.3 | 1.1 | = | 0 | [6 empty] | 152000
| 90mm dia Pipe | 100 | 0.3 | 1.1 | = | 33 | [6 empty] | 152000
| 75mm dia Pipe | 300 | 0.3 | 1.1 | = | 99
| 63mm dia Pipe | 400 | 0.3 | 1.1 | = | 132 | [6 empty] | 152000
| 50 mm dia Pipe | 350 | 0.3 | 1.1 | = | 115.5
| 40mm dia Pipe | 350 | 0.3 | 1.1 | = | 115.5
|  | 1500 |  |  |  | 495 | M3
| Add 5% extra for fittings = |  |  |  |  | 24.75 | M3
[6 empty] | 519.75 | M3 | P/M3 | 360.7 | 187473.825
2/ 2.26 | Filling available excavated earth (excluding rock) in trenches, plinth, sides of foundations etc. in layers not exceeding 20cm in depth, consolidating each deposited layer by ramming and watering, lead up to 50 m and lift upto 1.5 m. |  |  |  |  | 509.355 | M3 | P/M3 | 123.9 | 63109.0845
3/ 15.2.1 | Demolishing cement concrete manually/by mechanical means including disposal of material within 50 metres lead as per direction of Engineer - in - charge. | [8 empty] | 19660.725
1:3:6 or richer mix
|  | 450 | 0.3 | 0.15 | = | 20.25 | M3 | P/M3 | 970.9
4/ 4.1.3 | Providing and laying in position cement concrete of specified grade excluding the cost of centering and shuttering all work upto plinth |  |  |  |  | 20.25 | M3 | P/M3 | 3998.1 | 80961.525 | 4969
1:2:4 (1 cement: 2 coarse sand : 4 graded stone aggregate 40mm nominal size)
5 | Carriage of the following materials from quarry to work site including loading, unloading and staking at work site as per specification & direction of E/I.
| Coarse Sand (44Km Pucca & 1Km Kaccha Carriage) |  |  |  |  | 9.315 | M3 | P/M3 | 1160.62 | 10811.1753
| Stone chips (195Km Pucca & 5Km unsurafced Carriage) |  |  |  |  | 18.63 | M3 | P/M3 | 4291.17 | 79944.4971
6A/ 18.12 | Providing and fixing G.I.Pipes complete with G.I. Fittings including trenching and refilling etc.
18.12.6 | 50mm dia G.I.Pipe from T/well to PVC Tank |  |  |  |  | 14 | M | P/M | 572.6 | 8016.4 |  |  |  | 611.3975
18.12.8 | 80mm dia G.I.Pipe from PVC Tank to Distribution main |  |  |  |  | 14 | M | P/M | 818.2 | 11454.8
18.12.7 | 65mm dia G.I.Pipe for wash out |  |  |  |  | 12 | M | P/M | 667.7 | 8012.4
7A/ 18.31.1.1 | P/F C.I sluice Valve (with Cap) complete with bolts,nuts,rubber insertions etc
6B/ | Providing and fixing brass gate valve with C.I. wheel of approved quality (screwed end).
| 80mm dia Pipe |  |  |  |  | 2 | Nos. | Each | 2227.6 | 4455.2
| 65mm dia Pipe |  |  |  |  | 1 | Nos. | Each | 1490.7 | 1490.7
| 50mm dia Pipe |  |  |  |  | 1 | Nos. | Each | 878.2 | 878.2
7/ 18.33 | Constructing masonry Chamber 60x60x75 cm inside, in brick work in cement mortar 1:4 (1 cement : 4 coarse sand) for sluice valve,with C.I. surface box 100mm top diameter, 160 mm bottom diameter and 180 mm deep ( inside) with chained lid and RCC top slab 1:2:4 mix (1 cement : 2 coarse sand : 4 graded stone aggregate 20mm nominal size ) , necessary excavation, foundation concrete 1:5:10(1 cement : 5 fine sand : 10 graded stone aggregate 40 mm nominalsize) and inside plastering with cement mortar 1:3 (1 cement : 3coarse sand) 12 mm thick, finished with a floating coat of neat cement complete as per standard specifications & direction of E/I. |  |  |  |  | 4 | Nos. | Each | 7210.6 | 28842.4
| Work for additional depth | [10 empty] | 4.9933
Brick work (1:4) in foundation
| 2 | 1.1 | 0.25 | 0.35 | 0.1925
| 2 | 0.6 | 0.25 | 0.35 | 0.105
6.1.12 |  |  |  |  | 0.2975 | 1.19 | M3 | P/M3 | 5017.9 | 5971.301
13.11.1 | Plaster (1:3)
| 8 | 1.1 |  | 0.35 | 3.08 | 12.32 | M2 | P/M2 | 164.3 | 2024.176
8 | Carriage 10% of item 9 | [8 empty] | 3683.7877
9A/ 18.48 | Providing and placing on terrace (at all floor levels) polyethylene water storage tank, ISI : 12701 marked, with cover and suitable locking arrangement and making necessary holes for inlet, outlet and overflow pipes but without fittings and the base support for tank. |  |  |  |  | 10000 | Ltrs. | P/Ltr. | 9.7 | 97000
9B | Providing and fixing MS clamp consisting of 32mm X 5mm thick two no. rings spaced suitably distance apart. | [7 empty] | LS | 3000
10A | Supplying all materials labours & fixing 50mm dia. G.I pipe for using as filling station etc. All as per direction of E/I
| 50mm dia. Pipe from distribution main |  |  |  |  | 3.5 | M | P/M | 572.6 | 2004.1
10B | Providing and fixing G.I fittings
| 80mmx80mmx50mm dia Tee |  |  |  |  | 1 | No | Each | 225 | 225
| 50mm dia bend |  |  |  |  | 3 | No | Each | 175 | 525
| Providing and fixing gun metal gate valve with C.I. wheel of approved quality (screwed end) :50mm nominal dia. |  |  |  |  | 1 | N | Each | 811.4 | 811.4
10C | Providing designation of 100 A brick Flat soling joints filled with local sand including cost of watering, taxes & royalty all complete as per specification & direction of E/I.
|  | 1 | 0.45 | 0.45 |  | 0.2025 | m2 | p/m2 | 283.3 | 57.3683
11 | Providing and fixing PTMT extension nipple for water tank pipe, fittings of approved quality and colour.
| 50mm dia |  |  |  |  | 2 | Nos. | each | 300 | 600
| 63mm dia |  |  |  |  | 1 | No. | each | 350 | 350
| 80 mm dia |  |  |  |  | 1 | No. | each | 550 | 550
| Sub Total of Part - I | [8 empty] | 0
Part - II
12 | Providing and laying High Density Polyethyene pipe (HDPE pipe) of 20 mm to 225 mm OD and pressure 6.0 Kg/cm2 and 10 Kg/cm2 sutable for water supply which is available in all standard, like ISI-4984/1995 and various grades like PE-80, PE-100 including required specials. Rates are inclusive of , all taxes and duties (Exise duty @12.50% &CST @2% against Form 'C'), labour cess, contractor profit and overhead charges all complete as per direction of Engineer-in-charge.
12A | HDPE pipe of materials grade PE100- PN10 (dia in mm)
| 110mm dia Pipe |  |  |  |  | 0 | M | P/M | 646.25 | 0
| 90mm dia Pipe |  |  |  |  | 100 | M | P/M | 437.96 | 43796
| 75mm dia Pipe |  |  |  |  | 300 | M | P/M | 306.31 | 91893
| 63mm dia Pipe |  |  |  |  | 400 | M | P/M | 218.62 | 87448
13B | HDPE pipe of materials grade PE100- PN8 (dia in mm)
| 50 mm dia Pipe |  |  |  |  | 350 | M | P/M | 116.25 | 40687.5
| 40mm dia Pipe |  |  |  |  | 350 | M | P/M | 76.53 | 26785.5
13C | Providing all materials labours tools, fittings , specials and tackles for fitting, jointing and connecting HDPE pipes. (5% of the cost of the HDPE pipe .) | [8 empty] | 14530.5
| Sub Total Of Part (II) | [8 empty] | 0
| Grand Total | [8 empty] | 927053.5649
JE |  |  |  | AE |  |  |  |  | Executive Engineer
P. H. Division, Hajipur.

## Daudnagar (hidden)
Sub Estimate no. - 3
BIDUPUR DAUDNAGAR 09B DAUDNAGAR
WATER SUPPLY DISTRIBUTION SYSTEM
S.N. | Particulars |  |  |  |  | Quantity |  | Unit | Rate | Amount
1/ 2.8 | Earthwork in excavation over areas (exceeding 30 cm in depth 1.5 in width as well as 10 sqm on plan) including disposal of excavated earth lead upto 50m and lift upto 1.5m, disposal earth to be levelled and neatly dressed.
| 110mm dia Pipe | 0 | 0.3 | 1.1 | = | 0 | [6 empty] | 152000
| 90mm dia Pipe | 150 | 0.3 | 1.1 | = | 49.5 | [6 empty] | 152000
| 75mm dia Pipe | 400 | 0.3 | 1.1 | = | 132
| 63mm dia Pipe | 300 | 0.3 | 1.1 | = | 99 | [6 empty] | 152000
| 50 mm dia Pipe | 350 | 0.3 | 1.1 | = | 115.5
| 40mm dia Pipe | 200 | 0.3 | 1.1 | = | 66
|  | 1400 |  |  |  | 462 | M3
| Add 5% extra for fittings = |  |  |  |  | 23.1 | M3
[6 empty] | 485.1 | M3 | P/M3 | 360.7 | 174975.57
2/ 2.26 | Filling available excavated earth (excluding rock) in trenches, plinth, sides of foundations etc. in layers not exceeding 20cm in depth, consolidating each deposited layer by ramming and watering, lead up to 50 m and lift upto 1.5 m. |  |  |  |  | 475.398 | M3 | P/M3 | 123.9 | 58901.8122
3/ 15.2.1 | Demolishing cement concrete manually/by mechanical means including disposal of material within 50 metres lead as per direction of Engineer - in - charge. | [8 empty] | 18350.01
1:3:6 or richer mix
|  | 420 | 0.3 | 0.15 | = | 18.9 | M3 | P/M3 | 970.9
4/ 4.1.3 | Providing and laying in position cement concrete of specified grade excluding the cost of centering and shuttering all work upto plinth |  |  |  |  | 18.9 | M3 | P/M3 | 3998.1 | 75564.09 | 4969
1:2:4 (1 cement: 2 coarse sand : 4 graded stone aggregate 40mm nominal size)
5 | Carriage of the following materials from quarry to work site including loading, unloading and staking at work site as per specification & direction of E/I.
| Coarse Sand (44Km Pucca & 1Km Kaccha Carriage) |  |  |  |  | 8.694 | M3 | P/M3 | 1160.62 | 10090.4303
| Stone chips (195Km Pucca & 5Km unsurafced Carriage) |  |  |  |  | 17.388 | M3 | P/M3 | 4291.17 | 74614.864
6A/ 18.12 | Providing and fixing G.I.Pipes complete with G.I. Fittings including trenching and refilling etc.
18.12.6 | 50mm dia G.I.Pipe from T/well to PVC Tank |  |  |  |  | 14 | M | P/M | 572.6 | 8016.4 |  |  |  | 611.3975
18.12.8 | 80mm dia G.I.Pipe from PVC Tank to Distribution main |  |  |  |  | 14 | M | P/M | 818.2 | 11454.8
18.12.7 | 65mm dia G.I.Pipe for wash out |  |  |  |  | 12 | M | P/M | 667.7 | 8012.4
7A/ 18.31.1.1 | P/F C.I sluice Valve (with Cap) complete with bolts,nuts,rubber insertions etc
6B/ | Providing and fixing brass gate valve with C.I. wheel of approved quality (screwed end).
| 80mm dia Pipe |  |  |  |  | 2 | Nos. | Each | 2227.6 | 4455.2
| 65mm dia Pipe |  |  |  |  | 2 | Nos. | Each | 1490.7 | 2981.4
| 50mm dia Pipe |  |  |  |  | 1 | Nos. | Each | 878.2 | 878.2
7/ 18.33 | Constructing masonry Chamber 60x60x75 cm inside, in brick work in cement mortar 1:4 (1 cement : 4 coarse sand) for sluice valve,with C.I. surface box 100mm top diameter, 160 mm bottom diameter and 180 mm deep ( inside) with chained lid and RCC top slab 1:2:4 mix (1 cement : 2 coarse sand : 4 graded stone aggregate 20mm nominal size ) , necessary excavation, foundation concrete 1:5:10(1 cement : 5 fine sand : 10 graded stone aggregate 40 mm nominalsize) and inside plastering with cement mortar 1:3 (1 cement : 3coarse sand) 12 mm thick, finished with a floating coat of neat cement complete as per standard specifications & direction of E/I. |  |  |  |  | 5 | Nos. | Each | 7210.6 | 36053
| Work for additional depth | [10 empty] | 4.9933
Brick work (1:4) in foundation
| 2 | 1.1 | 0.25 | 0.35 | 0.1925
| 2 | 0.6 | 0.25 | 0.35 | 0.105
6.1.12 |  |  |  |  | 0.2975 | 1.4875 | M3 | P/M3 | 5017.9 | 7464.1262
13.11.1 | Plaster (1:3)
| 8 | 1.1 |  | 0.35 | 3.08 | 15.4 | M2 | P/M2 | 164.3 | 2530.22
8 | Carriage 10% of item 9 | [8 empty] | 4604.7346
9A/ 18.48 | Providing and placing on terrace (at all floor levels) polyethylene water storage tank, ISI : 12701 marked, with cover and suitable locking arrangement and making necessary holes for inlet, outlet and overflow pipes but without fittings and the base support for tank. |  |  |  |  | 10000 | Ltrs. | P/Ltr. | 9.7 | 97000
9B | Providing and fixing MS clamp consisting of 32mm X 5mm thick two no. rings spaced suitably distance apart. | [7 empty] | LS | 3000
10A | Supplying all materials labours & fixing 50mm dia. G.I pipe for using as filling station etc. All as per direction of E/I
| 50mm dia. Pipe from distribution main |  |  |  |  | 3.5 | M | P/M | 572.6 | 2004.1
10B | Providing and fixing G.I fittings
| 80mmx80mmx50mm dia Tee |  |  |  |  | 1 | No | Each | 225 | 225
| 50mm dia bend |  |  |  |  | 3 | No | Each | 175 | 525
| Providing and fixing gun metal gate valve with C.I. wheel of approved quality (screwed end) :50mm nominal dia. |  |  |  |  | 1 | N | Each | 811.4 | 811.4
10C | Providing designation of 100 A brick Flat soling joints filled with local sand including cost of watering, taxes & royalty all complete as per specification & direction of E/I.
|  | 1 | 0.45 | 0.45 |  | 0.2025 | m2 | p/m2 | 283.3 | 57.3683
11 | Providing and fixing PTMT extension nipple for water tank pipe, fittings of approved quality and colour.
| 50mm dia |  |  |  |  | 2 | Nos. | each | 300 | 600
| 63mm dia |  |  |  |  | 1 | No. | each | 350 | 350
| 80 mm dia |  |  |  |  | 1 | No. | each | 550 | 550
| Sub Total of Part - I | [8 empty] | 0
Part - II
12 | Providing and laying High Density Polyethyene pipe (HDPE pipe) of 20 mm to 225 mm OD and pressure 6.0 Kg/cm2 and 10 Kg/cm2 sutable for water supply which is available in all standard, like ISI-4984/1995 and various grades like PE-80, PE-100 including required specials. Rates are inclusive of , all taxes and duties (Exise duty @12.50% &CST @2% against Form 'C'), labour cess, contractor profit and overhead charges all complete as per direction of Engineer-in-charge.
12A | HDPE pipe of materials grade PE100- PN10 (dia in mm)
| 110mm dia Pipe |  |  |  |  | 0 | M | P/M | 646.25 | 0
| 90mm dia Pipe |  |  |  |  | 150 | M | P/M | 437.96 | 65694
| 75mm dia Pipe |  |  |  |  | 400 | M | P/M | 306.31 | 122524
| 63mm dia Pipe |  |  |  |  | 300 | M | P/M | 218.62 | 65586
13B | HDPE pipe of materials grade PE100- PN8 (dia in mm)
| 50 mm dia Pipe |  |  |  |  | 350 | M | P/M | 116.25 | 40687.5
| 40mm dia Pipe |  |  |  |  | 200 | M | P/M | 76.53 | 15306
13C | Providing all materials labours tools, fittings , specials and tackles for fitting, jointing and connecting HDPE pipes. (5% of the cost of the HDPE pipe .) | [8 empty] | 15489.875
| Sub Total Of Part (II) | [8 empty] | 0
| Grand Total | [8 empty] | 929357.5006
Executive Engineer
P. H. Division, Hajipur.

## Dilawarpur Govardhan 02B&6 (hidden)
Sub Estimate no. - 3A
Dilawarpur Govardhan Ward No. :-02B&6
WATER SUPPLY DISTRIBUTION SYSTEM
S.N. | Particulars |  |  |  |  | Quantity |  | Unit | Rate | Amount
1/ 2.8 | Earthwork in excavation over areas (exceeding 30 cm in depth 1.5 in width as well as 10 sqm on plan) including disposal of excavated earth lead upto 50m and lift upto 1.5m, disposal earth to be levelled and neatly dressed.
| 110mm dia Pipe | 0 | 0.3 | 1.1 | = | 0 | [6 empty] | 152000
| 90mm dia Pipe | 150 | 0.3 | 1.1 | = | 49.5 | [6 empty] | 152000
| 75mm dia Pipe | 450 | 0.3 | 1.1 | = | 148.5
| 63mm dia Pipe | 400 | 0.3 | 1.1 | = | 132 | [6 empty] | 152000
| 50 mm dia Pipe | 300 | 0.3 | 1.1 | = | 99
| 40mm dia Pipe | 300 | 0.3 | 1.1 | = | 99
|  | 1600 |  |  |  | 528 | M3
| Add 5% extra for fittings = |  |  |  |  | 26.4 | M3
[6 empty] | 554.4 | M3 | P/M3 | 360.7 | 199972.08
2/ 2.26 | Filling available excavated earth (excluding rock) in trenches, plinth, sides of foundations etc. in layers not exceeding 20cm in depth, consolidating each deposited layer by ramming and watering, lead up to 50 m and lift upto 1.5 m. |  |  |  |  | 543.312 | M3 | P/M3 | 123.9 | 67316.3568
3/ 15.2.1 | Demolishing cement concrete manually/by mechanical means including disposal of material within 50 metres lead as per direction of Engineer - in - charge. | [8 empty] | 20971.44
1:3:6 or richer mix
|  | 480 | 0.3 | 0.15 | = | 21.6 | M3 | P/M3 | 970.9
4/ 4.1.3 | Providing and laying in position cement concrete of specified grade excluding the cost of centering and shuttering all work upto plinth |  |  |  |  | 21.6 | M3 | P/M3 | 3998.1 | 86358.96 | 4969
1:2:4 (1 cement: 2 coarse sand : 4 graded stone aggregate 40mm nominal size)
5 | Carriage of the following materials from quarry to work site including loading, unloading and staking at work site as per specification & direction of E/I.
| Coarse Sand (44Km Pucca & 1Km Kaccha Carriage) |  |  |  |  | 9.936 | M3 | P/M3 | 1160.62 | 11531.9203
| Stone chips (195Km Pucca & 5Km unsurafced Carriage) |  |  |  |  | 19.872 | M3 | P/M3 | 4291.17 | 85274.1302
6A/ 18.12 | Providing and fixing G.I.Pipes complete with G.I. Fittings including trenching and refilling etc.
18.12.6 | 50mm dia G.I.Pipe from T/well to PVC Tank |  |  |  |  | 14 | M | P/M | 572.6 | 8016.4 |  |  |  | 611.3975
18.12.8 | 80mm dia G.I.Pipe from PVC Tank to Distribution main |  |  |  |  | 14 | M | P/M | 818.2 | 11454.8
18.12.7 | 65mm dia G.I.Pipe for wash out |  |  |  |  | 12 | M | P/M | 667.7 | 8012.4
7A/ 18.31.1.1 | P/F C.I sluice Valve (with Cap) complete with bolts,nuts,rubber insertions etc
6B/ | Providing and fixing brass gate valve with C.I. wheel of approved quality (screwed end).
| 80mm dia Pipe |  |  |  |  | 2 | Nos. | Each | 2227.6 | 4455.2
| 65mm dia Pipe |  |  |  |  | 2 | Nos. | Each | 1490.7 | 2981.4
| 50mm dia Pipe |  |  |  |  | 1 | Nos. | Each | 878.2 | 878.2
7/ 18.33 | Constructing masonry Chamber 60x60x75 cm inside, in brick work in cement mortar 1:4 (1 cement : 4 coarse sand) for sluice valve,with C.I. surface box 100mm top diameter, 160 mm bottom diameter and 180 mm deep ( inside) with chained lid and RCC top slab 1:2:4 mix (1 cement : 2 coarse sand : 4 graded stone aggregate 20mm nominal size ) , necessary excavation, foundation concrete 1:5:10(1 cement : 5 fine sand : 10 graded stone aggregate 40 mm nominalsize) and inside plastering with cement mortar 1:3 (1 cement : 3coarse sand) 12 mm thick, finished with a floating coat of neat cement complete as per standard specifications & direction of E/I. |  |  |  |  | 5 | Nos. | Each | 7210.6 | 36053
| Work for additional depth | [10 empty] | 4.9933
Brick work (1:4) in foundation
| 2 | 1.1 | 0.25 | 0.35 | 0.1925
| 2 | 0.6 | 0.25 | 0.35 | 0.105
6.1.12 |  |  |  |  | 0.2975 | 1.4875 | M3 | P/M3 | 5017.9 | 7464.1262
13.11.1 | Plaster (1:3)
| 8 | 1.1 |  | 0.35 | 3.08 | 15.4 | M2 | P/M2 | 164.3 | 2530.22
8 | Carriage 10% of item 9 | [8 empty] | 4604.7346
9A/ 18.48 | Providing and placing on terrace (at all floor levels) polyethylene water storage tank, ISI : 12701 marked, with cover and suitable locking arrangement and making necessary holes for inlet, outlet and overflow pipes but without fittings and the base support for tank. |  |  |  |  | 10000 | Ltrs. | P/Ltr. | 9.7 | 97000
9B | Providing and fixing MS clamp consisting of 32mm X 5mm thick two no. rings spaced suitably distance apart. | [7 empty] | LS | 3000
10A | Supplying all materials labours & fixing 50mm dia. G.I pipe for using as filling station etc. All as per direction of E/I
| 50mm dia. Pipe from distribution main |  |  |  |  | 3.5 | M | P/M | 572.6 | 2004.1
10B | Providing and fixing G.I fittings
| 80mmx80mmx50mm dia Tee |  |  |  |  | 1 | No | Each | 225 | 225
| 50mm dia bend |  |  |  |  | 3 | No | Each | 175 | 525
| Providing and fixing gun metal gate valve with C.I. wheel of approved quality (screwed end) :50mm nominal dia. |  |  |  |  | 1 | N | Each | 811.4 | 811.4
10C | Providing designation of 100 A brick Flat soling joints filled with local sand including cost of watering, taxes & royalty all complete as per specification & direction of E/I.
|  | 1 | 0.45 | 0.45 |  | 0.2025 | m2 | p/m2 | 283.3 | 57.3683
11 | Providing and fixing PTMT extension nipple for water tank pipe, fittings of approved quality and colour.
| 50mm dia |  |  |  |  | 2 | Nos. | each | 300 | 600
| 63mm dia |  |  |  |  | 1 | No. | each | 350 | 350
| 80 mm dia |  |  |  |  | 1 | No. | each | 550 | 550
| Sub Total of Part - I | [8 empty] | 0
Part - II
12 | Providing and laying High Density Polyethyene pipe (HDPE pipe) of 20 mm to 225 mm OD and pressure 6.0 Kg/cm2 and 10 Kg/cm2 sutable for water supply which is available in all standard, like ISI-4984/1995 and various grades like PE-80, PE-100 including required specials. Rates are inclusive of , all taxes and duties (Exise duty @12.50% &CST @2% against Form 'C'), labour cess, contractor profit and overhead charges all complete as per direction of Engineer-in-charge.
12A | HDPE pipe of materials grade PE100- PN10 (dia in mm)
| 110mm dia Pipe |  |  |  |  | 0 | M | P/M | 646.25 | 0
| 90mm dia Pipe |  |  |  |  | 150 | M | P/M | 437.96 | 65694
| 75mm dia Pipe |  |  |  |  | 450 | M | P/M | 306.31 | 137839.5
| 63mm dia Pipe |  |  |  |  | 400 | M | P/M | 218.62 | 87448
13B | HDPE pipe of materials grade PE100- PN8 (dia in mm)
| 50 mm dia Pipe |  |  |  |  | 300 | M | P/M | 116.25 | 34875
| 40mm dia Pipe |  |  |  |  | 300 | M | P/M | 76.53 | 22959
13C | Providing all materials labours tools, fittings , specials and tackles for fitting, jointing and connecting HDPE pipes. (5% of the cost of the HDPE pipe .) | [8 empty] | 17440.775
| Sub Total Of Part (II) | [8 empty] | 0
| Grand Total | [8 empty] | 1029254.5115
JE |  |  |  | AE |  |  |  |  | Executive Engineer
P. H. Division, Hajipur.

## Dilawarpur Govardhan 03B&8 (hidden)
Sub Estimate no. - 3B
Dilawarpur Govardhan Ward No. :-03B&8
WATER SUPPLY DISTRIBUTION SYSTEM
S.N. | Particulars |  |  |  |  | Quantity |  | Unit | Rate | Amount
1/ 2.8 | Earthwork in excavation over areas (exceeding 30 cm in depth 1.5 in width as well as 10 sqm on plan) including disposal of excavated earth lead upto 50m and lift upto 1.5m, disposal earth to be levelled and neatly dressed.
| 110mm dia Pipe | 0 | 0.3 | 1.1 | = | 0 | [6 empty] | 152000
| 90mm dia Pipe | 150 | 0.3 | 1.1 | = | 49.5 | [6 empty] | 152000
| 75mm dia Pipe | 450 | 0.3 | 1.1 | = | 148.5
| 63mm dia Pipe | 550 | 0.3 | 1.1 | = | 181.5 | [6 empty] | 152000
| 50 mm dia Pipe | 350 | 0.3 | 1.1 | = | 115.5
| 40mm dia Pipe | 300 | 0.3 | 1.1 | = | 99
|  | 1800 |  |  |  | 594 | M3
| Add 5% extra for fittings = |  |  |  |  | 29.7 | M3
[6 empty] | 623.7 | M3 | P/M3 | 360.7 | 224968.59
2/ 2.26 | Filling available excavated earth (excluding rock) in trenches, plinth, sides of foundations etc. in layers not exceeding 20cm in depth, consolidating each deposited layer by ramming and watering, lead up to 50 m and lift upto 1.5 m. |  |  |  |  | 611.226 | M3 | P/M3 | 123.9 | 75730.9014
3/ 15.2.1 | Demolishing cement concrete manually/by mechanical means including disposal of material within 50 metres lead as per direction of Engineer - in - charge. | [8 empty] | 23592.87
1:3:6 or richer mix
|  | 540 | 0.3 | 0.15 | = | 24.3 | M3 | P/M3 | 970.9
4/ 4.1.3 | Providing and laying in position cement concrete of specified grade excluding the cost of centering and shuttering all work upto plinth |  |  |  |  | 24.3 | M3 | P/M3 | 3998.1 | 97153.83 | 4969
1:2:4 (1 cement: 2 coarse sand : 4 graded stone aggregate 40mm nominal size)
5 | Carriage of the following materials from quarry to work site including loading, unloading and staking at work site as per specification & direction of E/I.
| Coarse Sand (44Km Pucca & 1Km Kaccha Carriage) |  |  |  |  | 11.178 | M3 | P/M3 | 1160.62 | 12973.4104
| Stone chips (195Km Pucca & 5Km unsurafced Carriage) |  |  |  |  | 22.356 | M3 | P/M3 | 4291.17 | 95933.3965
6A/ 18.12 | Providing and fixing G.I.Pipes complete with G.I. Fittings including trenching and refilling etc.
18.12.6 | 50mm dia G.I.Pipe from T/well to PVC Tank |  |  |  |  | 14 | M | P/M | 572.6 | 8016.4 |  |  |  | 611.3975
18.12.8 | 80mm dia G.I.Pipe from PVC Tank to Distribution main |  |  |  |  | 14 | M | P/M | 818.2 | 11454.8
18.12.7 | 65mm dia G.I.Pipe for wash out |  |  |  |  | 12 | M | P/M | 667.7 | 8012.4
7A/ 18.31.1.1 | P/F C.I sluice Valve (with Cap) complete with bolts,nuts,rubber insertions etc
6B/ | Providing and fixing brass gate valve with C.I. wheel of approved quality (screwed end).
| 80mm dia Pipe |  |  |  |  | 2 | Nos. | Each | 2227.6 | 4455.2
| 65mm dia Pipe |  |  |  |  | 1 | Nos. | Each | 1490.7 | 1490.7
| 50mm dia Pipe |  |  |  |  | 1 | Nos. | Each | 878.2 | 878.2
7/ 18.33 | Constructing masonry Chamber 60x60x75 cm inside, in brick work in cement mortar 1:4 (1 cement : 4 coarse sand) for sluice valve,with C.I. surface box 100mm top diameter, 160 mm bottom diameter and 180 mm deep ( inside) with chained lid and RCC top slab 1:2:4 mix (1 cement : 2 coarse sand : 4 graded stone aggregate 20mm nominal size ) , necessary excavation, foundation concrete 1:5:10(1 cement : 5 fine sand : 10 graded stone aggregate 40 mm nominalsize) and inside plastering with cement mortar 1:3 (1 cement : 3coarse sand) 12 mm thick, finished with a floating coat of neat cement complete as per standard specifications & direction of E/I. |  |  |  |  | 4 | Nos. | Each | 7210.6 | 28842.4
| Work for additional depth | [10 empty] | 4.9933
Brick work (1:4) in foundation
| 2 | 1.1 | 0.25 | 0.35 | 0.1925
| 2 | 0.6 | 0.25 | 0.35 | 0.105
6.1.12 |  |  |  |  | 0.2975 | 1.19 | M3 | P/M3 | 5017.9 | 5971.301
13.11.1 | Plaster (1:3)
| 8 | 1.1 |  | 0.35 | 3.08 | 12.32 | M2 | P/M2 | 164.3 | 2024.176
8 | Carriage 10% of item 9 | [8 empty] | 3683.7877
9A/ 18.48 | Providing and placing on terrace (at all floor levels) polyethylene water storage tank, ISI : 12701 marked, with cover and suitable locking arrangement and making necessary holes for inlet, outlet and overflow pipes but without fittings and the base support for tank. |  |  |  |  | 10000 | Ltrs. | P/Ltr. | 9.7 | 97000
9B | Providing and fixing MS clamp consisting of 32mm X 5mm thick two no. rings spaced suitably distance apart. | [7 empty] | LS | 3000
10A | Supplying all materials labours & fixing 50mm dia. G.I pipe for using as filling station etc. All as per direction of E/I
| 50mm dia. Pipe from distribution main |  |  |  |  | 3.5 | M | P/M | 572.6 | 2004.1
10B | Providing and fixing G.I fittings
| 80mmx80mmx50mm dia Tee |  |  |  |  | 1 | No | Each | 225 | 225
| 50mm dia bend |  |  |  |  | 3 | No | Each | 175 | 525
| Providing and fixing gun metal gate valve with C.I. wheel of approved quality (screwed end) :50mm nominal dia. |  |  |  |  | 1 | N | Each | 811.4 | 811.4
10C | Providing designation of 100 A brick Flat soling joints filled with local sand including cost of watering, taxes & royalty all complete as per specification & direction of E/I.
|  | 1 | 0.45 | 0.45 |  | 0.2025 | m2 | p/m2 | 283.3 | 57.3683
11 | Providing and fixing PTMT extension nipple for water tank pipe, fittings of approved quality and colour.
| 50mm dia |  |  |  |  | 2 | Nos. | each | 300 | 600
| 63mm dia |  |  |  |  | 1 | No. | each | 350 | 350
| 80 mm dia |  |  |  |  | 1 | No. | each | 550 | 550
| Sub Total of Part - I | [8 empty] | 0
Part - II
12 | Providing and laying High Density Polyethyene pipe (HDPE pipe) of 20 mm to 225 mm OD and pressure 6.0 Kg/cm2 and 10 Kg/cm2 sutable for water supply which is available in all standard, like ISI-4984/1995 and various grades like PE-80, PE-100 including required specials. Rates are inclusive of , all taxes and duties (Exise duty @12.50% &CST @2% against Form 'C'), labour cess, contractor profit and overhead charges all complete as per direction of Engineer-in-charge.
12A | HDPE pipe of materials grade PE100- PN10 (dia in mm)
| 110mm dia Pipe |  |  |  |  | 0 | M | P/M | 646.25 | 0
| 90mm dia Pipe |  |  |  |  | 150 | M | P/M | 437.96 | 65694
| 75mm dia Pipe |  |  |  |  | 450 | M | P/M | 306.31 | 137839.5
| 63mm dia Pipe |  |  |  |  | 550 | M | P/M | 218.62 | 120241
13B | HDPE pipe of materials grade PE100- PN8 (dia in mm)
| 50 mm dia Pipe |  |  |  |  | 350 | M | P/M | 116.25 | 40687.5
| 40mm dia Pipe |  |  |  |  | 300 | M | P/M | 76.53 | 22959
13C | Providing all materials labours tools, fittings , specials and tackles for fitting, jointing and connecting HDPE pipes. (5% of the cost of the HDPE pipe .) | [8 empty] | 19371.05
| Sub Total Of Part (II) | [8 empty] | 0
| Grand Total | [8 empty] | 1117097.2812
JE |  |  |  | AE |  |  |  |  | Executive Engineer
P. H. Division, Hajipur.

## Dilawarpur Govardhan 04B (hidden)
Sub Estimate no. - 3C
Dilawarpur Govardhan Ward No. :-04B
WATER SUPPLY DISTRIBUTION SYSTEM
S.N. | Particulars |  |  |  |  | Quantity |  | Unit | Rate | Amount
1/ 2.8 | Earthwork in excavation over areas (exceeding 30 cm in depth 1.5 in width as well as 10 sqm on plan) including disposal of excavated earth lead upto 50m and lift upto 1.5m, disposal earth to be levelled and neatly dressed.
| 110mm dia Pipe | 0 | 0.3 | 1.1 | = | 0 | [6 empty] | 152000
| 90mm dia Pipe | 200 | 0.3 | 1.1 | = | 66 | [6 empty] | 152000
| 75mm dia Pipe | 500 | 0.3 | 1.1 | = | 165
| 63mm dia Pipe | 550 | 0.3 | 1.1 | = | 181.5 | [6 empty] | 152000
| 50 mm dia Pipe | 450 | 0.3 | 1.1 | = | 148.5
| 40mm dia Pipe | 400 | 0.3 | 1.1 | = | 132
|  | 2100 |  |  |  | 693 | M3
| Add 5% extra for fittings = |  |  |  |  | 34.65 | M3
[6 empty] | 727.65 | M3 | P/M3 | 360.7 | 262463.355
2/ 2.26 | Filling available excavated earth (excluding rock) in trenches, plinth, sides of foundations etc. in layers not exceeding 20cm in depth, consolidating each deposited layer by ramming and watering, lead up to 50 m and lift upto 1.5 m. |  |  |  |  | 713.097 | M3 | P/M3 | 123.9 | 88352.7183
3/ 15.2.1 | Demolishing cement concrete manually/by mechanical means including disposal of material within 50 metres lead as per direction of Engineer - in - charge. | [8 empty] | 27525.015
1:3:6 or richer mix
|  | 630 | 0.3 | 0.15 | = | 28.35 | M3 | P/M3 | 970.9
4/ 4.1.3 | Providing and laying in position cement concrete of specified grade excluding the cost of centering and shuttering all work upto plinth |  |  |  |  | 28.35 | M3 | P/M3 | 3998.1 | 113346.135 | 4969
1:2:4 (1 cement: 2 coarse sand : 4 graded stone aggregate 40mm nominal size)
5 | Carriage of the following materials from quarry to work site including loading, unloading and staking at work site as per specification & direction of E/I.
| Coarse Sand (44Km Pucca & 1Km Kaccha Carriage) |  |  |  |  | 13.041 | M3 | P/M3 | 1160.62 | 15135.6454
| Stone chips (195Km Pucca & 5Km unsurafced Carriage) |  |  |  |  | 26.082 | M3 | P/M3 | 4291.17 | 111922.2959
6A/ 18.12 | Providing and fixing G.I.Pipes complete with G.I. Fittings including trenching and refilling etc.
18.12.6 | 50mm dia G.I.Pipe from T/well to PVC Tank |  |  |  |  | 14 | M | P/M | 572.6 | 8016.4 |  |  |  | 611.3975
18.12.8 | 80mm dia G.I.Pipe from PVC Tank to Distribution main |  |  |  |  | 14 | M | P/M | 818.2 | 11454.8
18.12.7 | 65mm dia G.I.Pipe for wash out |  |  |  |  | 12 | M | P/M | 667.7 | 8012.4
7A/ 18.31.1.1 | P/F C.I sluice Valve (with Cap) complete with bolts,nuts,rubber insertions etc
6B/ | Providing and fixing brass gate valve with C.I. wheel of approved quality (screwed end).
| 80mm dia Pipe |  |  |  |  | 2 | Nos. | Each | 2227.6 | 4455.2
| 65mm dia Pipe |  |  |  |  | 1 | Nos. | Each | 1490.7 | 1490.7
| 50mm dia Pipe |  |  |  |  | 1 | Nos. | Each | 878.2 | 878.2
7/ 18.33 | Constructing masonry Chamber 60x60x75 cm inside, in brick work in cement mortar 1:4 (1 cement : 4 coarse sand) for sluice valve,with C.I. surface box 100mm top diameter, 160 mm bottom diameter and 180 mm deep ( inside) with chained lid and RCC top slab 1:2:4 mix (1 cement : 2 coarse sand : 4 graded stone aggregate 20mm nominal size ) , necessary excavation, foundation concrete 1:5:10(1 cement : 5 fine sand : 10 graded stone aggregate 40 mm nominalsize) and inside plastering with cement mortar 1:3 (1 cement : 3coarse sand) 12 mm thick, finished with a floating coat of neat cement complete as per standard specifications & direction of E/I. |  |  |  |  | 4 | Nos. | Each | 7210.6 | 28842.4
| Work for additional depth | [10 empty] | 4.9933
Brick work (1:4) in foundation
| 2 | 1.1 | 0.25 | 0.35 | 0.1925
| 2 | 0.6 | 0.25 | 0.35 | 0.105
6.1.12 |  |  |  |  | 0.2975 | 1.19 | M3 | P/M3 | 5017.9 | 5971.301
13.11.1 | Plaster (1:3)
| 8 | 1.1 |  | 0.35 | 3.08 | 12.32 | M2 | P/M2 | 164.3 | 2024.176
8 | Carriage 10% of item 9 | [8 empty] | 3683.7877
9A/ 18.48 | Providing and placing on terrace (at all floor levels) polyethylene water storage tank, ISI : 12701 marked, with cover and suitable locking arrangement and making necessary holes for inlet, outlet and overflow pipes but without fittings and the base support for tank. |  |  |  |  | 10000 | Ltrs. | P/Ltr. | 9.7 | 97000
9B | Providing and fixing MS clamp consisting of 32mm X 5mm thick two no. rings spaced suitably distance apart. | [7 empty] | LS | 3000
10A | Supplying all materials labours & fixing 50mm dia. G.I pipe for using as filling station etc. All as per direction of E/I
| 50mm dia. Pipe from distribution main |  |  |  |  | 3.5 | M | P/M | 572.6 | 2004.1
10B | Providing and fixing G.I fittings
| 80mmx80mmx50mm dia Tee |  |  |  |  | 1 | No | Each | 225 | 225
| 50mm dia bend |  |  |  |  | 3 | No | Each | 175 | 525
| Providing and fixing gun metal gate valve with C.I. wheel of approved quality (screwed end) :50mm nominal dia. |  |  |  |  | 1 | N | Each | 811.4 | 811.4
10C | Providing designation of 100 A brick Flat soling joints filled with local sand including cost of watering, taxes & royalty all complete as per specification & direction of E/I.
|  | 1 | 0.45 | 0.45 |  | 0.2025 | m2 | p/m2 | 283.3 | 57.3683
11 | Providing and fixing PTMT extension nipple for water tank pipe, fittings of approved quality and colour.
| 50mm dia |  |  |  |  | 2 | Nos. | each | 300 | 600
| 63mm dia |  |  |  |  | 1 | No. | each | 350 | 350
| 80 mm dia |  |  |  |  | 1 | No. | each | 550 | 550
| Sub Total of Part - I | [8 empty] | 0
Part - II
12 | Providing and laying High Density Polyethyene pipe (HDPE pipe) of 20 mm to 225 mm OD and pressure 6.0 Kg/cm2 and 10 Kg/cm2 sutable for water supply which is available in all standard, like ISI-4984/1995 and various grades like PE-80, PE-100 including required specials. Rates are inclusive of , all taxes and duties (Exise duty @12.50% &CST @2% against Form 'C'), labour cess, contractor profit and overhead charges all complete as per direction of Engineer-in-charge.
12A | HDPE pipe of materials grade PE100- PN10 (dia in mm)
| 110mm dia Pipe |  |  |  |  | 0 | M | P/M | 646.25 | 0
| 90mm dia Pipe |  |  |  |  | 200 | M | P/M | 437.96 | 87592
| 75mm dia Pipe |  |  |  |  | 500 | M | P/M | 306.31 | 153155
| 63mm dia Pipe |  |  |  |  | 550 | M | P/M | 218.62 | 120241
13B | HDPE pipe of materials grade PE100- PN8 (dia in mm)
| 50 mm dia Pipe |  |  |  |  | 450 | M | P/M | 116.25 | 52312.5
| 40mm dia Pipe |  |  |  |  | 400 | M | P/M | 76.53 | 30612
13C | Providing all materials labours tools, fittings , specials and tackles for fitting, jointing and connecting HDPE pipes. (5% of the cost of the HDPE pipe .) | [8 empty] | 22195.625
| Sub Total Of Part (II) | [8 empty] | 0
| Grand Total | [8 empty] | 1264805.5226
JE |  |  |  | AE |  |  |  |  | Executive Engineer
P. H. Division, Hajipur.

## Dilawarpur Govardhan 05B&6 (hidden)
Sub Estimate no. - 3D
Dilawarpur Govardhan Ward No. :- 05B&06
WATER SUPPLY DISTRIBUTION SYSTEM
S.N. | Particulars |  |  |  |  | Quantity |  | Unit | Rate | Amount
1/ 2.8 | Earthwork in excavation over areas (exceeding 30 cm in depth 1.5 in width as well as 10 sqm on plan) including disposal of excavated earth lead upto 50m and lift upto 1.5m, disposal earth to be levelled and neatly dressed.
| 110mm dia Pipe | 0 | 0.3 | 1.1 | = | 0 | [6 empty] | 152000
| 90mm dia Pipe | 150 | 0.3 | 1.1 | = | 49.5 | [6 empty] | 152000
| 75mm dia Pipe | 450 | 0.3 | 1.1 | = | 148.5
| 63mm dia Pipe | 550 | 0.3 | 1.1 | = | 181.5 | [6 empty] | 152000
| 50 mm dia Pipe | 350 | 0.3 | 1.1 | = | 115.5
| 40mm dia Pipe | 350 | 0.3 | 1.1 | = | 115.5
|  | 1850 |  |  |  | 610.5 | M3
| Add 5% extra for fittings = |  |  |  |  | 30.525 | M3
[6 empty] | 641.025 | M3 | P/M3 | 360.7 | 231217.7175
2/ 2.26 | Filling available excavated earth (excluding rock) in trenches, plinth, sides of foundations etc. in layers not exceeding 20cm in depth, consolidating each deposited layer by ramming and watering, lead up to 50 m and lift upto 1.5 m. |  |  |  |  | 628.2045 | M3 | P/M3 | 123.9 | 77834.5375
3/ 15.2.1 | Demolishing cement concrete manually/by mechanical means including disposal of material within 50 metres lead as per direction of Engineer - in - charge. | [8 empty] | 24248.2275
1:3:6 or richer mix
|  | 555 | 0.3 | 0.15 | = | 24.975 | M3 | P/M3 | 970.9
4/ 4.1.3 | Providing and laying in position cement concrete of specified grade excluding the cost of centering and shuttering all work upto plinth |  |  |  |  | 24.975 | M3 | P/M3 | 3998.1 | 99852.5475 | 4969
1:2:4 (1 cement: 2 coarse sand : 4 graded stone aggregate 40mm nominal size)
5 | Carriage of the following materials from quarry to work site including loading, unloading and staking at work site as per specification & direction of E/I.
| Coarse Sand (44Km Pucca & 1Km Kaccha Carriage) |  |  |  |  | 11.4885 | M3 | P/M3 | 1160.62 | 13333.7829
| Stone chips (195Km Pucca & 5Km unsurafced Carriage) |  |  |  |  | 22.977 | M3 | P/M3 | 4291.17 | 98598.2131
6A/ 18.12 | Providing and fixing G.I.Pipes complete with G.I. Fittings including trenching and refilling etc.
18.12.6 | 50mm dia G.I.Pipe from T/well to PVC Tank |  |  |  |  | 14 | M | P/M | 572.6 | 8016.4 |  |  |  | 611.3975
18.12.8 | 80mm dia G.I.Pipe from PVC Tank to Distribution main |  |  |  |  | 14 | M | P/M | 818.2 | 11454.8
18.12.7 | 65mm dia G.I.Pipe for wash out |  |  |  |  | 12 | M | P/M | 667.7 | 8012.4
7A/ 18.31.1.1 | P/F C.I sluice Valve (with Cap) complete with bolts,nuts,rubber insertions etc
6B/ | Providing and fixing brass gate valve with C.I. wheel of approved quality (screwed end).
| 80mm dia Pipe |  |  |  |  | 2 | Nos. | Each | 2227.6 | 4455.2
| 65mm dia Pipe |  |  |  |  | 2 | Nos. | Each | 1490.7 | 2981.4
| 50mm dia Pipe |  |  |  |  | 1 | Nos. | Each | 878.2 | 878.2
7/ 18.33 | Constructing masonry Chamber 60x60x75 cm inside, in brick work in cement mortar 1:4 (1 cement : 4 coarse sand) for sluice valve,with C.I. surface box 100mm top diameter, 160 mm bottom diameter and 180 mm deep ( inside) with chained lid and RCC top slab 1:2:4 mix (1 cement : 2 coarse sand : 4 graded stone aggregate 20mm nominal size ) , necessary excavation, foundation concrete 1:5:10(1 cement : 5 fine sand : 10 graded stone aggregate 40 mm nominalsize) and inside plastering with cement mortar 1:3 (1 cement : 3coarse sand) 12 mm thick, finished with a floating coat of neat cement complete as per standard specifications & direction of E/I. |  |  |  |  | 5 | Nos. | Each | 7210.6 | 36053
| Work for additional depth | [10 empty] | 4.9933
Brick work (1:4) in foundation
| 2 | 1.1 | 0.25 | 0.35 | 0.1925
| 2 | 0.6 | 0.25 | 0.35 | 0.105
6.1.12 |  |  |  |  | 0.2975 | 1.4875 | M3 | P/M3 | 5017.9 | 7464.1262
13.11.1 | Plaster (1:3)
| 8 | 1.1 |  | 0.35 | 3.08 | 15.4 | M2 | P/M2 | 164.3 | 2530.22
8 | Carriage 10% of item 9 | [8 empty] | 4604.7346
9A/ 18.48 | Providing and placing on terrace (at all floor levels) polyethylene water storage tank, ISI : 12701 marked, with cover and suitable locking arrangement and making necessary holes for inlet, outlet and overflow pipes but without fittings and the base support for tank. |  |  |  |  | 10000 | Ltrs. | P/Ltr. | 9.7 | 97000
9B | Providing and fixing MS clamp consisting of 32mm X 5mm thick two no. rings spaced suitably distance apart. | [7 empty] | LS | 3000
10A | Supplying all materials labours & fixing 50mm dia. G.I pipe for using as filling station etc. All as per direction of E/I
| 50mm dia. Pipe from distribution main |  |  |  |  | 3.5 | M | P/M | 572.6 | 2004.1
10B | Providing and fixing G.I fittings
| 80mmx80mmx50mm dia Tee |  |  |  |  | 1 | No | Each | 225 | 225
| 50mm dia bend |  |  |  |  | 3 | No | Each | 175 | 525
| Providing and fixing gun metal gate valve with C.I. wheel of approved quality (screwed end) :50mm nominal dia. |  |  |  |  | 1 | N | Each | 811.4 | 811.4
10C | Providing designation of 100 A brick Flat soling joints filled with local sand including cost of watering, taxes & royalty all complete as per specification & direction of E/I.
|  | 1 | 0.45 | 0.45 |  | 0.2025 | m2 | p/m2 | 283.3 | 57.3683
11 | Providing and fixing PTMT extension nipple for water tank pipe, fittings of approved quality and colour.
| 50mm dia |  |  |  |  | 2 | Nos. | each | 300 | 600
| 63mm dia |  |  |  |  | 1 | No. | each | 350 | 350
| 80 mm dia |  |  |  |  | 1 | No. | each | 550 | 550
| Sub Total of Part - I | [8 empty] | 0
Part - II
12 | Providing and laying High Density Polyethyene pipe (HDPE pipe) of 20 mm to 225 mm OD and pressure 6.0 Kg/cm2 and 10 Kg/cm2 sutable for water supply which is available in all standard, like ISI-4984/1995 and various grades like PE-80, PE-100 including required specials. Rates are inclusive of , all taxes and duties (Exise duty @12.50% &CST @2% against Form 'C'), labour cess, contractor profit and overhead charges all complete as per direction of Engineer-in-charge.
12A | HDPE pipe of materials grade PE100- PN10 (dia in mm)
| 110mm dia Pipe |  |  |  |  | 0 | M | P/M | 646.25 | 0
| 90mm dia Pipe |  |  |  |  | 150 | M | P/M | 437.96 | 65694
| 75mm dia Pipe |  |  |  |  | 450 | M | P/M | 306.31 | 137839.5
| 63mm dia Pipe |  |  |  |  | 550 | M | P/M | 218.62 | 120241
13B | HDPE pipe of materials grade PE100- PN8 (dia in mm)
| 50 mm dia Pipe |  |  |  |  | 350 | M | P/M | 116.25 | 40687.5
| 40mm dia Pipe |  |  |  |  | 350 | M | P/M | 76.53 | 26785.5
13C | Providing all materials labours tools, fittings , specials and tackles for fitting, jointing and connecting HDPE pipes. (5% of the cost of the HDPE pipe .) | [8 empty] | 19562.375
| Sub Total Of Part (II) | [8 empty] | 0
| Grand Total | [8 empty] | 1147468.2501
JE |  |  |  | AE |  |  |  |  | Executive Engineer
P. H. Division, Hajipur.

## Dilawarpur Govardhan 07B &6 (hidden)
Sub Estimate no. - 3E
Dilawarpur Govardhan Ward No. :-07B & 6
WATER SUPPLY DISTRIBUTION SYSTEM
S.N. | Particulars |  |  |  |  | Quantity |  | Unit | Rate | Amount
1/ 2.8 | Earthwork in excavation over areas (exceeding 30 cm in depth 1.5 in width as well as 10 sqm on plan) including disposal of excavated earth lead upto 50m and lift upto 1.5m, disposal earth to be levelled and neatly dressed.
| 110mm dia Pipe | 0 | 0.3 | 1.1 | = | 0 | [6 empty] | 152000
| 90mm dia Pipe | 150 | 0.3 | 1.1 | = | 49.5 | [6 empty] | 152000
| 75mm dia Pipe | 450 | 0.3 | 1.1 | = | 148.5
| 63mm dia Pipe | 400 | 0.3 | 1.1 | = | 132 | [6 empty] | 152000
| 50 mm dia Pipe | 300 | 0.3 | 1.1 | = | 99
| 40mm dia Pipe | 300 | 0.3 | 1.1 | = | 99
|  | 1600 |  |  |  | 528 | M3
| Add 5% extra for fittings = |  |  |  |  | 26.4 | M3
[6 empty] | 554.4 | M3 | P/M3 | 360.7 | 199972.08
2/ 2.26 | Filling available excavated earth (excluding rock) in trenches, plinth, sides of foundations etc. in layers not exceeding 20cm in depth, consolidating each deposited layer by ramming and watering, lead up to 50 m and lift upto 1.5 m. |  |  |  |  | 543.312 | M3 | P/M3 | 123.9 | 67316.3568
3/ 15.2.1 | Demolishing cement concrete manually/by mechanical means including disposal of material within 50 metres lead as per direction of Engineer - in - charge. | [8 empty] | 20971.44
1:3:6 or richer mix
|  | 480 | 0.3 | 0.15 | = | 21.6 | M3 | P/M3 | 970.9
4/ 4.1.3 | Providing and laying in position cement concrete of specified grade excluding the cost of centering and shuttering all work upto plinth |  |  |  |  | 21.6 | M3 | P/M3 | 3998.1 | 86358.96 | 4969
1:2:4 (1 cement: 2 coarse sand : 4 graded stone aggregate 40mm nominal size)
5 | Carriage of the following materials from quarry to work site including loading, unloading and staking at work site as per specification & direction of E/I.
| Coarse Sand (44Km Pucca & 1Km Kaccha Carriage) |  |  |  |  | 9.936 | M3 | P/M3 | 1160.62 | 11531.9203
| Stone chips (195Km Pucca & 5Km unsurafced Carriage) |  |  |  |  | 19.872 | M3 | P/M3 | 4291.17 | 85274.1302
6A/ 18.12 | Providing and fixing G.I.Pipes complete with G.I. Fittings including trenching and refilling etc.
18.12.6 | 50mm dia G.I.Pipe from T/well to PVC Tank |  |  |  |  | 14 | M | P/M | 572.6 | 8016.4 |  |  |  | 611.3975
18.12.8 | 80mm dia G.I.Pipe from PVC Tank to Distribution main |  |  |  |  | 14 | M | P/M | 818.2 | 11454.8
18.12.7 | 65mm dia G.I.Pipe for wash out |  |  |  |  | 12 | M | P/M | 667.7 | 8012.4
7A/ 18.31.1.1 | P/F C.I sluice Valve (with Cap) complete with bolts,nuts,rubber insertions etc
6B/ | Providing and fixing brass gate valve with C.I. wheel of approved quality (screwed end).
| 80mm dia Pipe |  |  |  |  | 2 | Nos. | Each | 2227.6 | 4455.2
| 65mm dia Pipe |  |  |  |  | 2 | Nos. | Each | 1490.7 | 2981.4
| 50mm dia Pipe |  |  |  |  | 1 | Nos. | Each | 878.2 | 878.2
7/ 18.33 | Constructing masonry Chamber 60x60x75 cm inside, in brick work in cement mortar 1:4 (1 cement : 4 coarse sand) for sluice valve,with C.I. surface box 100mm top diameter, 160 mm bottom diameter and 180 mm deep ( inside) with chained lid and RCC top slab 1:2:4 mix (1 cement : 2 coarse sand : 4 graded stone aggregate 20mm nominal size ) , necessary excavation, foundation concrete 1:5:10(1 cement : 5 fine sand : 10 graded stone aggregate 40 mm nominalsize) and inside plastering with cement mortar 1:3 (1 cement : 3coarse sand) 12 mm thick, finished with a floating coat of neat cement complete as per standard specifications & direction of E/I. |  |  |  |  | 5 | Nos. | Each | 7210.6 | 36053
| Work for additional depth | [10 empty] | 4.9933
Brick work (1:4) in foundation
| 2 | 1.1 | 0.25 | 0.35 | 0.1925
| 2 | 0.6 | 0.25 | 0.35 | 0.105
6.1.12 |  |  |  |  | 0.2975 | 1.4875 | M3 | P/M3 | 5017.9 | 7464.1262
13.11.1 | Plaster (1:3)
| 8 | 1.1 |  | 0.35 | 3.08 | 15.4 | M2 | P/M2 | 164.3 | 2530.22
8 | Carriage 10% of item 9 | [8 empty] | 4604.7346
9A/ 18.48 | Providing and placing on terrace (at all floor levels) polyethylene water storage tank, ISI : 12701 marked, with cover and suitable locking arrangement and making necessary holes for inlet, outlet and overflow pipes but without fittings and the base support for tank. |  |  |  |  | 10000 | Ltrs. | P/Ltr. | 9.7 | 97000
9B | Providing and fixing MS clamp consisting of 32mm X 5mm thick two no. rings spaced suitably distance apart. | [7 empty] | LS | 3000
10A | Supplying all materials labours & fixing 50mm dia. G.I pipe for using as filling station etc. All as per direction of E/I
| 50mm dia. Pipe from distribution main |  |  |  |  | 3.5 | M | P/M | 572.6 | 2004.1
10B | Providing and fixing G.I fittings
| 80mmx80mmx50mm dia Tee |  |  |  |  | 1 | No | Each | 225 | 225
| 50mm dia bend |  |  |  |  | 3 | No | Each | 175 | 525
| Providing and fixing gun metal gate valve with C.I. wheel of approved quality (screwed end) :50mm nominal dia. |  |  |  |  | 1 | N | Each | 811.4 | 811.4
10C | Providing designation of 100 A brick Flat soling joints filled with local sand including cost of watering, taxes & royalty all complete as per specification & direction of E/I.
|  | 1 | 0.45 | 0.45 |  | 0.2025 | m2 | p/m2 | 283.3 | 57.3683
11 | Providing and fixing PTMT extension nipple for water tank pipe, fittings of approved quality and colour.
| 50mm dia |  |  |  |  | 2 | Nos. | each | 300 | 600
| 63mm dia |  |  |  |  | 1 | No. | each | 350 | 350
| 80 mm dia |  |  |  |  | 1 | No. | each | 550 | 550
| Sub Total of Part - I | [8 empty] | 0
Part - II
12 | Providing and laying High Density Polyethyene pipe (HDPE pipe) of 20 mm to 225 mm OD and pressure 6.0 Kg/cm2 and 10 Kg/cm2 sutable for water supply which is available in all standard, like ISI-4984/1995 and various grades like PE-80, PE-100 including required specials. Rates are inclusive of , all taxes and duties (Exise duty @12.50% &CST @2% against Form 'C'), labour cess, contractor profit and overhead charges all complete as per direction of Engineer-in-charge.
12A | HDPE pipe of materials grade PE100- PN10 (dia in mm)
| 110mm dia Pipe |  |  |  |  | 0 | M | P/M | 646.25 | 0
| 90mm dia Pipe |  |  |  |  | 150 | M | P/M | 437.96 | 65694
| 75mm dia Pipe |  |  |  |  | 450 | M | P/M | 306.31 | 137839.5
| 63mm dia Pipe |  |  |  |  | 400 | M | P/M | 218.62 | 87448
13B | HDPE pipe of materials grade PE100- PN8 (dia in mm)
| 50 mm dia Pipe |  |  |  |  | 300 | M | P/M | 116.25 | 34875
| 40mm dia Pipe |  |  |  |  | 300 | M | P/M | 76.53 | 22959
13C | Providing all materials labours tools, fittings , specials and tackles for fitting, jointing and connecting HDPE pipes. (5% of the cost of the HDPE pipe .) | [8 empty] | 17440.775
| Sub Total Of Part (II) | [8 empty] | 0
| Grand Total | [8 empty] | 1029254.5115
JE |  |  |  | AE |  |  |  |  | Executive Engineer
P. H. Division, Hajipur.

## Dilawarpur Govardhan 14B&15 (hidden)
Sub Estimate no. - 3F
Dilawarpur Govardhan Ward No. :-14B&15
WATER SUPPLY DISTRIBUTION SYSTEM
S.N. | Particulars |  |  |  |  | Quantity |  | Unit | Rate | Amount
1/ 2.8 | Earthwork in excavation over areas (exceeding 30 cm in depth 1.5 in width as well as 10 sqm on plan) including disposal of excavated earth lead upto 50m and lift upto 1.5m, disposal earth to be levelled and neatly dressed.
| 110mm dia Pipe | 0 | 0.3 | 1.1 | = | 0 | [6 empty] | 152000
| 90mm dia Pipe | 150 | 0.3 | 1.1 | = | 49.5 | [6 empty] | 152000
| 75mm dia Pipe | 450 | 0.3 | 1.1 | = | 148.5
| 63mm dia Pipe | 400 | 0.3 | 1.1 | = | 132 | [6 empty] | 152000
| 50 mm dia Pipe | 300 | 0.3 | 1.1 | = | 99
| 40mm dia Pipe | 300 | 0.3 | 1.1 | = | 99
|  | 1600 |  |  |  | 528 | M3
| Add 5% extra for fittings = |  |  |  |  | 26.4 | M3
[6 empty] | 554.4 | M3 | P/M3 | 360.7 | 199972.08
2/ 2.26 | Filling available excavated earth (excluding rock) in trenches, plinth, sides of foundations etc. in layers not exceeding 20cm in depth, consolidating each deposited layer by ramming and watering, lead up to 50 m and lift upto 1.5 m. |  |  |  |  | 543.312 | M3 | P/M3 | 123.9 | 67316.3568
3/ 15.2.1 | Demolishing cement concrete manually/by mechanical means including disposal of material within 50 metres lead as per direction of Engineer - in - charge. | [8 empty] | 20971.44
1:3:6 or richer mix
|  | 480 | 0.3 | 0.15 | = | 21.6 | M3 | P/M3 | 970.9
4/ 4.1.3 | Providing and laying in position cement concrete of specified grade excluding the cost of centering and shuttering all work upto plinth |  |  |  |  | 21.6 | M3 | P/M3 | 3998.1 | 86358.96 | 4969
1:2:4 (1 cement: 2 coarse sand : 4 graded stone aggregate 40mm nominal size)
5 | Carriage of the following materials from quarry to work site including loading, unloading and staking at work site as per specification & direction of E/I.
| Coarse Sand (44Km Pucca & 1Km Kaccha Carriage) |  |  |  |  | 9.936 | M3 | P/M3 | 1160.62 | 11531.9203
| Stone chips (195Km Pucca & 5Km unsurafced Carriage) |  |  |  |  | 19.872 | M3 | P/M3 | 4291.17 | 85274.1302
6A/ 18.12 | Providing and fixing G.I.Pipes complete with G.I. Fittings including trenching and refilling etc.
18.12.6 | 50mm dia G.I.Pipe from T/well to PVC Tank |  |  |  |  | 14 | M | P/M | 572.6 | 8016.4 |  |  |  | 611.3975
18.12.8 | 80mm dia G.I.Pipe from PVC Tank to Distribution main |  |  |  |  | 14 | M | P/M | 818.2 | 11454.8
18.12.7 | 65mm dia G.I.Pipe for wash out |  |  |  |  | 12 | M | P/M | 667.7 | 8012.4
7A/ 18.31.1.1 | P/F C.I sluice Valve (with Cap) complete with bolts,nuts,rubber insertions etc
6B/ | Providing and fixing brass gate valve with C.I. wheel of approved quality (screwed end).
| 80mm dia Pipe |  |  |  |  | 2 | Nos. | Each | 2227.6 | 4455.2
| 65mm dia Pipe |  |  |  |  | 2 | Nos. | Each | 1490.7 | 2981.4
| 50mm dia Pipe |  |  |  |  | 1 | Nos. | Each | 878.2 | 878.2
7/ 18.33 | Constructing masonry Chamber 60x60x75 cm inside, in brick work in cement mortar 1:4 (1 cement : 4 coarse sand) for sluice valve,with C.I. surface box 100mm top diameter, 160 mm bottom diameter and 180 mm deep ( inside) with chained lid and RCC top slab 1:2:4 mix (1 cement : 2 coarse sand : 4 graded stone aggregate 20mm nominal size ) , necessary excavation, foundation concrete 1:5:10(1 cement : 5 fine sand : 10 graded stone aggregate 40 mm nominalsize) and inside plastering with cement mortar 1:3 (1 cement : 3coarse sand) 12 mm thick, finished with a floating coat of neat cement complete as per standard specifications & direction of E/I. |  |  |  |  | 5 | Nos. | Each | 7210.6 | 36053
| Work for additional depth | [10 empty] | 4.9933
Brick work (1:4) in foundation
| 2 | 1.1 | 0.25 | 0.35 | 0.1925
| 2 | 0.6 | 0.25 | 0.35 | 0.105
6.1.12 |  |  |  |  | 0.2975 | 1.4875 | M3 | P/M3 | 5017.9 | 7464.1262
13.11.1 | Plaster (1:3)
| 8 | 1.1 |  | 0.35 | 3.08 | 15.4 | M2 | P/M2 | 164.3 | 2530.22
8 | Carriage 10% of item 9 | [8 empty] | 4604.7346
9A/ 18.48 | Providing and placing on terrace (at all floor levels) polyethylene water storage tank, ISI : 12701 marked, with cover and suitable locking arrangement and making necessary holes for inlet, outlet and overflow pipes but without fittings and the base support for tank. |  |  |  |  | 10000 | Ltrs. | P/Ltr. | 9.7 | 97000
9B | Providing and fixing MS clamp consisting of 32mm X 5mm thick two no. rings spaced suitably distance apart. | [7 empty] | LS | 3000
10A | Supplying all materials labours & fixing 50mm dia. G.I pipe for using as filling station etc. All as per direction of E/I
| 50mm dia. Pipe from distribution main |  |  |  |  | 3.5 | M | P/M | 572.6 | 2004.1
10B | Providing and fixing G.I fittings
| 80mmx80mmx50mm dia Tee |  |  |  |  | 1 | No | Each | 225 | 225
| 50mm dia bend |  |  |  |  | 3 | No | Each | 175 | 525
| Providing and fixing gun metal gate valve with C.I. wheel of approved quality (screwed end) :50mm nominal dia. |  |  |  |  | 1 | N | Each | 811.4 | 811.4
10C | Providing designation of 100 A brick Flat soling joints filled with local sand including cost of watering, taxes & royalty all complete as per specification & direction of E/I.
|  | 1 | 0.45 | 0.45 |  | 0.2025 | m2 | p/m2 | 283.3 | 57.3683
11 | Providing and fixing PTMT extension nipple for water tank pipe, fittings of approved quality and colour.
| 50mm dia |  |  |  |  | 2 | Nos. | each | 300 | 600
| 63mm dia |  |  |  |  | 1 | No. | each | 350 | 350
| 80 mm dia |  |  |  |  | 1 | No. | each | 550 | 550
| Sub Total of Part - I | [8 empty] | 0
Part - II
12 | Providing and laying High Density Polyethyene pipe (HDPE pipe) of 20 mm to 225 mm OD and pressure 6.0 Kg/cm2 and 10 Kg/cm2 sutable for water supply which is available in all standard, like ISI-4984/1995 and various grades like PE-80, PE-100 including required specials. Rates are inclusive of , all taxes and duties (Exise duty @12.50% &CST @2% against Form 'C'), labour cess, contractor profit and overhead charges all complete as per direction of Engineer-in-charge.
12A | HDPE pipe of materials grade PE100- PN10 (dia in mm)
| 110mm dia Pipe |  |  |  |  | 0 | M | P/M | 646.25 | 0
| 90mm dia Pipe |  |  |  |  | 150 | M | P/M | 437.96 | 65694
| 75mm dia Pipe |  |  |  |  | 450 | M | P/M | 306.31 | 137839.5
| 63mm dia Pipe |  |  |  |  | 400 | M | P/M | 218.62 | 87448
13B | HDPE pipe of materials grade PE100- PN8 (dia in mm)
| 50 mm dia Pipe |  |  |  |  | 300 | M | P/M | 116.25 | 34875
| 40mm dia Pipe |  |  |  |  | 300 | M | P/M | 76.53 | 22959
13C | Providing all materials labours tools, fittings , specials and tackles for fitting, jointing and connecting HDPE pipes. (5% of the cost of the HDPE pipe .) | [8 empty] | 17440.775
| Sub Total Of Part (II) | [8 empty] | 0
| Grand Total | [8 empty] | 1029254.5115
JE |  |  |  | AE |  |  |  |  | Executive Engineer
P. H. Division, Hajipur.

## Kanchanpur (hidden)
Sub Estimate no. - 3
BIDUPUR KANCHANPUR 09B YADAV TOLA
WATER SUPPLY DISTRIBUTION SYSTEM
S.N. | Particulars |  |  |  |  | Quantity |  | Unit | Rate | Amount
1/ 2.8 | Earthwork in excavation over areas (exceeding 30 cm in depth 1.5 in width as well as 10 sqm on plan) including disposal of excavated earth lead upto 50m and lift upto 1.5m, disposal earth to be levelled and neatly dressed.
| 110mm dia Pipe | 0 | 0.3 | 1.1 | = | 0 | [6 empty] | 152000
| 90mm dia Pipe | 100 | 0.3 | 1.1 | = | 33 | [6 empty] | 152000
| 75mm dia Pipe | 300 | 0.3 | 1.1 | = | 99
| 63mm dia Pipe | 350 | 0.3 | 1.1 | = | 115.5 | [6 empty] | 152000
| 50 mm dia Pipe | 250 | 0.3 | 1.1 | = | 82.5
| 40mm dia Pipe | 200 | 0.3 | 1.1 | = | 66
|  | 1200 |  |  |  | 396 | M3
| Add 5% extra for fittings = |  |  |  |  | 19.8 | M3
[6 empty] | 415.8 | M3 | P/M3 | 360.7 | 149979.06
2/ 2.26 | Filling available excavated earth (excluding rock) in trenches, plinth, sides of foundations etc. in layers not exceeding 20cm in depth, consolidating each deposited layer by ramming and watering, lead up to 50 m and lift upto 1.5 m. |  |  |  |  | 407.484 | M3 | P/M3 | 123.9 | 50487.2676
3/ 15.2.1 | Demolishing cement concrete manually/by mechanical means including disposal of material within 50 metres lead as per direction of Engineer - in - charge. | [8 empty] | 15728.58
1:3:6 or richer mix
|  | 360 | 0.3 | 0.15 | = | 16.2 | M3 | P/M3 | 970.9
4/ 4.1.3 | Providing and laying in position cement concrete of specified grade excluding the cost of centering and shuttering all work upto plinth |  |  |  |  | 16.2 | M3 | P/M3 | 3998.1 | 64769.22 | 4969
1:2:4 (1 cement: 2 coarse sand : 4 graded stone aggregate 40mm nominal size)
5 | Carriage of the following materials from quarry to work site including loading, unloading and staking at work site as per specification & direction of E/I.
| Coarse Sand (44Km Pucca & 1Km Kaccha Carriage) |  |  |  |  | 7.452 | M3 | P/M3 | 1160.62 | 8648.9402
| Stone chips (195Km Pucca & 5Km unsurafced Carriage) |  |  |  |  | 14.904 | M3 | P/M3 | 4291.17 | 63955.5977
6A/ 18.12 | Providing and fixing G.I.Pipes complete with G.I. Fittings including trenching and refilling etc.
18.12.6 | 50mm dia G.I.Pipe from T/well to PVC Tank |  |  |  |  | 14 | M | P/M | 572.6 | 8016.4 |  |  |  | 611.3975
18.12.8 | 80mm dia G.I.Pipe from PVC Tank to Distribution main |  |  |  |  | 14 | M | P/M | 818.2 | 11454.8
18.12.7 | 65mm dia G.I.Pipe for wash out |  |  |  |  | 12 | M | P/M | 667.7 | 8012.4
7A/ 18.31.1.1 | P/F C.I sluice Valve (with Cap) complete with bolts,nuts,rubber insertions etc
6B/ | Providing and fixing brass gate valve with C.I. wheel of approved quality (screwed end).
| 80mm dia Pipe |  |  |  |  | 2 | Nos. | Each | 2227.6 | 4455.2
| 65mm dia Pipe |  |  |  |  | 2 | Nos. | Each | 1490.7 | 2981.4
| 50mm dia Pipe |  |  |  |  | 2 | Nos. | Each | 878.2 | 1756.4
7/ 18.33 | Constructing masonry Chamber 60x60x75 cm inside, in brick work in cement mortar 1:4 (1 cement : 4 coarse sand) for sluice valve,with C.I. surface box 100mm top diameter, 160 mm bottom diameter and 180 mm deep ( inside) with chained lid and RCC top slab 1:2:4 mix (1 cement : 2 coarse sand : 4 graded stone aggregate 20mm nominal size ) , necessary excavation, foundation concrete 1:5:10(1 cement : 5 fine sand : 10 graded stone aggregate 40 mm nominalsize) and inside plastering with cement mortar 1:3 (1 cement : 3coarse sand) 12 mm thick, finished with a floating coat of neat cement complete as per standard specifications & direction of E/I. |  |  |  |  | 6 | Nos. | Each | 7210.6 | 43263.6
| Work for additional depth | [10 empty] | 4.9933
Brick work (1:4) in foundation
| 2 | 1.1 | 0.25 | 0.35 | 0.1925
| 2 | 0.6 | 0.25 | 0.35 | 0.105
6.1.12 |  |  |  |  | 0.2975 | 1.785 | M3 | P/M3 | 5017.9 | 8956.9515
13.11.1 | Plaster (1:3)
| 8 | 1.1 |  | 0.35 | 3.08 | 18.48 | M2 | P/M2 | 164.3 | 3036.264
8 | Carriage 10% of item 9 | [8 empty] | 5525.6816
9A/ 18.48 | Providing and placing on terrace (at all floor levels) polyethylene water storage tank, ISI : 12701 marked, with cover and suitable locking arrangement and making necessary holes for inlet, outlet and overflow pipes but without fittings and the base support for tank. |  |  |  |  | 10000 | Ltrs. | P/Ltr. | 9.7 | 97000
9B | Providing and fixing MS clamp consisting of 32mm X 5mm thick two no. rings spaced suitably distance apart. | [7 empty] | LS | 3000
10A | Supplying all materials labours & fixing 50mm dia. G.I pipe for using as filling station etc. All as per direction of E/I
| 50mm dia. Pipe from distribution main |  |  |  |  | 3.5 | M | P/M | 572.6 | 2004.1
10B | Providing and fixing G.I fittings
| 80mmx80mmx50mm dia Tee |  |  |  |  | 1 | No | Each | 225 | 225
| 50mm dia bend |  |  |  |  | 3 | No | Each | 175 | 525
| Providing and fixing gun metal gate valve with C.I. wheel of approved quality (screwed end) :50mm nominal dia. |  |  |  |  | 1 | N | Each | 811.4 | 811.4
10C | Providing designation of 100 A brick Flat soling joints filled with local sand including cost of watering, taxes & royalty all complete as per specification & direction of E/I.
|  | 1 | 0.45 | 0.45 |  | 0.2025 | m2 | p/m2 | 283.3 | 57.3683
11 | Providing and fixing PTMT extension nipple for water tank pipe, fittings of approved quality and colour.
| 50mm dia |  |  |  |  | 2 | Nos. | each | 300 | 600
| 63mm dia |  |  |  |  | 1 | No. | each | 350 | 350
| 80 mm dia |  |  |  |  | 1 | No. | each | 550 | 550
| Sub Total of Part - I | [8 empty] | 0
Part - II
12 | Providing and laying High Density Polyethyene pipe (HDPE pipe) of 20 mm to 225 mm OD and pressure 6.0 Kg/cm2 and 10 Kg/cm2 sutable for water supply which is available in all standard, like ISI-4984/1995 and various grades like PE-80, PE-100 including required specials. Rates are inclusive of , all taxes and duties (Exise duty @12.50% &CST @2% against Form 'C'), labour cess, contractor profit and overhead charges all complete as per direction of Engineer-in-charge.
12A | HDPE pipe of materials grade PE100- PN10 (dia in mm)
| 110mm dia Pipe |  |  |  |  | 0 | M | P/M | 646.25 | 0
| 90mm dia Pipe |  |  |  |  | 100 | M | P/M | 437.96 | 43796
| 75mm dia Pipe |  |  |  |  | 300 | M | P/M | 306.31 | 91893
| 63mm dia Pipe |  |  |  |  | 350 | M | P/M | 218.62 | 76517
13B | HDPE pipe of materials grade PE100- PN8 (dia in mm)
| 50 mm dia Pipe |  |  |  |  | 250 | M | P/M | 116.25 | 29062.5
| 40mm dia Pipe |  |  |  |  | 200 | M | P/M | 76.53 | 15306
13C | Providing all materials labours tools, fittings , specials and tackles for fitting, jointing and connecting HDPE pipes. (5% of the cost of the HDPE pipe .) | [8 empty] | 12828.725
| Sub Total Of Part (II) | [8 empty] | 0
| Grand Total | [8 empty] | 825553.8558
Executive Engineer
P. H. Division, Hajipur.

## Kathauliya (hidden)
Sub Estimate no. - 3
BIDUPUR KATHAULIYA 07B DALIT TOLA
WATER SUPPLY DISTRIBUTION SYSTEM
S.N. | Particulars |  |  |  |  | Quantity |  | Unit | Rate | Amount
1/ 2.8 | Earthwork in excavation over areas (exceeding 30 cm in depth 1.5 in width as well as 10 sqm on plan) including disposal of excavated earth lead upto 50m and lift upto 1.5m, disposal earth to be levelled and neatly dressed.
| 110mm dia Pipe | 0 | 0.3 | 1.1 | = | 0 | [6 empty] | 152000
| 90mm dia Pipe | 200 | 0.3 | 1.1 | = | 66 | [6 empty] | 152000
| 75mm dia Pipe | 500 | 0.3 | 1.1 | = | 165
| 63mm dia Pipe | 550 | 0.3 | 1.1 | = | 181.5 | [6 empty] | 152000
| 50 mm dia Pipe | 500 | 0.3 | 1.1 | = | 165
| 40mm dia Pipe | 450 | 0.3 | 1.1 | = | 148.5
|  | 2200 |  |  |  | 726 | M3
| Add 5% extra for fittings = |  |  |  |  | 36.3 | M3
[6 empty] | 762.3 | M3 | P/M3 | 360.7 | 274961.61
2/ 2.26 | Filling available excavated earth (excluding rock) in trenches, plinth, sides of foundations etc. in layers not exceeding 20cm in depth, consolidating each deposited layer by ramming and watering, lead up to 50 m and lift upto 1.5 m. |  |  |  |  | 747.054 | M3 | P/M3 | 123.9 | 92559.9906
3/ 15.2.1 | Demolishing cement concrete manually/by mechanical means including disposal of material within 50 metres lead as per direction of Engineer - in - charge. | [8 empty] | 28835.73
1:3:6 or richer mix
|  | 660 | 0.3 | 0.15 | = | 29.7 | M3 | P/M3 | 970.9
4/ 4.1.3 | Providing and laying in position cement concrete of specified grade excluding the cost of centering and shuttering all work upto plinth |  |  |  |  | 29.7 | M3 | P/M3 | 3998.1 | 118743.57 | 4969
1:2:4 (1 cement: 2 coarse sand : 4 graded stone aggregate 40mm nominal size)
5 | Carriage of the following materials from quarry to work site including loading, unloading and staking at work site as per specification & direction of E/I.
| Coarse Sand (44Km Pucca & 1Km Kaccha Carriage) |  |  |  |  | 13.662 | M3 | P/M3 | 1160.62 | 15856.3904
| Stone chips (195Km Pucca & 5Km unsurafced Carriage) |  |  |  |  | 27.324 | M3 | P/M3 | 4291.17 | 117251.9291
6A/ 18.12 | Providing and fixing G.I.Pipes complete with G.I. Fittings including trenching and refilling etc.
18.12.6 | 50mm dia G.I.Pipe from T/well to PVC Tank |  |  |  |  | 14 | M | P/M | 572.6 | 8016.4 |  |  |  | 611.3975
18.12.8 | 80mm dia G.I.Pipe from PVC Tank to Distribution main |  |  |  |  | 14 | M | P/M | 818.2 | 11454.8
18.12.7 | 65mm dia G.I.Pipe for wash out |  |  |  |  | 12 | M | P/M | 667.7 | 8012.4
7A/ 18.31.1.1 | P/F C.I sluice Valve (with Cap) complete with bolts,nuts,rubber insertions etc
6B/ | Providing and fixing brass gate valve with C.I. wheel of approved quality (screwed end).
| 80mm dia Pipe |  |  |  |  | 2 | Nos. | Each | 2227.6 | 4455.2
| 65mm dia Pipe |  |  |  |  | 2 | Nos. | Each | 1490.7 | 2981.4
| 50mm dia Pipe |  |  |  |  | 2 | Nos. | Each | 878.2 | 1756.4
7/ 18.33 | Constructing masonry Chamber 60x60x75 cm inside, in brick work in cement mortar 1:4 (1 cement : 4 coarse sand) for sluice valve,with C.I. surface box 100mm top diameter, 160 mm bottom diameter and 180 mm deep ( inside) with chained lid and RCC top slab 1:2:4 mix (1 cement : 2 coarse sand : 4 graded stone aggregate 20mm nominal size ) , necessary excavation, foundation concrete 1:5:10(1 cement : 5 fine sand : 10 graded stone aggregate 40 mm nominalsize) and inside plastering with cement mortar 1:3 (1 cement : 3coarse sand) 12 mm thick, finished with a floating coat of neat cement complete as per standard specifications & direction of E/I. |  |  |  |  | 6 | Nos. | Each | 7210.6 | 43263.6
| Work for additional depth | [10 empty] | 4.9933
Brick work (1:4) in foundation
| 2 | 1.1 | 0.25 | 0.35 | 0.1925
| 2 | 0.6 | 0.25 | 0.35 | 0.105
6.1.12 |  |  |  |  | 0.2975 | 1.785 | M3 | P/M3 | 5017.9 | 8956.9515
13.11.1 | Plaster (1:3)
| 8 | 1.1 |  | 0.35 | 3.08 | 18.48 | M2 | P/M2 | 164.3 | 3036.264
8 | Carriage 10% of item 9 | [8 empty] | 5525.6816
9A/ 18.48 | Providing and placing on terrace (at all floor levels) polyethylene water storage tank, ISI : 12701 marked, with cover and suitable locking arrangement and making necessary holes for inlet, outlet and overflow pipes but without fittings and the base support for tank. |  |  |  |  | 10000 | Ltrs. | P/Ltr. | 9.7 | 97000
9B | Providing and fixing MS clamp consisting of 32mm X 5mm thick two no. rings spaced suitably distance apart. | [7 empty] | LS | 3000
10A | Supplying all materials labours & fixing 50mm dia. G.I pipe for using as filling station etc. All as per direction of E/I
| 50mm dia. Pipe from distribution main |  |  |  |  | 3.5 | M | P/M | 572.6 | 2004.1
10B | Providing and fixing G.I fittings
| 80mmx80mmx50mm dia Tee |  |  |  |  | 1 | No | Each | 225 | 225
| 50mm dia bend |  |  |  |  | 3 | No | Each | 175 | 525
| Providing and fixing gun metal gate valve with C.I. wheel of approved quality (screwed end) :50mm nominal dia. |  |  |  |  | 1 | N | Each | 811.4 | 811.4
10C | Providing designation of 100 A brick Flat soling joints filled with local sand including cost of watering, taxes & royalty all complete as per specification & direction of E/I.
|  | 1 | 0.45 | 0.45 |  | 0.2025 | m2 | p/m2 | 283.3 | 57.3683
11 | Providing and fixing PTMT extension nipple for water tank pipe, fittings of approved quality and colour.
| 50mm dia |  |  |  |  | 2 | Nos. | each | 300 | 600
| 63mm dia |  |  |  |  | 1 | No. | each | 350 | 350
| 80 mm dia |  |  |  |  | 1 | No. | each | 550 | 550
| Sub Total of Part - I | [8 empty] | 0
Part - II
12 | Providing and laying High Density Polyethyene pipe (HDPE pipe) of 20 mm to 225 mm OD and pressure 6.0 Kg/cm2 and 10 Kg/cm2 sutable for water supply which is available in all standard, like ISI-4984/1995 and various grades like PE-80, PE-100 including required specials. Rates are inclusive of , all taxes and duties (Exise duty @12.50% &CST @2% against Form 'C'), labour cess, contractor profit and overhead charges all complete as per direction of Engineer-in-charge.
12A | HDPE pipe of materials grade PE100- PN10 (dia in mm)
| 110mm dia Pipe |  |  |  |  | 0 | M | P/M | 646.25 | 0
| 90mm dia Pipe |  |  |  |  | 200 | M | P/M | 437.96 | 87592
| 75mm dia Pipe |  |  |  |  | 500 | M | P/M | 306.31 | 153155
| 63mm dia Pipe |  |  |  |  | 550 | M | P/M | 218.62 | 120241
13B | HDPE pipe of materials grade PE100- PN8 (dia in mm)
| 50 mm dia Pipe |  |  |  |  | 500 | M | P/M | 116.25 | 58125
| 40mm dia Pipe |  |  |  |  | 450 | M | P/M | 76.53 | 34438.5
13C | Providing all materials labours tools, fittings , specials and tackles for fitting, jointing and connecting HDPE pipes. (5% of the cost of the HDPE pipe .) | [8 empty] | 22677.575
| Sub Total Of Part (II) | [8 empty] | 0
| Grand Total | [8 empty] | 1327020.2604
Executive Engineer
P. H. Division, Hajipur.

## Khanpur Pakri 02B&04B (hidden)
Sub Estimate no. - 3A
Khanpur Pakri WARD NO. :-02B&04B
WATER SUPPLY DISTRIBUTION SYSTEM
S.N. | Particulars |  |  |  |  | Quantity |  | Unit | Rate | Amount
1/ 2.8 | Earthwork in excavation over areas (exceeding 30 cm in depth 1.5 in width as well as 10 sqm on plan) including disposal of excavated earth lead upto 50m and lift upto 1.5m, disposal earth to be levelled and neatly dressed.
| 110mm dia Pipe | 0 | 0.3 | 1.1 | = | 0 | [6 empty] | 152000
| 90mm dia Pipe | 100 | 0.3 | 1.1 | = | 33 | [6 empty] | 152000
| 75mm dia Pipe | 200 | 0.3 | 1.1 | = | 66
| 63mm dia Pipe | 200 | 0.3 | 1.1 | = | 66 | [6 empty] | 152000
| 50 mm dia Pipe | 250 | 0.3 | 1.1 | = | 82.5
| 40mm dia Pipe | 300 | 0.3 | 1.1 | = | 99
|  | 1050 |  |  |  | 346.5 | M3
| Add 5% extra for fittings = |  |  |  |  | 17.325 | M3
[6 empty] | 363.825 | M3 | P/M3 | 360.7 | 131231.6775
2/ 2.26 | Filling available excavated earth (excluding rock) in trenches, plinth, sides of foundations etc. in layers not exceeding 20cm in depth, consolidating each deposited layer by ramming and watering, lead up to 50 m and lift upto 1.5 m. |  |  |  |  | 356.5485 | M3 | P/M3 | 123.9 | 44176.3592
3/ 15.2.1 | Demolishing cement concrete manually/by mechanical means including disposal of material within 50 metres lead as per direction of Engineer - in - charge. | [8 empty] | 13762.5075
1:3:6 or richer mix
|  | 315 | 0.3 | 0.15 | = | 14.175 | M3 | P/M3 | 970.9
4/ 4.1.3 | Providing and laying in position cement concrete of specified grade excluding the cost of centering and shuttering all work upto plinth |  |  |  |  | 14.175 | M3 | P/M3 | 3998.1 | 56673.0675 | 4969
1:2:4 (1 cement: 2 coarse sand : 4 graded stone aggregate 40mm nominal size)
5 | Carriage of the following materials from quarry to work site including loading, unloading and staking at work site as per specification & direction of E/I.
| Coarse Sand (44Km Pucca & 1Km Kaccha Carriage) |  |  |  |  | 6.5205 | M3 | P/M3 | 1160.62 | 7567.8227
| Stone chips (195Km Pucca & 5Km unsurafced Carriage) |  |  |  |  | 13.041 | M3 | P/M3 | 4291.17 | 55961.148
6A/ 18.12 | Providing and fixing G.I.Pipes complete with G.I. Fittings including trenching and refilling etc.
18.12.6 | 50mm dia G.I.Pipe from T/well to PVC Tank |  |  |  |  | 14 | M | P/M | 572.6 | 8016.4 |  |  |  | 611.3975
18.12.8 | 80mm dia G.I.Pipe from PVC Tank to Distribution main |  |  |  |  | 14 | M | P/M | 818.2 | 11454.8
18.12.7 | 65mm dia G.I.Pipe for wash out |  |  |  |  | 12 | M | P/M | 667.7 | 8012.4
7A/ 18.31.1.1 | P/F C.I sluice Valve (with Cap) complete with bolts,nuts,rubber insertions etc
6B/ | Providing and fixing brass gate valve with C.I. wheel of approved quality (screwed end).
| 80mm dia Pipe |  |  |  |  | 2 | Nos. | Each | 2227.6 | 4455.2
| 65mm dia Pipe |  |  |  |  | 2 | Nos. | Each | 1490.7 | 2981.4
| 50mm dia Pipe |  |  |  |  | 1 | Nos. | Each | 878.2 | 878.2
7/ 18.33 | Constructing masonry Chamber 60x60x75 cm inside, in brick work in cement mortar 1:4 (1 cement : 4 coarse sand) for sluice valve,with C.I. surface box 100mm top diameter, 160 mm bottom diameter and 180 mm deep ( inside) with chained lid and RCC top slab 1:2:4 mix (1 cement : 2 coarse sand : 4 graded stone aggregate 20mm nominal size ) , necessary excavation, foundation concrete 1:5:10(1 cement : 5 fine sand : 10 graded stone aggregate 40 mm nominalsize) and inside plastering with cement mortar 1:3 (1 cement : 3coarse sand) 12 mm thick, finished with a floating coat of neat cement complete as per standard specifications & direction of E/I. |  |  |  |  | 5 | Nos. | Each | 7210.6 | 36053
| Work for additional depth | [10 empty] | 4.9933
Brick work (1:4) in foundation
| 2 | 1.1 | 0.25 | 0.35 | 0.1925
| 2 | 0.6 | 0.25 | 0.35 | 0.105
6.1.12 |  |  |  |  | 0.2975 | 1.4875 | M3 | P/M3 | 5017.9 | 7464.1262
13.11.1 | Plaster (1:3)
| 8 | 1.1 |  | 0.35 | 3.08 | 15.4 | M2 | P/M2 | 164.3 | 2530.22
8 | Carriage 10% of item 9 | [8 empty] | 4604.7346
9A/ 18.48 | Providing and placing on terrace (at all floor levels) polyethylene water storage tank, ISI : 12701 marked, with cover and suitable locking arrangement and making necessary holes for inlet, outlet and overflow pipes but without fittings and the base support for tank. |  |  |  |  | 10000 | Ltrs. | P/Ltr. | 9.7 | 97000
9B | Providing and fixing MS clamp consisting of 32mm X 5mm thick two no. rings spaced suitably distance apart. | [7 empty] | LS | 3000
10A | Supplying all materials labours & fixing 50mm dia. G.I pipe for using as filling station etc. All as per direction of E/I
| 50mm dia. Pipe from distribution main |  |  |  |  | 3.5 | M | P/M | 572.6 | 2004.1
10B | Providing and fixing G.I fittings
| 80mmx80mmx50mm dia Tee |  |  |  |  | 1 | No | Each | 225 | 225
| 50mm dia bend |  |  |  |  | 3 | No | Each | 175 | 525
| Providing and fixing gun metal gate valve with C.I. wheel of approved quality (screwed end) :50mm nominal dia. |  |  |  |  | 1 | N | Each | 811.4 | 811.4
10C | Providing designation of 100 A brick Flat soling joints filled with local sand including cost of watering, taxes & royalty all complete as per specification & direction of E/I.
|  | 1 | 0.45 | 0.45 |  | 0.2025 | m2 | p/m2 | 283.3 | 57.3683
11 | Providing and fixing PTMT extension nipple for water tank pipe, fittings of approved quality and colour.
| 50mm dia |  |  |  |  | 2 | Nos. | each | 300 | 600
| 63mm dia |  |  |  |  | 1 | No. | each | 350 | 350
| 80 mm dia |  |  |  |  | 1 | No. | each | 550 | 550
| Sub Total of Part - I | [8 empty] | 0
Part - II
12 | Providing and laying High Density Polyethyene pipe (HDPE pipe) of 20 mm to 225 mm OD and pressure 6.0 Kg/cm2 and 10 Kg/cm2 sutable for water supply which is available in all standard, like ISI-4984/1995 and various grades like PE-80, PE-100 including required specials. Rates are inclusive of , all taxes and duties (Exise duty @12.50% &CST @2% against Form 'C'), labour cess, contractor profit and overhead charges all complete as per direction of Engineer-in-charge.
12A | HDPE pipe of materials grade PE100- PN10 (dia in mm)
| 110mm dia Pipe |  |  |  |  | 0 | M | P/M | 646.25 | 0
| 90mm dia Pipe |  |  |  |  | 100 | M | P/M | 437.96 | 43796
| 75mm dia Pipe |  |  |  |  | 200 | M | P/M | 306.31 | 61262
| 63mm dia Pipe |  |  |  |  | 200 | M | P/M | 218.62 | 43724
13B | HDPE pipe of materials grade PE100- PN8 (dia in mm)
| 50 mm dia Pipe |  |  |  |  | 250 | M | P/M | 116.25 | 29062.5
| 40mm dia Pipe |  |  |  |  | 300 | M | P/M | 76.53 | 22959
13C | Providing all materials labours tools, fittings , specials and tackles for fitting, jointing and connecting HDPE pipes. (5% of the cost of the HDPE pipe .) | [8 empty] | 10040.175
| Sub Total Of Part (II) | [8 empty] | 0
| Grand Total | [8 empty] | 711789.6065
JE |  |  |  | AE |  |  |  |  | Executive Engineer
P. H. Division, Hajipur.

## Khanpur Pakri 4B (hidden)
Sub Estimate no. - 3B
Khanpur Pakri WARD NO. :-04B
WATER SUPPLY DISTRIBUTION SYSTEM
S.N. | Particulars |  |  |  |  | Quantity |  | Unit | Rate | Amount
1/ 2.8 | Earthwork in excavation over areas (exceeding 30 cm in depth 1.5 in width as well as 10 sqm on plan) including disposal of excavated earth lead upto 50m and lift upto 1.5m, disposal earth to be levelled and neatly dressed.
| 110mm dia Pipe | 0 | 0.3 | 1.1 | = | 0 | [6 empty] | 152000
| 90mm dia Pipe | 100 | 0.3 | 1.1 | = | 33 | [6 empty] | 152000
| 75mm dia Pipe | 200 | 0.3 | 1.1 | = | 66
| 63mm dia Pipe | 250 | 0.3 | 1.1 | = | 82.5 | [6 empty] | 152000
| 50 mm dia Pipe | 250 | 0.3 | 1.1 | = | 82.5
| 40mm dia Pipe | 200 | 0.3 | 1.1 | = | 66
|  | 1000 |  |  |  | 330 | M3
| Add 5% extra for fittings = |  |  |  |  | 16.5 | M3
[6 empty] | 346.5 | M3 | P/M3 | 360.7 | 124982.55
2/ 2.26 | Filling available excavated earth (excluding rock) in trenches, plinth, sides of foundations etc. in layers not exceeding 20cm in depth, consolidating each deposited layer by ramming and watering, lead up to 50 m and lift upto 1.5 m. |  |  |  |  | 339.57 | M3 | P/M3 | 123.9 | 42072.723
3/ 15.2.1 | Demolishing cement concrete manually/by mechanical means including disposal of material within 50 metres lead as per direction of Engineer - in - charge. | [8 empty] | 13107.15
1:3:6 or richer mix
|  | 300 | 0.3 | 0.15 | = | 13.5 | M3 | P/M3 | 970.9
4/ 4.1.3 | Providing and laying in position cement concrete of specified grade excluding the cost of centering and shuttering all work upto plinth |  |  |  |  | 13.5 | M3 | P/M3 | 3998.1 | 53974.35 | 4969
1:2:4 (1 cement: 2 coarse sand : 4 graded stone aggregate 40mm nominal size)
5 | Carriage of the following materials from quarry to work site including loading, unloading and staking at work site as per specification & direction of E/I.
| Coarse Sand (44Km Pucca & 1Km Kaccha Carriage) |  |  |  |  | 6.21 | M3 | P/M3 | 1160.62 | 7207.4502
| Stone chips (195Km Pucca & 5Km unsurafced Carriage) |  |  |  |  | 12.42 | M3 | P/M3 | 4291.17 | 53296.3314
6A/ 18.12 | Providing and fixing G.I.Pipes complete with G.I. Fittings including trenching and refilling etc.
18.12.6 | 50mm dia G.I.Pipe from T/well to PVC Tank |  |  |  |  | 14 | M | P/M | 572.6 | 8016.4 |  |  |  | 611.3975
18.12.8 | 80mm dia G.I.Pipe from PVC Tank to Distribution main |  |  |  |  | 14 | M | P/M | 818.2 | 11454.8
18.12.7 | 65mm dia G.I.Pipe for wash out |  |  |  |  | 12 | M | P/M | 667.7 | 8012.4
7A/ 18.31.1.1 | P/F C.I sluice Valve (with Cap) complete with bolts,nuts,rubber insertions etc
6B/ | Providing and fixing brass gate valve with C.I. wheel of approved quality (screwed end).
| 80mm dia Pipe |  |  |  |  | 2 | Nos. | Each | 2227.6 | 4455.2
| 65mm dia Pipe |  |  |  |  | 1 | Nos. | Each | 1490.7 | 1490.7
| 50mm dia Pipe |  |  |  |  | 1 | Nos. | Each | 878.2 | 878.2
7/ 18.33 | Constructing masonry Chamber 60x60x75 cm inside, in brick work in cement mortar 1:4 (1 cement : 4 coarse sand) for sluice valve,with C.I. surface box 100mm top diameter, 160 mm bottom diameter and 180 mm deep ( inside) with chained lid and RCC top slab 1:2:4 mix (1 cement : 2 coarse sand : 4 graded stone aggregate 20mm nominal size ) , necessary excavation, foundation concrete 1:5:10(1 cement : 5 fine sand : 10 graded stone aggregate 40 mm nominalsize) and inside plastering with cement mortar 1:3 (1 cement : 3coarse sand) 12 mm thick, finished with a floating coat of neat cement complete as per standard specifications & direction of E/I. |  |  |  |  | 4 | Nos. | Each | 7210.6 | 28842.4
| Work for additional depth | [10 empty] | 4.9933
Brick work (1:4) in foundation
| 2 | 1.1 | 0.25 | 0.35 | 0.1925
| 2 | 0.6 | 0.25 | 0.35 | 0.105
6.1.12 |  |  |  |  | 0.2975 | 1.19 | M3 | P/M3 | 5017.9 | 5971.301
13.11.1 | Plaster (1:3)
| 8 | 1.1 |  | 0.35 | 3.08 | 12.32 | M2 | P/M2 | 164.3 | 2024.176
8 | Carriage 10% of item 9 | [8 empty] | 3683.7877
9A/ 18.48 | Providing and placing on terrace (at all floor levels) polyethylene water storage tank, ISI : 12701 marked, with cover and suitable locking arrangement and making necessary holes for inlet, outlet and overflow pipes but without fittings and the base support for tank. |  |  |  |  | 10000 | Ltrs. | P/Ltr. | 9.7 | 97000
9B | Providing and fixing MS clamp consisting of 32mm X 5mm thick two no. rings spaced suitably distance apart. | [7 empty] | LS | 3000
10A | Supplying all materials labours & fixing 50mm dia. G.I pipe for using as filling station etc. All as per direction of E/I
| 50mm dia. Pipe from distribution main |  |  |  |  | 3.5 | M | P/M | 572.6 | 2004.1
10B | Providing and fixing G.I fittings
| 80mmx80mmx50mm dia Tee |  |  |  |  | 1 | No | Each | 225 | 225
| 50mm dia bend |  |  |  |  | 3 | No | Each | 175 | 525
| Providing and fixing gun metal gate valve with C.I. wheel of approved quality (screwed end) :50mm nominal dia. |  |  |  |  | 1 | N | Each | 811.4 | 811.4
10C | Providing designation of 100 A brick Flat soling joints filled with local sand including cost of watering, taxes & royalty all complete as per specification & direction of E/I.
|  | 1 | 0.45 | 0.45 |  | 0.2025 | m2 | p/m2 | 283.3 | 57.3683
11 | Providing and fixing PTMT extension nipple for water tank pipe, fittings of approved quality and colour.
| 50mm dia |  |  |  |  | 2 | Nos. | each | 300 | 600
| 63mm dia |  |  |  |  | 1 | No. | each | 350 | 350
| 80 mm dia |  |  |  |  | 1 | No. | each | 550 | 550
| Sub Total of Part - I | [8 empty] | 0
Part - II
12 | Providing and laying High Density Polyethyene pipe (HDPE pipe) of 20 mm to 225 mm OD and pressure 6.0 Kg/cm2 and 10 Kg/cm2 sutable for water supply which is available in all standard, like ISI-4984/1995 and various grades like PE-80, PE-100 including required specials. Rates are inclusive of , all taxes and duties (Exise duty @12.50% &CST @2% against Form 'C'), labour cess, contractor profit and overhead charges all complete as per direction of Engineer-in-charge.
12A | HDPE pipe of materials grade PE100- PN10 (dia in mm)
| 110mm dia Pipe |  |  |  |  | 0 | M | P/M | 646.25 | 0
| 90mm dia Pipe |  |  |  |  | 100 | M | P/M | 437.96 | 43796
| 75mm dia Pipe |  |  |  |  | 200 | M | P/M | 306.31 | 61262
| 63mm dia Pipe |  |  |  |  | 250 | M | P/M | 218.62 | 54655
13B | HDPE pipe of materials grade PE100- PN8 (dia in mm)
| 50 mm dia Pipe |  |  |  |  | 250 | M | P/M | 116.25 | 29062.5
| 40mm dia Pipe |  |  |  |  | 200 | M | P/M | 76.53 | 15306
13C | Providing all materials labours tools, fittings , specials and tackles for fitting, jointing and connecting HDPE pipes. (5% of the cost of the HDPE pipe .) | [8 empty] | 10204.075
| Sub Total Of Part (II) | [8 empty] | 0
| Grand Total | [8 empty] | 688878.3625
JE |  |  |  | AE |  |  |  |  | Executive Engineer
P. H. Division, Hajipur.

## Khanpur Pakri 10B (hidden)
Sub Estimate no. - 3C
Khanpur Pakri WARD NO. :-10B
WATER SUPPLY DISTRIBUTION SYSTEM
S.N. | Particulars |  |  |  |  | Quantity |  | Unit | Rate | Amount
1/ 2.8 | Earthwork in excavation over areas (exceeding 30 cm in depth 1.5 in width as well as 10 sqm on plan) including disposal of excavated earth lead upto 50m and lift upto 1.5m, disposal earth to be levelled and neatly dressed.
| 110mm dia Pipe | 0 | 0.3 | 1.1 | = | 0 | [6 empty] | 152000
| 90mm dia Pipe | 150 | 0.3 | 1.1 | = | 49.5 | [6 empty] | 152000
| 75mm dia Pipe | 500 | 0.3 | 1.1 | = | 165
| 63mm dia Pipe | 550 | 0.3 | 1.1 | = | 181.5 | [6 empty] | 152000
| 50 mm dia Pipe | 450 | 0.3 | 1.1 | = | 148.5
| 40mm dia Pipe | 350 | 0.3 | 1.1 | = | 115.5
|  | 2000 |  |  |  | 660 | M3
| Add 5% extra for fittings = |  |  |  |  | 33 | M3
[6 empty] | 693 | M3 | P/M3 | 360.7 | 249965.1
2/ 2.26 | Filling available excavated earth (excluding rock) in trenches, plinth, sides of foundations etc. in layers not exceeding 20cm in depth, consolidating each deposited layer by ramming and watering, lead up to 50 m and lift upto 1.5 m. |  |  |  |  | 679.14 | M3 | P/M3 | 123.9 | 84145.446
3/ 15.2.1 | Demolishing cement concrete manually/by mechanical means including disposal of material within 50 metres lead as per direction of Engineer - in - charge. | [8 empty] | 26214.3
1:3:6 or richer mix
|  | 600 | 0.3 | 0.15 | = | 27 | M3 | P/M3 | 970.9
4/ 4.1.3 | Providing and laying in position cement concrete of specified grade excluding the cost of centering and shuttering all work upto plinth |  |  |  |  | 27 | M3 | P/M3 | 3998.1 | 107948.7 | 4969
1:2:4 (1 cement: 2 coarse sand : 4 graded stone aggregate 40mm nominal size)
5 | Carriage of the following materials from quarry to work site including loading, unloading and staking at work site as per specification & direction of E/I.
| Coarse Sand (44Km Pucca & 1Km Kaccha Carriage) |  |  |  |  | 12.42 | M3 | P/M3 | 1160.62 | 14414.9004
| Stone chips (195Km Pucca & 5Km unsurafced Carriage) |  |  |  |  | 24.84 | M3 | P/M3 | 4291.17 | 106592.6628
6A/ 18.12 | Providing and fixing G.I.Pipes complete with G.I. Fittings including trenching and refilling etc.
18.12.6 | 50mm dia G.I.Pipe from T/well to PVC Tank |  |  |  |  | 14 | M | P/M | 572.6 | 8016.4 |  |  |  | 611.3975
18.12.8 | 80mm dia G.I.Pipe from PVC Tank to Distribution main |  |  |  |  | 14 | M | P/M | 818.2 | 11454.8
18.12.7 | 65mm dia G.I.Pipe for wash out |  |  |  |  | 12 | M | P/M | 667.7 | 8012.4
7A/ 18.31.1.1 | P/F C.I sluice Valve (with Cap) complete with bolts,nuts,rubber insertions etc
6B/ | Providing and fixing brass gate valve with C.I. wheel of approved quality (screwed end).
| 80mm dia Pipe |  |  |  |  | 2 | Nos. | Each | 2227.6 | 4455.2
| 65mm dia Pipe |  |  |  |  | 1 | Nos. | Each | 1490.7 | 1490.7
| 50mm dia Pipe |  |  |  |  | 1 | Nos. | Each | 878.2 | 878.2
7/ 18.33 | Constructing masonry Chamber 60x60x75 cm inside, in brick work in cement mortar 1:4 (1 cement : 4 coarse sand) for sluice valve,with C.I. surface box 100mm top diameter, 160 mm bottom diameter and 180 mm deep ( inside) with chained lid and RCC top slab 1:2:4 mix (1 cement : 2 coarse sand : 4 graded stone aggregate 20mm nominal size ) , necessary excavation, foundation concrete 1:5:10(1 cement : 5 fine sand : 10 graded stone aggregate 40 mm nominalsize) and inside plastering with cement mortar 1:3 (1 cement : 3coarse sand) 12 mm thick, finished with a floating coat of neat cement complete as per standard specifications & direction of E/I. |  |  |  |  | 4 | Nos. | Each | 7210.6 | 28842.4
| Work for additional depth | [10 empty] | 4.9933
Brick work (1:4) in foundation
| 2 | 1.1 | 0.25 | 0.35 | 0.1925
| 2 | 0.6 | 0.25 | 0.35 | 0.105
6.1.12 |  |  |  |  | 0.2975 | 1.19 | M3 | P/M3 | 5017.9 | 5971.301
13.11.1 | Plaster (1:3)
| 8 | 1.1 |  | 0.35 | 3.08 | 12.32 | M2 | P/M2 | 164.3 | 2024.176
8 | Carriage 10% of item 9 | [8 empty] | 3683.7877
9A/ 18.48 | Providing and placing on terrace (at all floor levels) polyethylene water storage tank, ISI : 12701 marked, with cover and suitable locking arrangement and making necessary holes for inlet, outlet and overflow pipes but without fittings and the base support for tank. |  |  |  |  | 10000 | Ltrs. | P/Ltr. | 9.7 | 97000
9B | Providing and fixing MS clamp consisting of 32mm X 5mm thick two no. rings spaced suitably distance apart. | [7 empty] | LS | 3000
10A | Supplying all materials labours & fixing 50mm dia. G.I pipe for using as filling station etc. All as per direction of E/I
| 50mm dia. Pipe from distribution main |  |  |  |  | 3.5 | M | P/M | 572.6 | 2004.1
10B | Providing and fixing G.I fittings
| 80mmx80mmx50mm dia Tee |  |  |  |  | 1 | No | Each | 225 | 225
| 50mm dia bend |  |  |  |  | 3 | No | Each | 175 | 525
| Providing and fixing gun metal gate valve with C.I. wheel of approved quality (screwed end) :50mm nominal dia. |  |  |  |  | 1 | N | Each | 811.4 | 811.4
10C | Providing designation of 100 A brick Flat soling joints filled with local sand including cost of watering, taxes & royalty all complete as per specification & direction of E/I.
|  | 1 | 0.45 | 0.45 |  | 0.2025 | m2 | p/m2 | 283.3 | 57.3683
11 | Providing and fixing PTMT extension nipple for water tank pipe, fittings of approved quality and colour.
| 50mm dia |  |  |  |  | 2 | Nos. | each | 300 | 600
| 63mm dia |  |  |  |  | 1 | No. | each | 350 | 350
| 80 mm dia |  |  |  |  | 1 | No. | each | 550 | 550
| Sub Total of Part - I | [8 empty] | 0
Part - II
12 | Providing and laying High Density Polyethyene pipe (HDPE pipe) of 20 mm to 225 mm OD and pressure 6.0 Kg/cm2 and 10 Kg/cm2 sutable for water supply which is available in all standard, like ISI-4984/1995 and various grades like PE-80, PE-100 including required specials. Rates are inclusive of , all taxes and duties (Exise duty @12.50% &CST @2% against Form 'C'), labour cess, contractor profit and overhead charges all complete as per direction of Engineer-in-charge.
12A | HDPE pipe of materials grade PE100- PN10 (dia in mm)
| 110mm dia Pipe |  |  |  |  | 0 | M | P/M | 646.25 | 0
| 90mm dia Pipe |  |  |  |  | 150 | M | P/M | 437.96 | 65694
| 75mm dia Pipe |  |  |  |  | 500 | M | P/M | 306.31 | 153155
| 63mm dia Pipe |  |  |  |  | 550 | M | P/M | 218.62 | 120241
13B | HDPE pipe of materials grade PE100- PN8 (dia in mm)
| 50 mm dia Pipe |  |  |  |  | 450 | M | P/M | 116.25 | 52312.5
| 40mm dia Pipe |  |  |  |  | 350 | M | P/M | 76.53 | 26785.5
13C | Providing all materials labours tools, fittings , specials and tackles for fitting, jointing and connecting HDPE pipes. (5% of the cost of the HDPE pipe .) | [8 empty] | 20909.4
| Sub Total Of Part (II) | [8 empty] | 0
| Grand Total | [8 empty] | 1208330.7421
JE |  |  |  | AE |  |  |  |  | Executive Engineer
P. H. Division, Hajipur.

## Bajitpur Saidat 09B&13B (hidden)
Sub Estimate no. - 3C
Bajitpur Saidat Ward No. :-09B&13B
WATER SUPPLY DISTRIBUTION SYSTEM
S.N. | Particulars |  |  |  |  | Quantity |  | Unit | Rate | Amount
1/ 2.8 | Earthwork in excavation over areas (exceeding 30 cm in depth 1.5 in width as well as 10 sqm on plan) including disposal of excavated earth lead upto 50m and lift upto 1.5m, disposal earth to be levelled and neatly dressed.
| 110mm dia Pipe | 0 | 0.3 | 1.1 | = | 0 | [6 empty] | 152000
| 90mm dia Pipe | 100 | 0.3 | 1.1 | = | 33 | [6 empty] | 152000
| 75mm dia Pipe | 250 | 0.3 | 1.1 | = | 82.5
| 63mm dia Pipe | 250 | 0.3 | 1.1 | = | 82.5 | [6 empty] | 152000
| 50 mm dia Pipe | 200 | 0.3 | 1.1 | = | 66
| 40mm dia Pipe | 200 | 0.3 | 1.1 | = | 66
|  | 1000 |  |  |  | 330 | M3
| Add 5% extra for fittings = |  |  |  |  | 16.5 | M3
[6 empty] | 346.5 | M3 | P/M3 | 360.7 | 124982.55
2/ 2.26 | Filling available excavated earth (excluding rock) in trenches, plinth, sides of foundations etc. in layers not exceeding 20cm in depth, consolidating each deposited layer by ramming and watering, lead up to 50 m and lift upto 1.5 m. |  |  |  |  | 339.57 | M3 | P/M3 | 123.9 | 42072.723
3/ 15.2.1 | Demolishing cement concrete manually/by mechanical means including disposal of material within 50 metres lead as per direction of Engineer - in - charge. | [8 empty] | 13107.15
1:3:6 or richer mix
|  | 300 | 0.3 | 0.15 | = | 13.5 | M3 | P/M3 | 970.9
4/ 4.1.3 | Providing and laying in position cement concrete of specified grade excluding the cost of centering and shuttering all work upto plinth |  |  |  |  | 13.5 | M3 | P/M3 | 3998.1 | 53974.35 | 4969
1:2:4 (1 cement: 2 coarse sand : 4 graded stone aggregate 40mm nominal size)
5 | Carriage of the following materials from quarry to work site including loading, unloading and staking at work site as per specification & direction of E/I.
| Coarse Sand (44Km Pucca & 1Km Kaccha Carriage) |  |  |  |  | 6.21 | M3 | P/M3 | 1160.62 | 7207.4502
| Stone chips (195Km Pucca & 5Km unsurafced Carriage) |  |  |  |  | 12.42 | M3 | P/M3 | 4291.17 | 53296.3314
6A/ 18.12 | Providing and fixing G.I.Pipes complete with G.I. Fittings including trenching and refilling etc.
18.12.6 | 50mm dia G.I.Pipe from T/well to PVC Tank |  |  |  |  | 14 | M | P/M | 572.6 | 8016.4 |  |  |  | 611.3975
18.12.8 | 80mm dia G.I.Pipe from PVC Tank to Distribution main |  |  |  |  | 14 | M | P/M | 818.2 | 11454.8
18.12.7 | 65mm dia G.I.Pipe for wash out |  |  |  |  | 12 | M | P/M | 667.7 | 8012.4
7A/ 18.31.1.1 | P/F C.I sluice Valve (with Cap) complete with bolts,nuts,rubber insertions etc
6B/ | Providing and fixing brass gate valve with C.I. wheel of approved quality (screwed end).
| 80mm dia Pipe |  |  |  |  | 2 | Nos. | Each | 2227.6 | 4455.2
| 65mm dia Pipe |  |  |  |  | 1 | Nos. | Each | 1490.7 | 1490.7
| 50mm dia Pipe |  |  |  |  | 1 | Nos. | Each | 878.2 | 878.2
7/ 18.33 | Constructing masonry Chamber 60x60x75 cm inside, in brick work in cement mortar 1:4 (1 cement : 4 coarse sand) for sluice valve,with C.I. surface box 100mm top diameter, 160 mm bottom diameter and 180 mm deep ( inside) with chained lid and RCC top slab 1:2:4 mix (1 cement : 2 coarse sand : 4 graded stone aggregate 20mm nominal size ) , necessary excavation, foundation concrete 1:5:10(1 cement : 5 fine sand : 10 graded stone aggregate 40 mm nominalsize) and inside plastering with cement mortar 1:3 (1 cement : 3coarse sand) 12 mm thick, finished with a floating coat of neat cement complete as per standard specifications & direction of E/I. |  |  |  |  | 4 | Nos. | Each | 7210.6 | 28842.4
| Work for additional depth | [10 empty] | 4.9933
Brick work (1:4) in foundation
| 2 | 1.1 | 0.25 | 0.35 | 0.1925
| 2 | 0.6 | 0.25 | 0.35 | 0.105
6.1.12 |  |  |  |  | 0.2975 | 1.19 | M3 | P/M3 | 5017.9 | 5971.301
13.11.1 | Plaster (1:3)
| 8 | 1.1 |  | 0.35 | 3.08 | 12.32 | M2 | P/M2 | 164.3 | 2024.176
8 | Carriage 10% of item 9 | [8 empty] | 3683.7877
9A/ 18.48 | Providing and placing on terrace (at all floor levels) polyethylene water storage tank, ISI : 12701 marked, with cover and suitable locking arrangement and making necessary holes for inlet, outlet and overflow pipes but without fittings and the base support for tank. |  |  |  |  | 10000 | Ltrs. | P/Ltr. | 9.7 | 97000
9B | Providing and fixing MS clamp consisting of 32mm X 5mm thick two no. rings spaced suitably distance apart. | [7 empty] | LS | 3000
10A | Supplying all materials labours & fixing 50mm dia. G.I pipe for using as filling station etc. All as per direction of E/I
| 50mm dia. Pipe from distribution main |  |  |  |  | 3.5 | M | P/M | 572.6 | 2004.1
10B | Providing and fixing G.I fittings
| 80mmx80mmx50mm dia Tee |  |  |  |  | 1 | No | Each | 225 | 225
| 50mm dia bend |  |  |  |  | 3 | No | Each | 175 | 525
| Providing and fixing gun metal gate valve with C.I. wheel of approved quality (screwed end) :50mm nominal dia. |  |  |  |  | 1 | N | Each | 811.4 | 811.4
10C | Providing designation of 100 A brick Flat soling joints filled with local sand including cost of watering, taxes & royalty all complete as per specification & direction of E/I.
|  | 1 | 0.45 | 0.45 |  | 0.2025 | m2 | p/m2 | 283.3 | 57.3683
11 | Providing and fixing PTMT extension nipple for water tank pipe, fittings of approved quality and colour.
| 50mm dia |  |  |  |  | 2 | Nos. | each | 300 | 600
| 63mm dia |  |  |  |  | 1 | No. | each | 350 | 350
| 80 mm dia |  |  |  |  | 1 | No. | each | 550 | 550
| Sub Total of Part - I | [8 empty] | 0
Part - II
12 | Providing and laying High Density Polyethyene pipe (HDPE pipe) of 20 mm to 225 mm OD and pressure 6.0 Kg/cm2 and 10 Kg/cm2 sutable for water supply which is available in all standard, like ISI-4984/1995 and various grades like PE-80, PE-100 including required specials. Rates are inclusive of , all taxes and duties (Exise duty @12.50% &CST @2% against Form 'C'), labour cess, contractor profit and overhead charges all complete as per direction of Engineer-in-charge.
12A | HDPE pipe of materials grade PE100- PN10 (dia in mm)
| 110mm dia Pipe |  |  |  |  | 0 | M | P/M | 646.25 | 0
| 90mm dia Pipe |  |  |  |  | 100 | M | P/M | 437.96 | 43796
| 75mm dia Pipe |  |  |  |  | 250 | M | P/M | 306.31 | 76577.5
| 63mm dia Pipe |  |  |  |  | 250 | M | P/M | 218.62 | 54655
13B | HDPE pipe of materials grade PE100- PN8 (dia in mm)
| 50 mm dia Pipe |  |  |  |  | 200 | M | P/M | 116.25 | 23250
| 40mm dia Pipe |  |  |  |  | 200 | M | P/M | 76.53 | 15306
13C | Providing all materials labours tools, fittings , specials and tackles for fitting, jointing and connecting HDPE pipes. (5% of the cost of the HDPE pipe .) | [8 empty] | 10679.225
| Sub Total Of Part (II) | [8 empty] | 0
| Grand Total | [8 empty] | 698856.5125
JE |  |  |  | AE |  |  |  |  | Executive Engineer
P. H. Division, Hajipur.

## Khilwat 01B (hidden)
Sub Estimate no. - 3A
Khilwat WARD NO. :-01B
WATER SUPPLY DISTRIBUTION SYSTEM
S.N. | Particulars |  |  |  |  | Quantity |  | Unit | Rate | Amount
1/ 2.8 | Earthwork in excavation over areas (exceeding 30 cm in depth 1.5 in width as well as 10 sqm on plan) including disposal of excavated earth lead upto 50m and lift upto 1.5m, disposal earth to be levelled and neatly dressed.
| 110mm dia Pipe | 0 | 0.3 | 1.1 | = | 0 | [6 empty] | 152000
| 90mm dia Pipe | 150 | 0.3 | 1.1 | = | 49.5 | [6 empty] | 152000
| 75mm dia Pipe | 450 | 0.3 | 1.1 | = | 148.5
| 63mm dia Pipe | 550 | 0.3 | 1.1 | = | 181.5 | [6 empty] | 152000
| 50 mm dia Pipe | 350 | 0.3 | 1.1 | = | 115.5
| 40mm dia Pipe | 300 | 0.3 | 1.1 | = | 99
|  | 1800 |  |  |  | 594 | M3
| Add 5% extra for fittings = |  |  |  |  | 29.7 | M3
[6 empty] | 623.7 | M3 | P/M3 | 360.7 | 224968.59
2/ 2.26 | Filling available excavated earth (excluding rock) in trenches, plinth, sides of foundations etc. in layers not exceeding 20cm in depth, consolidating each deposited layer by ramming and watering, lead up to 50 m and lift upto 1.5 m. |  |  |  |  | 611.226 | M3 | P/M3 | 123.9 | 75730.9014
3/ 15.2.1 | Demolishing cement concrete manually/by mechanical means including disposal of material within 50 metres lead as per direction of Engineer - in - charge. | [8 empty] | 23592.87
1:3:6 or richer mix
|  | 540 | 0.3 | 0.15 | = | 24.3 | M3 | P/M3 | 970.9
4/ 4.1.3 | Providing and laying in position cement concrete of specified grade excluding the cost of centering and shuttering all work upto plinth |  |  |  |  | 24.3 | M3 | P/M3 | 3998.1 | 97153.83 | 4969
1:2:4 (1 cement: 2 coarse sand : 4 graded stone aggregate 40mm nominal size)
5 | Carriage of the following materials from quarry to work site including loading, unloading and staking at work site as per specification & direction of E/I.
| Coarse Sand (44Km Pucca & 1Km Kaccha Carriage) |  |  |  |  | 11.178 | M3 | P/M3 | 1160.62 | 12973.4104
| Stone chips (195Km Pucca & 5Km unsurafced Carriage) |  |  |  |  | 22.356 | M3 | P/M3 | 4291.17 | 95933.3965
6A/ 18.12 | Providing and fixing G.I.Pipes complete with G.I. Fittings including trenching and refilling etc.
18.12.6 | 50mm dia G.I.Pipe from T/well to PVC Tank |  |  |  |  | 14 | M | P/M | 572.6 | 8016.4 |  |  |  | 611.3975
18.12.8 | 80mm dia G.I.Pipe from PVC Tank to Distribution main |  |  |  |  | 14 | M | P/M | 818.2 | 11454.8
18.12.7 | 65mm dia G.I.Pipe for wash out |  |  |  |  | 12 | M | P/M | 667.7 | 8012.4
7A/ 18.31.1.1 | P/F C.I sluice Valve (with Cap) complete with bolts,nuts,rubber insertions etc
6B/ | Providing and fixing brass gate valve with C.I. wheel of approved quality (screwed end).
| 80mm dia Pipe |  |  |  |  | 2 | Nos. | Each | 2227.6 | 4455.2
| 65mm dia Pipe |  |  |  |  | 2 | Nos. | Each | 1490.7 | 2981.4
| 50mm dia Pipe |  |  |  |  | 1 | Nos. | Each | 878.2 | 878.2
7/ 18.33 | Constructing masonry Chamber 60x60x75 cm inside, in brick work in cement mortar 1:4 (1 cement : 4 coarse sand) for sluice valve,with C.I. surface box 100mm top diameter, 160 mm bottom diameter and 180 mm deep ( inside) with chained lid and RCC top slab 1:2:4 mix (1 cement : 2 coarse sand : 4 graded stone aggregate 20mm nominal size ) , necessary excavation, foundation concrete 1:5:10(1 cement : 5 fine sand : 10 graded stone aggregate 40 mm nominalsize) and inside plastering with cement mortar 1:3 (1 cement : 3coarse sand) 12 mm thick, finished with a floating coat of neat cement complete as per standard specifications & direction of E/I. |  |  |  |  | 5 | Nos. | Each | 7210.6 | 36053
| Work for additional depth | [10 empty] | 4.9933
Brick work (1:4) in foundation
| 2 | 1.1 | 0.25 | 0.35 | 0.1925
| 2 | 0.6 | 0.25 | 0.35 | 0.105
6.1.12 |  |  |  |  | 0.2975 | 1.4875 | M3 | P/M3 | 5017.9 | 7464.1262
13.11.1 | Plaster (1:3)
| 8 | 1.1 |  | 0.35 | 3.08 | 15.4 | M2 | P/M2 | 164.3 | 2530.22
8 | Carriage 10% of item 9 | [8 empty] | 4604.7346
9A/ 18.48 | Providing and placing on terrace (at all floor levels) polyethylene water storage tank, ISI : 12701 marked, with cover and suitable locking arrangement and making necessary holes for inlet, outlet and overflow pipes but without fittings and the base support for tank. |  |  |  |  | 10000 | Ltrs. | P/Ltr. | 9.7 | 97000
9B | Providing and fixing MS clamp consisting of 32mm X 5mm thick two no. rings spaced suitably distance apart. | [7 empty] | LS | 3000
10A | Supplying all materials labours & fixing 50mm dia. G.I pipe for using as filling station etc. All as per direction of E/I
| 50mm dia. Pipe from distribution main |  |  |  |  | 3.5 | M | P/M | 572.6 | 2004.1
10B | Providing and fixing G.I fittings
| 80mmx80mmx50mm dia Tee |  |  |  |  | 1 | No | Each | 225 | 225
| 50mm dia bend |  |  |  |  | 3 | No | Each | 175 | 525
| Providing and fixing gun metal gate valve with C.I. wheel of approved quality (screwed end) :50mm nominal dia. |  |  |  |  | 1 | N | Each | 811.4 | 811.4
10C | Providing designation of 100 A brick Flat soling joints filled with local sand including cost of watering, taxes & royalty all complete as per specification & direction of E/I.
|  | 1 | 0.45 | 0.45 |  | 0.2025 | m2 | p/m2 | 283.3 | 57.3683
11 | Providing and fixing PTMT extension nipple for water tank pipe, fittings of approved quality and colour.
| 50mm dia |  |  |  |  | 2 | Nos. | each | 300 | 600
| 63mm dia |  |  |  |  | 1 | No. | each | 350 | 350
| 80 mm dia |  |  |  |  | 1 | No. | each | 550 | 550
| Sub Total of Part - I | [8 empty] | 0
Part - II
12 | Providing and laying High Density Polyethyene pipe (HDPE pipe) of 20 mm to 225 mm OD and pressure 6.0 Kg/cm2 and 10 Kg/cm2 sutable for water supply which is available in all standard, like ISI-4984/1995 and various grades like PE-80, PE-100 including required specials. Rates are inclusive of , all taxes and duties (Exise duty @12.50% &CST @2% against Form 'C'), labour cess, contractor profit and overhead charges all complete as per direction of Engineer-in-charge.
12A | HDPE pipe of materials grade PE100- PN10 (dia in mm)
| 110mm dia Pipe |  |  |  |  | 0 | M | P/M | 646.25 | 0
| 90mm dia Pipe |  |  |  |  | 150 | M | P/M | 437.96 | 65694
| 75mm dia Pipe |  |  |  |  | 450 | M | P/M | 306.31 | 137839.5
| 63mm dia Pipe |  |  |  |  | 550 | M | P/M | 218.62 | 120241
13B | HDPE pipe of materials grade PE100- PN8 (dia in mm)
| 50 mm dia Pipe |  |  |  |  | 350 | M | P/M | 116.25 | 40687.5
| 40mm dia Pipe |  |  |  |  | 300 | M | P/M | 76.53 | 22959
13C | Providing all materials labours tools, fittings , specials and tackles for fitting, jointing and connecting HDPE pipes. (5% of the cost of the HDPE pipe .) | [8 empty] | 19371.05
| Sub Total Of Part (II) | [8 empty] | 0
| Grand Total | [8 empty] | 1128718.3974
JE |  |  |  | AE |  |  |  |  | Executive Engineer
P. H. Division, Hajipur.

## Khilwat 02B (hidden)
Sub Estimate no. - 3
Khilwat Ward No. :-02B
WATER SUPPLY DISTRIBUTION SYSTEM
S.N. | Particulars |  |  |  |  | Quantity |  | Unit | Rate | Amount
1/ 2.8 | Earthwork in excavation over areas (exceeding 30 cm in depth 1.5 in width as well as 10 sqm on plan) including disposal of excavated earth lead upto 50m and lift upto 1.5m, disposal earth to be levelled and neatly dressed.
| 110mm dia Pipe | 0 | 0.3 | 1.1 | = | 0 | [6 empty] | 152000
| 90mm dia Pipe | 100 | 0.3 | 1.1 | = | 33 | [6 empty] | 152000
| 75mm dia Pipe | 200 | 0.3 | 1.1 | = | 66
| 63mm dia Pipe | 300 | 0.3 | 1.1 | = | 99 | [6 empty] | 152000
| 50 mm dia Pipe | 300 | 0.3 | 1.1 | = | 99
| 40mm dia Pipe | 300 | 0.3 | 1.1 | = | 99
|  | 1200 |  |  |  | 396 | M3
| Add 5% extra for fittings = |  |  |  |  | 19.8 | M3
[6 empty] | 415.8 | M3 | P/M3 | 360.7 | 149979.06
2/ 2.26 | Filling available excavated earth (excluding rock) in trenches, plinth, sides of foundations etc. in layers not exceeding 20cm in depth, consolidating each deposited layer by ramming and watering, lead up to 50 m and lift upto 1.5 m. |  |  |  |  | 407.484 | M3 | P/M3 | 123.9 | 50487.2676
3/ 15.2.1 | Demolishing cement concrete manually/by mechanical means including disposal of material within 50 metres lead as per direction of Engineer - in - charge. | [8 empty] | 15728.58
1:3:6 or richer mix
|  | 360 | 0.3 | 0.15 | = | 16.2 | M3 | P/M3 | 970.9
4/ 4.1.3 | Providing and laying in position cement concrete of specified grade excluding the cost of centering and shuttering all work upto plinth |  |  |  |  | 16.2 | M3 | P/M3 | 3998.1 | 64769.22 | 4969
1:2:4 (1 cement: 2 coarse sand : 4 graded stone aggregate 40mm nominal size)
5 | Carriage of the following materials from quarry to work site including loading, unloading and staking at work site as per specification & direction of E/I.
| Coarse Sand (44Km Pucca & 1Km Kaccha Carriage) |  |  |  |  | 7.452 | M3 | P/M3 | 1160.62 | 8648.9402
| Stone chips (195Km Pucca & 5Km unsurafced Carriage) |  |  |  |  | 14.904 | M3 | P/M3 | 4291.17 | 63955.5977
6A/ 18.12 | Providing and fixing G.I.Pipes complete with G.I. Fittings including trenching and refilling etc.
18.12.6 | 50mm dia G.I.Pipe from T/well to PVC Tank |  |  |  |  | 14 | M | P/M | 572.6 | 8016.4 |  |  |  | 611.3975
18.12.8 | 80mm dia G.I.Pipe from PVC Tank to Distribution main |  |  |  |  | 14 | M | P/M | 818.2 | 11454.8
18.12.7 | 65mm dia G.I.Pipe for wash out |  |  |  |  | 12 | M | P/M | 667.7 | 8012.4
7A/ 18.31.1.1 | P/F C.I sluice Valve (with Cap) complete with bolts,nuts,rubber insertions etc
6B/ | Providing and fixing brass gate valve with C.I. wheel of approved quality (screwed end).
| 80mm dia Pipe |  |  |  |  | 2 | Nos. | Each | 2227.6 | 4455.2
| 65mm dia Pipe |  |  |  |  | 1 | Nos. | Each | 1490.7 | 1490.7
| 50mm dia Pipe |  |  |  |  | 1 | Nos. | Each | 878.2 | 878.2
7/ 18.33 | Constructing masonry Chamber 60x60x75 cm inside, in brick work in cement mortar 1:4 (1 cement : 4 coarse sand) for sluice valve,with C.I. surface box 100mm top diameter, 160 mm bottom diameter and 180 mm deep ( inside) with chained lid and RCC top slab 1:2:4 mix (1 cement : 2 coarse sand : 4 graded stone aggregate 20mm nominal size ) , necessary excavation, foundation concrete 1:5:10(1 cement : 5 fine sand : 10 graded stone aggregate 40 mm nominalsize) and inside plastering with cement mortar 1:3 (1 cement : 3coarse sand) 12 mm thick, finished with a floating coat of neat cement complete as per standard specifications & direction of E/I. |  |  |  |  | 4 | Nos. | Each | 7210.6 | 28842.4
| Work for additional depth | [10 empty] | 4.9933
Brick work (1:4) in foundation
| 2 | 1.1 | 0.25 | 0.35 | 0.1925
| 2 | 0.6 | 0.25 | 0.35 | 0.105
6.1.12 |  |  |  |  | 0.2975 | 1.19 | M3 | P/M3 | 5017.9 | 5971.301
13.11.1 | Plaster (1:3)
| 8 | 1.1 |  | 0.35 | 3.08 | 12.32 | M2 | P/M2 | 164.3 | 2024.176
8 | Carriage 10% of item 9 | [8 empty] | 3683.7877
9A/ 18.48 | Providing and placing on terrace (at all floor levels) polyethylene water storage tank, ISI : 12701 marked, with cover and suitable locking arrangement and making necessary holes for inlet, outlet and overflow pipes but without fittings and the base support for tank. |  |  |  |  | 10000 | Ltrs. | P/Ltr. | 9.7 | 97000
9B | Providing and fixing MS clamp consisting of 32mm X 5mm thick two no. rings spaced suitably distance apart. | [7 empty] | LS | 3000
10A | Supplying all materials labours & fixing 50mm dia. G.I pipe for using as filling station etc. All as per direction of E/I
| 50mm dia. Pipe from distribution main |  |  |  |  | 3.5 | M | P/M | 572.6 | 2004.1
10B | Providing and fixing G.I fittings
| 80mmx80mmx50mm dia Tee |  |  |  |  | 1 | No | Each | 225 | 225
| 50mm dia bend |  |  |  |  | 3 | No | Each | 175 | 525
| Providing and fixing gun metal gate valve with C.I. wheel of approved quality (screwed end) :50mm nominal dia. |  |  |  |  | 1 | N | Each | 811.4 | 811.4
10C | Providing designation of 100 A brick Flat soling joints filled with local sand including cost of watering, taxes & royalty all complete as per specification & direction of E/I.
|  | 1 | 0.45 | 0.45 |  | 0.2025 | m2 | p/m2 | 283.3 | 57.3683
11 | Providing and fixing PTMT extension nipple for water tank pipe, fittings of approved quality and colour.
| 50mm dia |  |  |  |  | 2 | Nos. | each | 300 | 600
| 63mm dia |  |  |  |  | 1 | No. | each | 350 | 350
| 80 mm dia |  |  |  |  | 1 | No. | each | 550 | 550
| Sub Total of Part - I | [8 empty] | 0
Part - II
12 | Providing and laying High Density Polyethyene pipe (HDPE pipe) of 20 mm to 225 mm OD and pressure 6.0 Kg/cm2 and 10 Kg/cm2 sutable for water supply which is available in all standard, like ISI-4984/1995 and various grades like PE-80, PE-100 including required specials. Rates are inclusive of , all taxes and duties (Exise duty @12.50% &CST @2% against Form 'C'), labour cess, contractor profit and overhead charges all complete as per direction of Engineer-in-charge.
12A | HDPE pipe of materials grade PE100- PN10 (dia in mm)
| 110mm dia Pipe |  |  |  |  | 0 | M | P/M | 646.25 | 0
| 90mm dia Pipe |  |  |  |  | 100 | M | P/M | 437.96 | 43796
| 75mm dia Pipe |  |  |  |  | 200 | M | P/M | 306.31 | 61262
| 63mm dia Pipe |  |  |  |  | 300 | M | P/M | 218.62 | 65586
13B | HDPE pipe of materials grade PE100- PN8 (dia in mm)
| 50 mm dia Pipe |  |  |  |  | 300 | M | P/M | 116.25 | 34875
| 40mm dia Pipe |  |  |  |  | 300 | M | P/M | 76.53 | 22959
13C | Providing all materials labours tools, fittings , specials and tackles for fitting, jointing and connecting HDPE pipes. (5% of the cost of the HDPE pipe .) | [8 empty] | 11423.9
| Sub Total Of Part (II) | [8 empty] | 0
| Grand Total | [8 empty] | 773422.7985
JE |  |  |  | AE |  |  |  |  | Executive Engineer
P. H. Division, Hajipur.

## Khilwat 09B (hidden)
Sub Estimate no. - 3B
Khilwat WARD NO. :-09B
WATER SUPPLY DISTRIBUTION SYSTEM
S.N. | Particulars |  |  |  |  | Quantity |  | Unit | Rate | Amount
1/ 2.8 | Earthwork in excavation over areas (exceeding 30 cm in depth 1.5 in width as well as 10 sqm on plan) including disposal of excavated earth lead upto 50m and lift upto 1.5m, disposal earth to be levelled and neatly dressed.
| 110mm dia Pipe | 0 | 0.3 | 1.1 | = | 0 | [6 empty] | 152000
| 90mm dia Pipe | 150 | 0.3 | 1.1 | = | 49.5 | [6 empty] | 152000
| 75mm dia Pipe | 350 | 0.3 | 1.1 | = | 115.5
| 63mm dia Pipe | 300 | 0.3 | 1.1 | = | 99 | [6 empty] | 152000
| 50 mm dia Pipe | 200 | 0.3 | 1.1 | = | 66
| 40mm dia Pipe | 200 | 0.3 | 1.1 | = | 66
|  | 1200 |  |  |  | 396 | M3
| Add 5% extra for fittings = |  |  |  |  | 19.8 | M3
[6 empty] | 415.8 | M3 | P/M3 | 360.7 | 149979.06
2/ 2.26 | Filling available excavated earth (excluding rock) in trenches, plinth, sides of foundations etc. in layers not exceeding 20cm in depth, consolidating each deposited layer by ramming and watering, lead up to 50 m and lift upto 1.5 m. |  |  |  |  | 407.484 | M3 | P/M3 | 123.9 | 50487.2676
3/ 15.2.1 | Demolishing cement concrete manually/by mechanical means including disposal of material within 50 metres lead as per direction of Engineer - in - charge. | [8 empty] | 15728.58
1:3:6 or richer mix
|  | 360 | 0.3 | 0.15 | = | 16.2 | M3 | P/M3 | 970.9
4/ 4.1.3 | Providing and laying in position cement concrete of specified grade excluding the cost of centering and shuttering all work upto plinth |  |  |  |  | 16.2 | M3 | P/M3 | 3998.1 | 64769.22 | 4969
1:2:4 (1 cement: 2 coarse sand : 4 graded stone aggregate 40mm nominal size)
5 | Carriage of the following materials from quarry to work site including loading, unloading and staking at work site as per specification & direction of E/I.
| Coarse Sand (44Km Pucca & 1Km Kaccha Carriage) |  |  |  |  | 7.452 | M3 | P/M3 | 1160.62 | 8648.9402
| Stone chips (195Km Pucca & 5Km unsurafced Carriage) |  |  |  |  | 14.904 | M3 | P/M3 | 4291.17 | 63955.5977
6A/ 18.12 | Providing and fixing G.I.Pipes complete with G.I. Fittings including trenching and refilling etc.
18.12.6 | 50mm dia G.I.Pipe from T/well to PVC Tank |  |  |  |  | 14 | M | P/M | 572.6 | 8016.4 |  |  |  | 611.3975
18.12.8 | 80mm dia G.I.Pipe from PVC Tank to Distribution main |  |  |  |  | 14 | M | P/M | 818.2 | 11454.8
18.12.7 | 65mm dia G.I.Pipe for wash out |  |  |  |  | 12 | M | P/M | 667.7 | 8012.4
7A/ 18.31.1.1 | P/F C.I sluice Valve (with Cap) complete with bolts,nuts,rubber insertions etc
6B/ | Providing and fixing brass gate valve with C.I. wheel of approved quality (screwed end).
| 80mm dia Pipe |  |  |  |  | 2 | Nos. | Each | 2227.6 | 4455.2
| 65mm dia Pipe |  |  |  |  | 1 | Nos. | Each | 1490.7 | 1490.7
| 50mm dia Pipe |  |  |  |  | 1 | Nos. | Each | 878.2 | 878.2
7/ 18.33 | Constructing masonry Chamber 60x60x75 cm inside, in brick work in cement mortar 1:4 (1 cement : 4 coarse sand) for sluice valve,with C.I. surface box 100mm top diameter, 160 mm bottom diameter and 180 mm deep ( inside) with chained lid and RCC top slab 1:2:4 mix (1 cement : 2 coarse sand : 4 graded stone aggregate 20mm nominal size ) , necessary excavation, foundation concrete 1:5:10(1 cement : 5 fine sand : 10 graded stone aggregate 40 mm nominalsize) and inside plastering with cement mortar 1:3 (1 cement : 3coarse sand) 12 mm thick, finished with a floating coat of neat cement complete as per standard specifications & direction of E/I. |  |  |  |  | 4 | Nos. | Each | 7210.6 | 28842.4
| Work for additional depth | [10 empty] | 4.9933
Brick work (1:4) in foundation
| 2 | 1.1 | 0.25 | 0.35 | 0.1925
| 2 | 0.6 | 0.25 | 0.35 | 0.105
6.1.12 |  |  |  |  | 0.2975 | 1.19 | M3 | P/M3 | 5017.9 | 5971.301
13.11.1 | Plaster (1:3)
| 8 | 1.1 |  | 0.35 | 3.08 | 12.32 | M2 | P/M2 | 164.3 | 2024.176
8 | Carriage 10% of item 9 | [8 empty] | 3683.7877
9A/ 18.48 | Providing and placing on terrace (at all floor levels) polyethylene water storage tank, ISI : 12701 marked, with cover and suitable locking arrangement and making necessary holes for inlet, outlet and overflow pipes but without fittings and the base support for tank. |  |  |  |  | 10000 | Ltrs. | P/Ltr. | 9.7 | 97000
9B | Providing and fixing MS clamp consisting of 32mm X 5mm thick two no. rings spaced suitably distance apart. | [7 empty] | LS | 3000
10A | Supplying all materials labours & fixing 50mm dia. G.I pipe for using as filling station etc. All as per direction of E/I
| 50mm dia. Pipe from distribution main |  |  |  |  | 3.5 | M | P/M | 572.6 | 2004.1
10B | Providing and fixing G.I fittings
| 80mmx80mmx50mm dia Tee |  |  |  |  | 1 | No | Each | 225 | 225
| 50mm dia bend |  |  |  |  | 3 | No | Each | 175 | 525
| Providing and fixing gun metal gate valve with C.I. wheel of approved quality (screwed end) :50mm nominal dia. |  |  |  |  | 1 | N | Each | 811.4 | 811.4
10C | Providing designation of 100 A brick Flat soling joints filled with local sand including cost of watering, taxes & royalty all complete as per specification & direction of E/I.
|  | 1 | 0.45 | 0.45 |  | 0.2025 | m2 | p/m2 | 283.3 | 57.3683
11 | Providing and fixing PTMT extension nipple for water tank pipe, fittings of approved quality and colour.
| 50mm dia |  |  |  |  | 2 | Nos. | each | 300 | 600
| 63mm dia |  |  |  |  | 1 | No. | each | 350 | 350
| 80 mm dia |  |  |  |  | 1 | No. | each | 550 | 550
| Sub Total of Part - I | [8 empty] | 0
Part - II
12 | Providing and laying High Density Polyethyene pipe (HDPE pipe) of 20 mm to 225 mm OD and pressure 6.0 Kg/cm2 and 10 Kg/cm2 sutable for water supply which is available in all standard, like ISI-4984/1995 and various grades like PE-80, PE-100 including required specials. Rates are inclusive of , all taxes and duties (Exise duty @12.50% &CST @2% against Form 'C'), labour cess, contractor profit and overhead charges all complete as per direction of Engineer-in-charge.
12A | HDPE pipe of materials grade PE100- PN10 (dia in mm)
| 110mm dia Pipe |  |  |  |  | 0 | M | P/M | 646.25 | 0
| 90mm dia Pipe |  |  |  |  | 150 | M | P/M | 437.96 | 65694
| 75mm dia Pipe |  |  |  |  | 350 | M | P/M | 306.31 | 107208.5
| 63mm dia Pipe |  |  |  |  | 300 | M | P/M | 218.62 | 65586
13B | HDPE pipe of materials grade PE100- PN8 (dia in mm)
| 50 mm dia Pipe |  |  |  |  | 200 | M | P/M | 116.25 | 23250
| 40mm dia Pipe |  |  |  |  | 200 | M | P/M | 76.53 | 15306
13C | Providing all materials labours tools, fittings , specials and tackles for fitting, jointing and connecting HDPE pipes. (5% of the cost of the HDPE pipe .) | [8 empty] | 13852.225
| Sub Total Of Part (II) | [8 empty] | 0
| Grand Total | [8 empty] | 824417.6235
JE |  |  |  | AE |  |  |  |  | Executive Engineer
P. H. Division, Hajipur.

## Khilwat 12B&13B (hidden)
Sub Estimate no. - 3C
Khilwat WARD NO. :-12B&13B
WATER SUPPLY DISTRIBUTION SYSTEM
S.N. | Particulars |  |  |  |  | Quantity |  | Unit | Rate | Amount
1/ 2.8 | Earthwork in excavation over areas (exceeding 30 cm in depth 1.5 in width as well as 10 sqm on plan) including disposal of excavated earth lead upto 50m and lift upto 1.5m, disposal earth to be levelled and neatly dressed.
| 110mm dia Pipe | 0 | 0.3 | 1.1 | = | 0 | [6 empty] | 152000
| 90mm dia Pipe | 150 | 0.3 | 1.1 | = | 49.5 | [6 empty] | 152000
| 75mm dia Pipe | 350 | 0.3 | 1.1 | = | 115.5
| 63mm dia Pipe | 300 | 0.3 | 1.1 | = | 99 | [6 empty] | 152000
| 50 mm dia Pipe | 200 | 0.3 | 1.1 | = | 66
| 40mm dia Pipe | 200 | 0.3 | 1.1 | = | 66
|  | 1200 |  |  |  | 396 | M3
| Add 5% extra for fittings = |  |  |  |  | 19.8 | M3
[6 empty] | 415.8 | M3 | P/M3 | 360.7 | 149979.06
2/ 2.26 | Filling available excavated earth (excluding rock) in trenches, plinth, sides of foundations etc. in layers not exceeding 20cm in depth, consolidating each deposited layer by ramming and watering, lead up to 50 m and lift upto 1.5 m. |  |  |  |  | 407.484 | M3 | P/M3 | 123.9 | 50487.2676
3/ 15.2.1 | Demolishing cement concrete manually/by mechanical means including disposal of material within 50 metres lead as per direction of Engineer - in - charge. | [8 empty] | 15728.58
1:3:6 or richer mix
|  | 360 | 0.3 | 0.15 | = | 16.2 | M3 | P/M3 | 970.9
4/ 4.1.3 | Providing and laying in position cement concrete of specified grade excluding the cost of centering and shuttering all work upto plinth |  |  |  |  | 16.2 | M3 | P/M3 | 3998.1 | 64769.22 | 4969
1:2:4 (1 cement: 2 coarse sand : 4 graded stone aggregate 40mm nominal size)
5 | Carriage of the following materials from quarry to work site including loading, unloading and staking at work site as per specification & direction of E/I.
| Coarse Sand (44Km Pucca & 1Km Kaccha Carriage) |  |  |  |  | 7.452 | M3 | P/M3 | 1160.62 | 8648.9402
| Stone chips (195Km Pucca & 5Km unsurafced Carriage) |  |  |  |  | 14.904 | M3 | P/M3 | 4291.17 | 63955.5977
6A/ 18.12 | Providing and fixing G.I.Pipes complete with G.I. Fittings including trenching and refilling etc.
18.12.6 | 50mm dia G.I.Pipe from T/well to PVC Tank |  |  |  |  | 14 | M | P/M | 572.6 | 8016.4 |  |  |  | 611.3975
18.12.8 | 80mm dia G.I.Pipe from PVC Tank to Distribution main |  |  |  |  | 14 | M | P/M | 818.2 | 11454.8
18.12.7 | 65mm dia G.I.Pipe for wash out |  |  |  |  | 12 | M | P/M | 667.7 | 8012.4
7A/ 18.31.1.1 | P/F C.I sluice Valve (with Cap) complete with bolts,nuts,rubber insertions etc
6B/ | Providing and fixing brass gate valve with C.I. wheel of approved quality (screwed end).
| 80mm dia Pipe |  |  |  |  | 2 | Nos. | Each | 2227.6 | 4455.2
| 65mm dia Pipe |  |  |  |  | 1 | Nos. | Each | 1490.7 | 1490.7
| 50mm dia Pipe |  |  |  |  | 1 | Nos. | Each | 878.2 | 878.2
7/ 18.33 | Constructing masonry Chamber 60x60x75 cm inside, in brick work in cement mortar 1:4 (1 cement : 4 coarse sand) for sluice valve,with C.I. surface box 100mm top diameter, 160 mm bottom diameter and 180 mm deep ( inside) with chained lid and RCC top slab 1:2:4 mix (1 cement : 2 coarse sand : 4 graded stone aggregate 20mm nominal size ) , necessary excavation, foundation concrete 1:5:10(1 cement : 5 fine sand : 10 graded stone aggregate 40 mm nominalsize) and inside plastering with cement mortar 1:3 (1 cement : 3coarse sand) 12 mm thick, finished with a floating coat of neat cement complete as per standard specifications & direction of E/I. |  |  |  |  | 4 | Nos. | Each | 7210.6 | 28842.4
| Work for additional depth | [10 empty] | 4.9933
Brick work (1:4) in foundation
| 2 | 1.1 | 0.25 | 0.35 | 0.1925
| 2 | 0.6 | 0.25 | 0.35 | 0.105
6.1.12 |  |  |  |  | 0.2975 | 1.19 | M3 | P/M3 | 5017.9 | 5971.301
13.11.1 | Plaster (1:3)
| 8 | 1.1 |  | 0.35 | 3.08 | 12.32 | M2 | P/M2 | 164.3 | 2024.176
8 | Carriage 10% of item 9 | [8 empty] | 3683.7877
9A/ 18.48 | Providing and placing on terrace (at all floor levels) polyethylene water storage tank, ISI : 12701 marked, with cover and suitable locking arrangement and making necessary holes for inlet, outlet and overflow pipes but without fittings and the base support for tank. |  |  |  |  | 10000 | Ltrs. | P/Ltr. | 9.7 | 97000
9B | Providing and fixing MS clamp consisting of 32mm X 5mm thick two no. rings spaced suitably distance apart. | [7 empty] | LS | 3000
10A | Supplying all materials labours & fixing 50mm dia. G.I pipe for using as filling station etc. All as per direction of E/I
| 50mm dia. Pipe from distribution main |  |  |  |  | 3.5 | M | P/M | 572.6 | 2004.1
10B | Providing and fixing G.I fittings
| 80mmx80mmx50mm dia Tee |  |  |  |  | 1 | No | Each | 225 | 225
| 50mm dia bend |  |  |  |  | 3 | No | Each | 175 | 525
| Providing and fixing gun metal gate valve with C.I. wheel of approved quality (screwed end) :50mm nominal dia. |  |  |  |  | 1 | N | Each | 811.4 | 811.4
10C | Providing designation of 100 A brick Flat soling joints filled with local sand including cost of watering, taxes & royalty all complete as per specification & direction of E/I.
|  | 1 | 0.45 | 0.45 |  | 0.2025 | m2 | p/m2 | 283.3 | 57.3683
11 | Providing and fixing PTMT extension nipple for water tank pipe, fittings of approved quality and colour.
| 50mm dia |  |  |  |  | 2 | Nos. | each | 300 | 600
| 63mm dia |  |  |  |  | 1 | No. | each | 350 | 350
| 80 mm dia |  |  |  |  | 1 | No. | each | 550 | 550
| Sub Total of Part - I | [8 empty] | 0
Part - II
12 | Providing and laying High Density Polyethyene pipe (HDPE pipe) of 20 mm to 225 mm OD and pressure 6.0 Kg/cm2 and 10 Kg/cm2 sutable for water supply which is available in all standard, like ISI-4984/1995 and various grades like PE-80, PE-100 including required specials. Rates are inclusive of , all taxes and duties (Exise duty @12.50% &CST @2% against Form 'C'), labour cess, contractor profit and overhead charges all complete as per direction of Engineer-in-charge.
12A | HDPE pipe of materials grade PE100- PN10 (dia in mm)
| 110mm dia Pipe |  |  |  |  | 0 | M | P/M | 646.25 | 0
| 90mm dia Pipe |  |  |  |  | 150 | M | P/M | 437.96 | 65694
| 75mm dia Pipe |  |  |  |  | 350 | M | P/M | 306.31 | 107208.5
| 63mm dia Pipe |  |  |  |  | 300 | M | P/M | 218.62 | 65586
13B | HDPE pipe of materials grade PE100- PN8 (dia in mm)
| 50 mm dia Pipe |  |  |  |  | 200 | M | P/M | 116.25 | 23250
| 40mm dia Pipe |  |  |  |  | 200 | M | P/M | 76.53 | 15306
13C | Providing all materials labours tools, fittings , specials and tackles for fitting, jointing and connecting HDPE pipes. (5% of the cost of the HDPE pipe .) | [8 empty] | 13852.225
| Sub Total Of Part (II) | [8 empty] | 0
| Grand Total | [8 empty] | 824417.6235
JE |  |  |  | AE |  |  |  |  | Executive Engineer
P. H. Division, Hajipur.

## Kutubpur 12B&11B (hidden)
Sub Estimate no. - 3A
Kutubpur Ward no. :- 12B&11B
WATER SUPPLY DISTRIBUTION SYSTEM
S.N. | Particulars |  |  |  |  | Quantity |  | Unit | Rate | Amount
1/ 2.8 | Earthwork in excavation over areas (exceeding 30 cm in depth 1.5 in width as well as 10 sqm on plan) including disposal of excavated earth lead upto 50m and lift upto 1.5m, disposal earth to be levelled and neatly dressed.
| 110mm dia Pipe | 0 | 0.3 | 1.1 | = | 0 | [6 empty] | 152000
| 90mm dia Pipe | 250 | 0.3 | 1.1 | = | 82.5 | [6 empty] | 152000
| 75mm dia Pipe | 700 | 0.3 | 1.1 | = | 231
| 63mm dia Pipe | 800 | 0.3 | 1.1 | = | 264 | [6 empty] | 152000
| 50 mm dia Pipe | 400 | 0.3 | 1.1 | = | 132
| 40mm dia Pipe | 400 | 0.3 | 1.1 | = | 132
|  | 2550 |  |  |  | 841.5 | M3
| Add 5% extra for fittings = |  |  |  |  | 42.075 | M3
[6 empty] | 883.575 | M3 | P/M3 | 360.7 | 318705.5025
2/ 2.26 | Filling available excavated earth (excluding rock) in trenches, plinth, sides of foundations etc. in layers not exceeding 20cm in depth, consolidating each deposited layer by ramming and watering, lead up to 50 m and lift upto 1.5 m. |  |  |  |  | 865.9035 | M3 | P/M3 | 123.9 | 107285.4437
3/ 15.2.1 | Demolishing cement concrete manually/by mechanical means including disposal of material within 50 metres lead as per direction of Engineer - in - charge. | [8 empty] | 33423.2325
1:3:6 or richer mix
|  | 765 | 0.3 | 0.15 | = | 34.425 | M3 | P/M3 | 970.9
4/ 4.1.3 | Providing and laying in position cement concrete of specified grade excluding the cost of centering and shuttering all work upto plinth |  |  |  |  | 34.425 | M3 | P/M3 | 3998.1 | 137634.5925 | 4969
1:2:4 (1 cement: 2 coarse sand : 4 graded stone aggregate 40mm nominal size)
5 | Carriage of the following materials from quarry to work site including loading, unloading and staking at work site as per specification & direction of E/I.
| Coarse Sand (44Km Pucca & 1Km Kaccha Carriage) |  |  |  |  | 15.8355 | M3 | P/M3 | 1160.62 | 18378.998
| Stone chips (195Km Pucca & 5Km unsurafced Carriage) |  |  |  |  | 31.671 | M3 | P/M3 | 4291.17 | 135905.6451
6A/ 18.12 | Providing and fixing G.I.Pipes complete with G.I. Fittings including trenching and refilling etc.
18.12.6 | 50mm dia G.I.Pipe from T/well to PVC Tank |  |  |  |  | 14 | M | P/M | 572.6 | 8016.4 |  |  |  | 611.3975
18.12.8 | 80mm dia G.I.Pipe from PVC Tank to Distribution main |  |  |  |  | 14 | M | P/M | 818.2 | 11454.8
18.12.7 | 65mm dia G.I.Pipe for wash out |  |  |  |  | 12 | M | P/M | 667.7 | 8012.4
7A/ 18.31.1.1 | P/F C.I sluice Valve (with Cap) complete with bolts,nuts,rubber insertions etc
6B/ | Providing and fixing brass gate valve with C.I. wheel of approved quality (screwed end).
| 80mm dia Pipe |  |  |  |  | 2 | Nos. | Each | 2227.6 | 4455.2
| 65mm dia Pipe |  |  |  |  | 1 | Nos. | Each | 1490.7 | 1490.7
| 50mm dia Pipe |  |  |  |  | 1 | Nos. | Each | 878.2 | 878.2
7/ 18.33 | Constructing masonry Chamber 60x60x75 cm inside, in brick work in cement mortar 1:4 (1 cement : 4 coarse sand) for sluice valve,with C.I. surface box 100mm top diameter, 160 mm bottom diameter and 180 mm deep ( inside) with chained lid and RCC top slab 1:2:4 mix (1 cement : 2 coarse sand : 4 graded stone aggregate 20mm nominal size ) , necessary excavation, foundation concrete 1:5:10(1 cement : 5 fine sand : 10 graded stone aggregate 40 mm nominalsize) and inside plastering with cement mortar 1:3 (1 cement : 3coarse sand) 12 mm thick, finished with a floating coat of neat cement complete as per standard specifications & direction of E/I. |  |  |  |  | 4 | Nos. | Each | 7210.6 | 28842.4
| Work for additional depth | [10 empty] | 4.9933
Brick work (1:4) in foundation
| 2 | 1.1 | 0.25 | 0.35 | 0.1925
| 2 | 0.6 | 0.25 | 0.35 | 0.105
6.1.12 |  |  |  |  | 0.2975 | 1.19 | M3 | P/M3 | 5017.9 | 5971.301
13.11.1 | Plaster (1:3)
| 8 | 1.1 |  | 0.35 | 3.08 | 12.32 | M2 | P/M2 | 164.3 | 2024.176
8 | Carriage 10% of item 9 | [8 empty] | 3683.7877
9A/ 18.48 | Providing and placing on terrace (at all floor levels) polyethylene water storage tank, ISI : 12701 marked, with cover and suitable locking arrangement and making necessary holes for inlet, outlet and overflow pipes but without fittings and the base support for tank. |  |  |  |  | 10000 | Ltrs. | P/Ltr. | 9.7 | 97000
9B | Providing and fixing MS clamp consisting of 32mm X 5mm thick two no. rings spaced suitably distance apart. | [7 empty] | LS | 3000
10A | Supplying all materials labours & fixing 50mm dia. G.I pipe for using as filling station etc. All as per direction of E/I
| 50mm dia. Pipe from distribution main |  |  |  |  | 3.5 | M | P/M | 572.6 | 2004.1
10B | Providing and fixing G.I fittings
| 80mmx80mmx50mm dia Tee |  |  |  |  | 1 | No | Each | 225 | 225
| 50mm dia bend |  |  |  |  | 3 | No | Each | 175 | 525
| Providing and fixing gun metal gate valve with C.I. wheel of approved quality (screwed end) :50mm nominal dia. |  |  |  |  | 1 | N | Each | 811.4 | 811.4
10C | Providing designation of 100 A brick Flat soling joints filled with local sand including cost of watering, taxes & royalty all complete as per specification & direction of E/I.
|  | 1 | 0.45 | 0.45 |  | 0.2025 | m2 | p/m2 | 283.3 | 57.3683
11 | Providing and fixing PTMT extension nipple for water tank pipe, fittings of approved quality and colour.
| 50mm dia |  |  |  |  | 2 | Nos. | each | 300 | 600
| 63mm dia |  |  |  |  | 1 | No. | each | 350 | 350
| 80 mm dia |  |  |  |  | 1 | No. | each | 550 | 550
| Sub Total of Part - I | [8 empty] | 0
Part - II
12 | Providing and laying High Density Polyethyene pipe (HDPE pipe) of 20 mm to 225 mm OD and pressure 6.0 Kg/cm2 and 10 Kg/cm2 sutable for water supply which is available in all standard, like ISI-4984/1995 and various grades like PE-80, PE-100 including required specials. Rates are inclusive of , all taxes and duties (Exise duty @12.50% &CST @2% against Form 'C'), labour cess, contractor profit and overhead charges all complete as per direction of Engineer-in-charge.
12A | HDPE pipe of materials grade PE100- PN10 (dia in mm)
| 110mm dia Pipe |  |  |  |  | 0 | M | P/M | 646.25 | 0
| 90mm dia Pipe |  |  |  |  | 250 | M | P/M | 437.96 | 109490
| 75mm dia Pipe |  |  |  |  | 700 | M | P/M | 306.31 | 214417
| 63mm dia Pipe |  |  |  |  | 800 | M | P/M | 218.62 | 174896
13B | HDPE pipe of materials grade PE100- PN8 (dia in mm)
| 50 mm dia Pipe |  |  |  |  | 400 | M | P/M | 116.25 | 46500
| 40mm dia Pipe |  |  |  |  | 400 | M | P/M | 76.53 | 30612
13C | Providing all materials labours tools, fittings , specials and tackles for fitting, jointing and connecting HDPE pipes. (5% of the cost of the HDPE pipe .) | [8 empty] | 28795.75
| Sub Total Of Part (II) | [8 empty] | 0
| Grand Total | [8 empty] | 1535996.3972
JE |  |  |  | AE |  |  |  |  | Executive Engineer
P. H. Division, Hajipur.

## Kutubpur 13B (hidden)
Sub Estimate no. - 3B
Kutubpur Ward no. :- 13B
WATER SUPPLY DISTRIBUTION SYSTEM
S.N. | Particulars |  |  |  |  | Quantity |  | Unit | Rate | Amount
1/ 2.8 | Earthwork in excavation over areas (exceeding 30 cm in depth 1.5 in width as well as 10 sqm on plan) including disposal of excavated earth lead upto 50m and lift upto 1.5m, disposal earth to be levelled and neatly dressed.
| 110mm dia Pipe | 0 | 0.3 | 1.1 | = | 0 | [6 empty] | 152000
| 90mm dia Pipe | 150 | 0.3 | 1.1 | = | 49.5 | [6 empty] | 152000
| 75mm dia Pipe | 450 | 0.3 | 1.1 | = | 148.5
| 63mm dia Pipe | 400 | 0.3 | 1.1 | = | 132 | [6 empty] | 152000
| 50 mm dia Pipe | 300 | 0.3 | 1.1 | = | 99
| 40mm dia Pipe | 300 | 0.3 | 1.1 | = | 99
|  | 1600 |  |  |  | 528 | M3
| Add 5% extra for fittings = |  |  |  |  | 26.4 | M3
[6 empty] | 554.4 | M3 | P/M3 | 360.7 | 199972.08
2/ 2.26 | Filling available excavated earth (excluding rock) in trenches, plinth, sides of foundations etc. in layers not exceeding 20cm in depth, consolidating each deposited layer by ramming and watering, lead up to 50 m and lift upto 1.5 m. |  |  |  |  | 543.312 | M3 | P/M3 | 123.9 | 67316.3568
3/ 15.2.1 | Demolishing cement concrete manually/by mechanical means including disposal of material within 50 metres lead as per direction of Engineer - in - charge. | [8 empty] | 20971.44
1:3:6 or richer mix
|  | 480 | 0.3 | 0.15 | = | 21.6 | M3 | P/M3 | 970.9
4/ 4.1.3 | Providing and laying in position cement concrete of specified grade excluding the cost of centering and shuttering all work upto plinth |  |  |  |  | 21.6 | M3 | P/M3 | 3998.1 | 86358.96 | 4969
1:2:4 (1 cement: 2 coarse sand : 4 graded stone aggregate 40mm nominal size)
5 | Carriage of the following materials from quarry to work site including loading, unloading and staking at work site as per specification & direction of E/I.
| Coarse Sand (44Km Pucca & 1Km Kaccha Carriage) |  |  |  |  | 9.936 | M3 | P/M3 | 1160.62 | 11531.9203
| Stone chips (195Km Pucca & 5Km unsurafced Carriage) |  |  |  |  | 19.872 | M3 | P/M3 | 4291.17 | 85274.1302
6A/ 18.12 | Providing and fixing G.I.Pipes complete with G.I. Fittings including trenching and refilling etc.
18.12.6 | 50mm dia G.I.Pipe from T/well to PVC Tank |  |  |  |  | 14 | M | P/M | 572.6 | 8016.4 |  |  |  | 611.3975
18.12.8 | 80mm dia G.I.Pipe from PVC Tank to Distribution main |  |  |  |  | 14 | M | P/M | 818.2 | 11454.8
18.12.7 | 65mm dia G.I.Pipe for wash out |  |  |  |  | 12 | M | P/M | 667.7 | 8012.4
7A/ 18.31.1.1 | P/F C.I sluice Valve (with Cap) complete with bolts,nuts,rubber insertions etc
6B/ | Providing and fixing brass gate valve with C.I. wheel of approved quality (screwed end).
| 80mm dia Pipe |  |  |  |  | 2 | Nos. | Each | 2227.6 | 4455.2
| 65mm dia Pipe |  |  |  |  | 1 | Nos. | Each | 1490.7 | 1490.7
| 50mm dia Pipe |  |  |  |  | 1 | Nos. | Each | 878.2 | 878.2
7/ 18.33 | Constructing masonry Chamber 60x60x75 cm inside, in brick work in cement mortar 1:4 (1 cement : 4 coarse sand) for sluice valve,with C.I. surface box 100mm top diameter, 160 mm bottom diameter and 180 mm deep ( inside) with chained lid and RCC top slab 1:2:4 mix (1 cement : 2 coarse sand : 4 graded stone aggregate 20mm nominal size ) , necessary excavation, foundation concrete 1:5:10(1 cement : 5 fine sand : 10 graded stone aggregate 40 mm nominalsize) and inside plastering with cement mortar 1:3 (1 cement : 3coarse sand) 12 mm thick, finished with a floating coat of neat cement complete as per standard specifications & direction of E/I. |  |  |  |  | 4 | Nos. | Each | 7210.6 | 28842.4
| Work for additional depth | [10 empty] | 4.9933
Brick work (1:4) in foundation
| 2 | 1.1 | 0.25 | 0.35 | 0.1925
| 2 | 0.6 | 0.25 | 0.35 | 0.105
6.1.12 |  |  |  |  | 0.2975 | 1.19 | M3 | P/M3 | 5017.9 | 5971.301
13.11.1 | Plaster (1:3)
| 8 | 1.1 |  | 0.35 | 3.08 | 12.32 | M2 | P/M2 | 164.3 | 2024.176
8 | Carriage 10% of item 9 | [8 empty] | 3683.7877
9A/ 18.48 | Providing and placing on terrace (at all floor levels) polyethylene water storage tank, ISI : 12701 marked, with cover and suitable locking arrangement and making necessary holes for inlet, outlet and overflow pipes but without fittings and the base support for tank. |  |  |  |  | 10000 | Ltrs. | P/Ltr. | 9.7 | 97000
9B | Providing and fixing MS clamp consisting of 32mm X 5mm thick two no. rings spaced suitably distance apart. | [7 empty] | LS | 3000
10A | Supplying all materials labours & fixing 50mm dia. G.I pipe for using as filling station etc. All as per direction of E/I
| 50mm dia. Pipe from distribution main |  |  |  |  | 3.5 | M | P/M | 572.6 | 2004.1
10B | Providing and fixing G.I fittings
| 80mmx80mmx50mm dia Tee |  |  |  |  | 1 | No | Each | 225 | 225
| 50mm dia bend |  |  |  |  | 3 | No | Each | 175 | 525
| Providing and fixing gun metal gate valve with C.I. wheel of approved quality (screwed end) :50mm nominal dia. |  |  |  |  | 1 | N | Each | 811.4 | 811.4
10C | Providing designation of 100 A brick Flat soling joints filled with local sand including cost of watering, taxes & royalty all complete as per specification & direction of E/I.
|  | 1 | 0.45 | 0.45 |  | 0.2025 | m2 | p/m2 | 283.3 | 57.3683
11 | Providing and fixing PTMT extension nipple for water tank pipe, fittings of approved quality and colour.
| 50mm dia |  |  |  |  | 2 | Nos. | each | 300 | 600
| 63mm dia |  |  |  |  | 1 | No. | each | 350 | 350
| 80 mm dia |  |  |  |  | 1 | No. | each | 550 | 550
| Sub Total of Part - I | [8 empty] | 0
Part - II
12 | Providing and laying High Density Polyethyene pipe (HDPE pipe) of 20 mm to 225 mm OD and pressure 6.0 Kg/cm2 and 10 Kg/cm2 sutable for water supply which is available in all standard, like ISI-4984/1995 and various grades like PE-80, PE-100 including required specials. Rates are inclusive of , all taxes and duties (Exise duty @12.50% &CST @2% against Form 'C'), labour cess, contractor profit and overhead charges all complete as per direction of Engineer-in-charge.
12A | HDPE pipe of materials grade PE100- PN10 (dia in mm)
| 110mm dia Pipe |  |  |  |  | 0 | M | P/M | 646.25 | 0
| 90mm dia Pipe |  |  |  |  | 150 | M | P/M | 437.96 | 65694
| 75mm dia Pipe |  |  |  |  | 450 | M | P/M | 306.31 | 137839.5
| 63mm dia Pipe |  |  |  |  | 400 | M | P/M | 218.62 | 87448
13B | HDPE pipe of materials grade PE100- PN8 (dia in mm)
| 50 mm dia Pipe |  |  |  |  | 300 | M | P/M | 116.25 | 34875
| 40mm dia Pipe |  |  |  |  | 300 | M | P/M | 76.53 | 22959
13C | Providing all materials labours tools, fittings , specials and tackles for fitting, jointing and connecting HDPE pipes. (5% of the cost of the HDPE pipe .) | [8 empty] | 17440.775
| Sub Total Of Part (II) | [8 empty] | 0
| Grand Total | [8 empty] | 1017633.3953
JE |  |  |  | AE |  |  |  |  | Executive Engineer
P. H. Division, Hajipur.

## Mail Pakri 14B&7B (hidden)
Sub Estimate no. - 3A
Mail Pakri Ward no. :- 14B&7B
WATER SUPPLY DISTRIBUTION SYSTEM
S.N. | Particulars |  |  |  |  | Quantity |  | Unit | Rate | Amount
1/ 2.8 | Earthwork in excavation over areas (exceeding 30 cm in depth 1.5 in width as well as 10 sqm on plan) including disposal of excavated earth lead upto 50m and lift upto 1.5m, disposal earth to be levelled and neatly dressed.
| 110mm dia Pipe | 0 | 0.3 | 1.1 | = | 0 | [6 empty] | 152000
| 90mm dia Pipe | 150 | 0.3 | 1.1 | = | 49.5 | [6 empty] | 152000
| 75mm dia Pipe | 450 | 0.3 | 1.1 | = | 148.5
| 63mm dia Pipe | 550 | 0.3 | 1.1 | = | 181.5 | [6 empty] | 152000
| 50 mm dia Pipe | 350 | 0.3 | 1.1 | = | 115.5
| 40mm dia Pipe | 300 | 0.3 | 1.1 | = | 99
|  | 1800 |  |  |  | 594 | M3
| Add 5% extra for fittings = |  |  |  |  | 29.7 | M3
[6 empty] | 623.7 | M3 | P/M3 | 360.7 | 224968.59
2/ 2.26 | Filling available excavated earth (excluding rock) in trenches, plinth, sides of foundations etc. in layers not exceeding 20cm in depth, consolidating each deposited layer by ramming and watering, lead up to 50 m and lift upto 1.5 m. |  |  |  |  | 611.226 | M3 | P/M3 | 123.9 | 75730.9014
3/ 15.2.1 | Demolishing cement concrete manually/by mechanical means including disposal of material within 50 metres lead as per direction of Engineer - in - charge. | [8 empty] | 23592.87
1:3:6 or richer mix
|  | 540 | 0.3 | 0.15 | = | 24.3 | M3 | P/M3 | 970.9
4/ 4.1.3 | Providing and laying in position cement concrete of specified grade excluding the cost of centering and shuttering all work upto plinth |  |  |  |  | 24.3 | M3 | P/M3 | 3998.1 | 97153.83 | 4969
1:2:4 (1 cement: 2 coarse sand : 4 graded stone aggregate 40mm nominal size)
5 | Carriage of the following materials from quarry to work site including loading, unloading and staking at work site as per specification & direction of E/I.
| Coarse Sand (44Km Pucca & 1Km Kaccha Carriage) |  |  |  |  | 11.178 | M3 | P/M3 | 1160.62 | 12973.4104
| Stone chips (195Km Pucca & 5Km unsurafced Carriage) |  |  |  |  | 22.356 | M3 | P/M3 | 4291.17 | 95933.3965
6A/ 18.12 | Providing and fixing G.I.Pipes complete with G.I. Fittings including trenching and refilling etc.
18.12.6 | 50mm dia G.I.Pipe from T/well to PVC Tank |  |  |  |  | 14 | M | P/M | 572.6 | 8016.4 |  |  |  | 611.3975
18.12.8 | 80mm dia G.I.Pipe from PVC Tank to Distribution main |  |  |  |  | 14 | M | P/M | 818.2 | 11454.8
18.12.7 | 65mm dia G.I.Pipe for wash out |  |  |  |  | 12 | M | P/M | 667.7 | 8012.4
7A/ 18.31.1.1 | P/F C.I sluice Valve (with Cap) complete with bolts,nuts,rubber insertions etc
6B/ | Providing and fixing brass gate valve with C.I. wheel of approved quality (screwed end).
| 80mm dia Pipe |  |  |  |  | 2 | Nos. | Each | 2227.6 | 4455.2
| 65mm dia Pipe |  |  |  |  | 1 | Nos. | Each | 1490.7 | 1490.7
| 50mm dia Pipe |  |  |  |  | 1 | Nos. | Each | 878.2 | 878.2
7/ 18.33 | Constructing masonry Chamber 60x60x75 cm inside, in brick work in cement mortar 1:4 (1 cement : 4 coarse sand) for sluice valve,with C.I. surface box 100mm top diameter, 160 mm bottom diameter and 180 mm deep ( inside) with chained lid and RCC top slab 1:2:4 mix (1 cement : 2 coarse sand : 4 graded stone aggregate 20mm nominal size ) , necessary excavation, foundation concrete 1:5:10(1 cement : 5 fine sand : 10 graded stone aggregate 40 mm nominalsize) and inside plastering with cement mortar 1:3 (1 cement : 3coarse sand) 12 mm thick, finished with a floating coat of neat cement complete as per standard specifications & direction of E/I. |  |  |  |  | 4 | Nos. | Each | 7210.6 | 28842.4
| Work for additional depth | [10 empty] | 4.9933
Brick work (1:4) in foundation
| 2 | 1.1 | 0.25 | 0.35 | 0.1925
| 2 | 0.6 | 0.25 | 0.35 | 0.105
6.1.12 |  |  |  |  | 0.2975 | 1.19 | M3 | P/M3 | 5017.9 | 5971.301
13.11.1 | Plaster (1:3)
| 8 | 1.1 |  | 0.35 | 3.08 | 12.32 | M2 | P/M2 | 164.3 | 2024.176
8 | Carriage 10% of item 9 | [8 empty] | 3683.7877
9A/ 18.48 | Providing and placing on terrace (at all floor levels) polyethylene water storage tank, ISI : 12701 marked, with cover and suitable locking arrangement and making necessary holes for inlet, outlet and overflow pipes but without fittings and the base support for tank. |  |  |  |  | 10000 | Ltrs. | P/Ltr. | 9.7 | 97000
9B | Providing and fixing MS clamp consisting of 32mm X 5mm thick two no. rings spaced suitably distance apart. | [7 empty] | LS | 3000
10A | Supplying all materials labours & fixing 50mm dia. G.I pipe for using as filling station etc. All as per direction of E/I
| 50mm dia. Pipe from distribution main |  |  |  |  | 3.5 | M | P/M | 572.6 | 2004.1
10B | Providing and fixing G.I fittings
| 80mmx80mmx50mm dia Tee |  |  |  |  | 1 | No | Each | 225 | 225
| 50mm dia bend |  |  |  |  | 3 | No | Each | 175 | 525
| Providing and fixing gun metal gate valve with C.I. wheel of approved quality (screwed end) :50mm nominal dia. |  |  |  |  | 1 | N | Each | 811.4 | 811.4
10C | Providing designation of 100 A brick Flat soling joints filled with local sand including cost of watering, taxes & royalty all complete as per specification & direction of E/I.
|  | 1 | 0.45 | 0.45 |  | 0.2025 | m2 | p/m2 | 283.3 | 57.3683
11 | Providing and fixing PTMT extension nipple for water tank pipe, fittings of approved quality and colour.
| 50mm dia |  |  |  |  | 2 | Nos. | each | 300 | 600
| 63mm dia |  |  |  |  | 1 | No. | each | 350 | 350
| 80 mm dia |  |  |  |  | 1 | No. | each | 550 | 550
| Sub Total of Part - I | [8 empty] | 0
Part - II
12 | Providing and laying High Density Polyethyene pipe (HDPE pipe) of 20 mm to 225 mm OD and pressure 6.0 Kg/cm2 and 10 Kg/cm2 sutable for water supply which is available in all standard, like ISI-4984/1995 and various grades like PE-80, PE-100 including required specials. Rates are inclusive of , all taxes and duties (Exise duty @12.50% &CST @2% against Form 'C'), labour cess, contractor profit and overhead charges all complete as per direction of Engineer-in-charge.
12A | HDPE pipe of materials grade PE100- PN10 (dia in mm)
| 110mm dia Pipe |  |  |  |  | 0 | M | P/M | 646.25 | 0
| 90mm dia Pipe |  |  |  |  | 150 | M | P/M | 437.96 | 65694
| 75mm dia Pipe |  |  |  |  | 450 | M | P/M | 306.31 | 137839.5
| 63mm dia Pipe |  |  |  |  | 550 | M | P/M | 218.62 | 120241
13B | HDPE pipe of materials grade PE100- PN8 (dia in mm)
| 50 mm dia Pipe |  |  |  |  | 350 | M | P/M | 116.25 | 40687.5
| 40mm dia Pipe |  |  |  |  | 300 | M | P/M | 76.53 | 22959
13C | Providing all materials labours tools, fittings , specials and tackles for fitting, jointing and connecting HDPE pipes. (5% of the cost of the HDPE pipe .) | [8 empty] | 19371.05
| Sub Total Of Part (II) | [8 empty] | 0
| Grand Total | [8 empty] | 1117097.2812
JE |  |  |  | AE |  |  |  |  | Executive Engineer
P. H. Division, Hajipur.

## Mail Pakri 10B&11B (hidden)
Sub Estimate no. - 3B
Mail Pakri Ward no. :- 10B&11B
WATER SUPPLY DISTRIBUTION SYSTEM
S.N. | Particulars |  |  |  |  | Quantity |  | Unit | Rate | Amount
1/ 2.8 | Earthwork in excavation over areas (exceeding 30 cm in depth 1.5 in width as well as 10 sqm on plan) including disposal of excavated earth lead upto 50m and lift upto 1.5m, disposal earth to be levelled and neatly dressed.
| 110mm dia Pipe | 0 | 0.3 | 1.1 | = | 0 | [6 empty] | 152000
| 90mm dia Pipe | 150 | 0.3 | 1.1 | = | 49.5 | [6 empty] | 152000
| 75mm dia Pipe | 450 | 0.3 | 1.1 | = | 148.5
| 63mm dia Pipe | 550 | 0.3 | 1.1 | = | 181.5 | [6 empty] | 152000
| 50 mm dia Pipe | 350 | 0.3 | 1.1 | = | 115.5
| 40mm dia Pipe | 300 | 0.3 | 1.1 | = | 99
|  | 1800 |  |  |  | 594 | M3
| Add 5% extra for fittings = |  |  |  |  | 29.7 | M3
[6 empty] | 623.7 | M3 | P/M3 | 360.7 | 224968.59
2/ 2.26 | Filling available excavated earth (excluding rock) in trenches, plinth, sides of foundations etc. in layers not exceeding 20cm in depth, consolidating each deposited layer by ramming and watering, lead up to 50 m and lift upto 1.5 m. |  |  |  |  | 611.226 | M3 | P/M3 | 123.9 | 75730.9014
3/ 15.2.1 | Demolishing cement concrete manually/by mechanical means including disposal of material within 50 metres lead as per direction of Engineer - in - charge. | [8 empty] | 23592.87
1:3:6 or richer mix
|  | 540 | 0.3 | 0.15 | = | 24.3 | M3 | P/M3 | 970.9
4/ 4.1.3 | Providing and laying in position cement concrete of specified grade excluding the cost of centering and shuttering all work upto plinth |  |  |  |  | 24.3 | M3 | P/M3 | 3998.1 | 97153.83 | 4969
1:2:4 (1 cement: 2 coarse sand : 4 graded stone aggregate 40mm nominal size)
5 | Carriage of the following materials from quarry to work site including loading, unloading and staking at work site as per specification & direction of E/I.
| Coarse Sand (44Km Pucca & 1Km Kaccha Carriage) |  |  |  |  | 11.178 | M3 | P/M3 | 1160.62 | 12973.4104
| Stone chips (195Km Pucca & 5Km unsurafced Carriage) |  |  |  |  | 22.356 | M3 | P/M3 | 4291.17 | 95933.3965
6A/ 18.12 | Providing and fixing G.I.Pipes complete with G.I. Fittings including trenching and refilling etc.
18.12.6 | 50mm dia G.I.Pipe from T/well to PVC Tank |  |  |  |  | 14 | M | P/M | 572.6 | 8016.4 |  |  |  | 611.3975
18.12.8 | 80mm dia G.I.Pipe from PVC Tank to Distribution main |  |  |  |  | 14 | M | P/M | 818.2 | 11454.8
18.12.7 | 65mm dia G.I.Pipe for wash out |  |  |  |  | 12 | M | P/M | 667.7 | 8012.4
7A/ 18.31.1.1 | P/F C.I sluice Valve (with Cap) complete with bolts,nuts,rubber insertions etc
6B/ | Providing and fixing brass gate valve with C.I. wheel of approved quality (screwed end).
| 80mm dia Pipe |  |  |  |  | 2 | Nos. | Each | 2227.6 | 4455.2
| 65mm dia Pipe |  |  |  |  | 1 | Nos. | Each | 1490.7 | 1490.7
| 50mm dia Pipe |  |  |  |  | 1 | Nos. | Each | 878.2 | 878.2
7/ 18.33 | Constructing masonry Chamber 60x60x75 cm inside, in brick work in cement mortar 1:4 (1 cement : 4 coarse sand) for sluice valve,with C.I. surface box 100mm top diameter, 160 mm bottom diameter and 180 mm deep ( inside) with chained lid and RCC top slab 1:2:4 mix (1 cement : 2 coarse sand : 4 graded stone aggregate 20mm nominal size ) , necessary excavation, foundation concrete 1:5:10(1 cement : 5 fine sand : 10 graded stone aggregate 40 mm nominalsize) and inside plastering with cement mortar 1:3 (1 cement : 3coarse sand) 12 mm thick, finished with a floating coat of neat cement complete as per standard specifications & direction of E/I. |  |  |  |  | 4 | Nos. | Each | 7210.6 | 28842.4
| Work for additional depth | [10 empty] | 4.9933
Brick work (1:4) in foundation
| 2 | 1.1 | 0.25 | 0.35 | 0.1925
| 2 | 0.6 | 0.25 | 0.35 | 0.105
6.1.12 |  |  |  |  | 0.2975 | 1.19 | M3 | P/M3 | 5017.9 | 5971.301
13.11.1 | Plaster (1:3)
| 8 | 1.1 |  | 0.35 | 3.08 | 12.32 | M2 | P/M2 | 164.3 | 2024.176
8 | Carriage 10% of item 9 | [8 empty] | 3683.7877
9A/ 18.48 | Providing and placing on terrace (at all floor levels) polyethylene water storage tank, ISI : 12701 marked, with cover and suitable locking arrangement and making necessary holes for inlet, outlet and overflow pipes but without fittings and the base support for tank. |  |  |  |  | 10000 | Ltrs. | P/Ltr. | 9.7 | 97000
9B | Providing and fixing MS clamp consisting of 32mm X 5mm thick two no. rings spaced suitably distance apart. | [7 empty] | LS | 3000
10A | Supplying all materials labours & fixing 50mm dia. G.I pipe for using as filling station etc. All as per direction of E/I
| 50mm dia. Pipe from distribution main |  |  |  |  | 3.5 | M | P/M | 572.6 | 2004.1
10B | Providing and fixing G.I fittings
| 80mmx80mmx50mm dia Tee |  |  |  |  | 1 | No | Each | 225 | 225
| 50mm dia bend |  |  |  |  | 3 | No | Each | 175 | 525
| Providing and fixing gun metal gate valve with C.I. wheel of approved quality (screwed end) :50mm nominal dia. |  |  |  |  | 1 | N | Each | 811.4 | 811.4
10C | Providing designation of 100 A brick Flat soling joints filled with local sand including cost of watering, taxes & royalty all complete as per specification & direction of E/I.
|  | 1 | 0.45 | 0.45 |  | 0.2025 | m2 | p/m2 | 283.3 | 57.3683
11 | Providing and fixing PTMT extension nipple for water tank pipe, fittings of approved quality and colour.
| 50mm dia |  |  |  |  | 2 | Nos. | each | 300 | 600
| 63mm dia |  |  |  |  | 1 | No. | each | 350 | 350
| 80 mm dia |  |  |  |  | 1 | No. | each | 550 | 550
| Sub Total of Part - I | [8 empty] | 0
Part - II
12 | Providing and laying High Density Polyethyene pipe (HDPE pipe) of 20 mm to 225 mm OD and pressure 6.0 Kg/cm2 and 10 Kg/cm2 sutable for water supply which is available in all standard, like ISI-4984/1995 and various grades like PE-80, PE-100 including required specials. Rates are inclusive of , all taxes and duties (Exise duty @12.50% &CST @2% against Form 'C'), labour cess, contractor profit and overhead charges all complete as per direction of Engineer-in-charge.
12A | HDPE pipe of materials grade PE100- PN10 (dia in mm)
| 110mm dia Pipe |  |  |  |  | 0 | M | P/M | 646.25 | 0
| 90mm dia Pipe |  |  |  |  | 150 | M | P/M | 437.96 | 65694
| 75mm dia Pipe |  |  |  |  | 450 | M | P/M | 306.31 | 137839.5
| 63mm dia Pipe |  |  |  |  | 550 | M | P/M | 218.62 | 120241
13B | HDPE pipe of materials grade PE100- PN8 (dia in mm)
| 50 mm dia Pipe |  |  |  |  | 350 | M | P/M | 116.25 | 40687.5
| 40mm dia Pipe |  |  |  |  | 300 | M | P/M | 76.53 | 22959
13C | Providing all materials labours tools, fittings , specials and tackles for fitting, jointing and connecting HDPE pipes. (5% of the cost of the HDPE pipe .) | [8 empty] | 19371.05
| Sub Total Of Part (II) | [8 empty] | 0
| Grand Total | [8 empty] | 1117097.2812
JE |  |  |  | AE |  |  |  |  | Executive Engineer
P. H. Division, Hajipur.

## Nawanagar 03B (hidden)
Sub Estimate no. - 3
BIDUPUR NAWANAGAR 03B YADAV TOLA
WATER SUPPLY DISTRIBUTION SYSTEM
S.N. | Particulars |  |  |  |  | Quantity |  | Unit | Rate | Amount
1/ 2.8 | Earthwork in excavation over areas (exceeding 30 cm in depth 1.5 in width as well as 10 sqm on plan) including disposal of excavated earth lead upto 50m and lift upto 1.5m, disposal earth to be levelled and neatly dressed.
| 110mm dia Pipe | 0 | 0.3 | 1.1 | = | 0 | [6 empty] | 152000
| 90mm dia Pipe | 100 | 0.3 | 1.1 | = | 33 | [6 empty] | 152000
| 75mm dia Pipe | 200 | 0.3 | 1.1 | = | 66
| 63mm dia Pipe | 250 | 0.3 | 1.1 | = | 82.5 | [6 empty] | 152000
| 50 mm dia Pipe | 250 | 0.3 | 1.1 | = | 82.5
| 40mm dia Pipe | 200 | 0.3 | 1.1 | = | 66
|  | 1000 |  |  |  | 330 | M3
| Add 5% extra for fittings = |  |  |  |  | 16.5 | M3
[6 empty] | 346.5 | M3 | P/M3 | 360.7 | 124982.55
2/ 2.26 | Filling available excavated earth (excluding rock) in trenches, plinth, sides of foundations etc. in layers not exceeding 20cm in depth, consolidating each deposited layer by ramming and watering, lead up to 50 m and lift upto 1.5 m. |  |  |  |  | 339.57 | M3 | P/M3 | 123.9 | 42072.723
3/ 15.2.1 | Demolishing cement concrete manually/by mechanical means including disposal of material within 50 metres lead as per direction of Engineer - in - charge. | [8 empty] | 13107.15
1:3:6 or richer mix
|  | 300 | 0.3 | 0.15 | = | 13.5 | M3 | P/M3 | 970.9
4/ 4.1.3 | Providing and laying in position cement concrete of specified grade excluding the cost of centering and shuttering all work upto plinth |  |  |  |  | 13.5 | M3 | P/M3 | 3998.1 | 53974.35 | 4969
1:2:4 (1 cement: 2 coarse sand : 4 graded stone aggregate 40mm nominal size)
5 | Carriage of the following materials from quarry to work site including loading, unloading and staking at work site as per specification & direction of E/I.
| Coarse Sand (44Km Pucca & 1Km Kaccha Carriage) |  |  |  |  | 6.21 | M3 | P/M3 | 1160.62 | 7207.4502
| Stone chips (195Km Pucca & 5Km unsurafced Carriage) |  |  |  |  | 12.42 | M3 | P/M3 | 4291.17 | 53296.3314
6A/ 18.12 | Providing and fixing G.I.Pipes complete with G.I. Fittings including trenching and refilling etc.
18.12.6 | 50mm dia G.I.Pipe from T/well to PVC Tank |  |  |  |  | 14 | M | P/M | 572.6 | 8016.4 |  |  |  | 611.3975
18.12.8 | 80mm dia G.I.Pipe from PVC Tank to Distribution main |  |  |  |  | 14 | M | P/M | 818.2 | 11454.8
18.12.7 | 65mm dia G.I.Pipe for wash out |  |  |  |  | 12 | M | P/M | 667.7 | 8012.4
7A/ 18.31.1.1 | P/F C.I sluice Valve (with Cap) complete with bolts,nuts,rubber insertions etc
6B/ | Providing and fixing brass gate valve with C.I. wheel of approved quality (screwed end).
| 80mm dia Pipe |  |  |  |  | 2 | Nos. | Each | 2227.6 | 4455.2
| 65mm dia Pipe |  |  |  |  | 2 | Nos. | Each | 1490.7 | 2981.4
| 50mm dia Pipe |  |  |  |  | 2 | Nos. | Each | 878.2 | 1756.4
7/ 18.33 | Constructing masonry Chamber 60x60x75 cm inside, in brick work in cement mortar 1:4 (1 cement : 4 coarse sand) for sluice valve,with C.I. surface box 100mm top diameter, 160 mm bottom diameter and 180 mm deep ( inside) with chained lid and RCC top slab 1:2:4 mix (1 cement : 2 coarse sand : 4 graded stone aggregate 20mm nominal size ) , necessary excavation, foundation concrete 1:5:10(1 cement : 5 fine sand : 10 graded stone aggregate 40 mm nominalsize) and inside plastering with cement mortar 1:3 (1 cement : 3coarse sand) 12 mm thick, finished with a floating coat of neat cement complete as per standard specifications & direction of E/I. |  |  |  |  | 6 | Nos. | Each | 7210.6 | 43263.6
| Work for additional depth | [10 empty] | 4.9933
Brick work (1:4) in foundation
| 2 | 1.1 | 0.25 | 0.35 | 0.1925
| 2 | 0.6 | 0.25 | 0.35 | 0.105
6.1.12 |  |  |  |  | 0.2975 | 1.785 | M3 | P/M3 | 5017.9 | 8956.9515
13.11.1 | Plaster (1:3)
| 8 | 1.1 |  | 0.35 | 3.08 | 18.48 | M2 | P/M2 | 164.3 | 3036.264
8 | Carriage 10% of item 9 | [8 empty] | 5525.6816
9A/ 18.48 | Providing and placing on terrace (at all floor levels) polyethylene water storage tank, ISI : 12701 marked, with cover and suitable locking arrangement and making necessary holes for inlet, outlet and overflow pipes but without fittings and the base support for tank. |  |  |  |  | 10000 | Ltrs. | P/Ltr. | 9.7 | 97000
9B | Providing and fixing MS clamp consisting of 32mm X 5mm thick two no. rings spaced suitably distance apart. | [7 empty] | LS | 3000
10A | Supplying all materials labours & fixing 50mm dia. G.I pipe for using as filling station etc. All as per direction of E/I
| 50mm dia. Pipe from distribution main |  |  |  |  | 3.5 | M | P/M | 572.6 | 2004.1
10B | Providing and fixing G.I fittings
| 80mmx80mmx50mm dia Tee |  |  |  |  | 1 | No | Each | 225 | 225
| 50mm dia bend |  |  |  |  | 3 | No | Each | 175 | 525
| Providing and fixing gun metal gate valve with C.I. wheel of approved quality (screwed end) :50mm nominal dia. |  |  |  |  | 1 | N | Each | 811.4 | 811.4
10C | Providing designation of 100 A brick Flat soling joints filled with local sand including cost of watering, taxes & royalty all complete as per specification & direction of E/I.
|  | 1 | 0.45 | 0.45 |  | 0.2025 | m2 | p/m2 | 283.3 | 57.3683
11 | Providing and fixing PTMT extension nipple for water tank pipe, fittings of approved quality and colour.
| 50mm dia |  |  |  |  | 2 | Nos. | each | 300 | 600
| 63mm dia |  |  |  |  | 1 | No. | each | 350 | 350
| 80 mm dia |  |  |  |  | 1 | No. | each | 550 | 550
| Sub Total of Part - I | [8 empty] | 0
Part - II
12 | Providing and laying High Density Polyethyene pipe (HDPE pipe) of 20 mm to 225 mm OD and pressure 6.0 Kg/cm2 and 10 Kg/cm2 sutable for water supply which is available in all standard, like ISI-4984/1995 and various grades like PE-80, PE-100 including required specials. Rates are inclusive of , all taxes and duties (Exise duty @12.50% &CST @2% against Form 'C'), labour cess, contractor profit and overhead charges all complete as per direction of Engineer-in-charge.
12A | HDPE pipe of materials grade PE100- PN10 (dia in mm)
| 110mm dia Pipe |  |  |  |  | 0 | M | P/M | 646.25 | 0
| 90mm dia Pipe |  |  |  |  | 100 | M | P/M | 437.96 | 43796
| 75mm dia Pipe |  |  |  |  | 200 | M | P/M | 306.31 | 61262
| 63mm dia Pipe |  |  |  |  | 250 | M | P/M | 218.62 | 54655
13B | HDPE pipe of materials grade PE100- PN8 (dia in mm)
| 50 mm dia Pipe |  |  |  |  | 250 | M | P/M | 116.25 | 29062.5
| 40mm dia Pipe |  |  |  |  | 200 | M | P/M | 76.53 | 15306
13C | Providing all materials labours tools, fittings , specials and tackles for fitting, jointing and connecting HDPE pipes. (5% of the cost of the HDPE pipe .) | [8 empty] | 10204.075
| Sub Total Of Part (II) | [8 empty] | 0
| Grand Total | [8 empty] | 711508.0949
Executive Engineer
P. H. Division, Hajipur.

## Rahimapur 9B&8B (hidden)
Sub Estimate no. - 3A
Rahimapur WARD NO. :-09B&08B
WATER SUPPLY DISTRIBUTION SYSTEM
S.N. | Particulars |  |  |  |  | Quantity |  | Unit | Rate | Amount
1/ 2.8 | Earthwork in excavation over areas (exceeding 30 cm in depth 1.5 in width as well as 10 sqm on plan) including disposal of excavated earth lead upto 50m and lift upto 1.5m, disposal earth to be levelled and neatly dressed.
| 110mm dia Pipe | 0 | 0.3 | 1.1 | = | 0 | [6 empty] | 152000
| 90mm dia Pipe | 150 | 0.3 | 1.1 | = | 49.5 | [6 empty] | 152000
| 75mm dia Pipe | 300 | 0.3 | 1.1 | = | 99
| 63mm dia Pipe | 350 | 0.3 | 1.1 | = | 115.5 | [6 empty] | 152000
| 50 mm dia Pipe | 350 | 0.3 | 1.1 | = | 115.5
| 40mm dia Pipe | 300 | 0.3 | 1.1 | = | 99
|  | 1450 |  |  |  | 478.5 | M3
| Add 5% extra for fittings = |  |  |  |  | 23.925 | M3
[6 empty] | 502.425 | M3 | P/M3 | 360.7 | 181224.6975
2/ 2.26 | Filling available excavated earth (excluding rock) in trenches, plinth, sides of foundations etc. in layers not exceeding 20cm in depth, consolidating each deposited layer by ramming and watering, lead up to 50 m and lift upto 1.5 m. |  |  |  |  | 492.3765 | M3 | P/M3 | 123.9 | 61005.4484
3/ 15.2.1 | Demolishing cement concrete manually/by mechanical means including disposal of material within 50 metres lead as per direction of Engineer - in - charge. | [8 empty] | 19005.3675
1:3:6 or richer mix
|  | 435 | 0.3 | 0.15 | = | 19.575 | M3 | P/M3 | 970.9
4/ 4.1.3 | Providing and laying in position cement concrete of specified grade excluding the cost of centering and shuttering all work upto plinth |  |  |  |  | 19.575 | M3 | P/M3 | 3998.1 | 78262.8075 | 4969
1:2:4 (1 cement: 2 coarse sand : 4 graded stone aggregate 40mm nominal size)
5 | Carriage of the following materials from quarry to work site including loading, unloading and staking at work site as per specification & direction of E/I.
| Coarse Sand (44Km Pucca & 1Km Kaccha Carriage) |  |  |  |  | 9.0045 | M3 | P/M3 | 1160.62 | 10450.8028
| Stone chips (195Km Pucca & 5Km unsurafced Carriage) |  |  |  |  | 18.009 | M3 | P/M3 | 4291.17 | 77279.6805
6A/ 18.12 | Providing and fixing G.I.Pipes complete with G.I. Fittings including trenching and refilling etc.
18.12.6 | 50mm dia G.I.Pipe from T/well to PVC Tank |  |  |  |  | 14 | M | P/M | 572.6 | 8016.4 |  |  |  | 611.3975
18.12.8 | 80mm dia G.I.Pipe from PVC Tank to Distribution main |  |  |  |  | 14 | M | P/M | 818.2 | 11454.8
18.12.7 | 65mm dia G.I.Pipe for wash out |  |  |  |  | 12 | M | P/M | 667.7 | 8012.4
7A/ 18.31.1.1 | P/F C.I sluice Valve (with Cap) complete with bolts,nuts,rubber insertions etc
6B/ | Providing and fixing brass gate valve with C.I. wheel of approved quality (screwed end).
| 80mm dia Pipe |  |  |  |  | 2 | Nos. | Each | 2227.6 | 4455.2
| 65mm dia Pipe |  |  |  |  | 2 | Nos. | Each | 1490.7 | 2981.4
| 50mm dia Pipe |  |  |  |  | 1 | Nos. | Each | 878.2 | 878.2
7/ 18.33 | Constructing masonry Chamber 60x60x75 cm inside, in brick work in cement mortar 1:4 (1 cement : 4 coarse sand) for sluice valve,with C.I. surface box 100mm top diameter, 160 mm bottom diameter and 180 mm deep ( inside) with chained lid and RCC top slab 1:2:4 mix (1 cement : 2 coarse sand : 4 graded stone aggregate 20mm nominal size ) , necessary excavation, foundation concrete 1:5:10(1 cement : 5 fine sand : 10 graded stone aggregate 40 mm nominalsize) and inside plastering with cement mortar 1:3 (1 cement : 3coarse sand) 12 mm thick, finished with a floating coat of neat cement complete as per standard specifications & direction of E/I. |  |  |  |  | 5 | Nos. | Each | 7210.6 | 36053
| Work for additional depth | [10 empty] | 4.9933
Brick work (1:4) in foundation
| 2 | 1.1 | 0.25 | 0.35 | 0.1925
| 2 | 0.6 | 0.25 | 0.35 | 0.105
6.1.12 |  |  |  |  | 0.2975 | 1.4875 | M3 | P/M3 | 5017.9 | 7464.1262
13.11.1 | Plaster (1:3)
| 8 | 1.1 |  | 0.35 | 3.08 | 15.4 | M2 | P/M2 | 164.3 | 2530.22
8 | Carriage 10% of item 9 | [8 empty] | 4604.7346
9A/ 18.48 | Providing and placing on terrace (at all floor levels) polyethylene water storage tank, ISI : 12701 marked, with cover and suitable locking arrangement and making necessary holes for inlet, outlet and overflow pipes but without fittings and the base support for tank. |  |  |  |  | 10000 | Ltrs. | P/Ltr. | 9.7 | 97000
9B | Providing and fixing MS clamp consisting of 32mm X 5mm thick two no. rings spaced suitably distance apart. | [7 empty] | LS | 3000
10A | Supplying all materials labours & fixing 50mm dia. G.I pipe for using as filling station etc. All as per direction of E/I
| 50mm dia. Pipe from distribution main |  |  |  |  | 3.5 | M | P/M | 572.6 | 2004.1
10B | Providing and fixing G.I fittings
| 80mmx80mmx50mm dia Tee |  |  |  |  | 1 | No | Each | 225 | 225
| 50mm dia bend |  |  |  |  | 3 | No | Each | 175 | 525
| Providing and fixing gun metal gate valve with C.I. wheel of approved quality (screwed end) :50mm nominal dia. |  |  |  |  | 1 | N | Each | 811.4 | 811.4
10C | Providing designation of 100 A brick Flat soling joints filled with local sand including cost of watering, taxes & royalty all complete as per specification & direction of E/I.
|  | 1 | 0.45 | 0.45 |  | 0.2025 | m2 | p/m2 | 283.3 | 57.3683
11 | Providing and fixing PTMT extension nipple for water tank pipe, fittings of approved quality and colour.
| 50mm dia |  |  |  |  | 2 | Nos. | each | 300 | 600
| 63mm dia |  |  |  |  | 1 | No. | each | 350 | 350
| 80 mm dia |  |  |  |  | 1 | No. | each | 550 | 550
| Sub Total of Part - I | [8 empty] | 0
Part - II
12 | Providing and laying High Density Polyethyene pipe (HDPE pipe) of 20 mm to 225 mm OD and pressure 6.0 Kg/cm2 and 10 Kg/cm2 sutable for water supply which is available in all standard, like ISI-4984/1995 and various grades like PE-80, PE-100 including required specials. Rates are inclusive of , all taxes and duties (Exise duty @12.50% &CST @2% against Form 'C'), labour cess, contractor profit and overhead charges all complete as per direction of Engineer-in-charge.
12A | HDPE pipe of materials grade PE100- PN10 (dia in mm)
| 110mm dia Pipe |  |  |  |  | 0 | M | P/M | 646.25 | 0
| 90mm dia Pipe |  |  |  |  | 150 | M | P/M | 437.96 | 65694
| 75mm dia Pipe |  |  |  |  | 300 | M | P/M | 306.31 | 91893
| 63mm dia Pipe |  |  |  |  | 350 | M | P/M | 218.62 | 76517
13B | HDPE pipe of materials grade PE100- PN8 (dia in mm)
| 50 mm dia Pipe |  |  |  |  | 350 | M | P/M | 116.25 | 40687.5
| 40mm dia Pipe |  |  |  |  | 300 | M | P/M | 76.53 | 22959
13C | Providing all materials labours tools, fittings , specials and tackles for fitting, jointing and connecting HDPE pipes. (5% of the cost of the HDPE pipe .) | [8 empty] | 14887.525
| Sub Total Of Part (II) | [8 empty] | 0
| Grand Total | [8 empty] | 931440.1783
JE |  |  |  | AE |  |  |  |  | Executive Engineer
P. H. Division, Hajipur.

## Rahimapur 02B (hidden)
Sub Estimate no. - 3B
Rahimapur WARD NO. :-02B
WATER SUPPLY DISTRIBUTION SYSTEM
S.N. | Particulars |  |  |  |  | Quantity |  | Unit | Rate | Amount
1/ 2.8 | Earthwork in excavation over areas (exceeding 30 cm in depth 1.5 in width as well as 10 sqm on plan) including disposal of excavated earth lead upto 50m and lift upto 1.5m, disposal earth to be levelled and neatly dressed.
| 110mm dia Pipe | 0 | 0.3 | 1.1 | = | 0 | [6 empty] | 152000
| 90mm dia Pipe | 150 | 0.3 | 1.1 | = | 49.5 | [6 empty] | 152000
| 75mm dia Pipe | 500 | 0.3 | 1.1 | = | 165
| 63mm dia Pipe | 550 | 0.3 | 1.1 | = | 181.5 | [6 empty] | 152000
| 50 mm dia Pipe | 350 | 0.3 | 1.1 | = | 115.5
| 40mm dia Pipe | 300 | 0.3 | 1.1 | = | 99
|  | 1850 |  |  |  | 610.5 | M3
| Add 5% extra for fittings = |  |  |  |  | 30.525 | M3
[6 empty] | 641.025 | M3 | P/M3 | 360.7 | 231217.7175
2/ 2.26 | Filling available excavated earth (excluding rock) in trenches, plinth, sides of foundations etc. in layers not exceeding 20cm in depth, consolidating each deposited layer by ramming and watering, lead up to 50 m and lift upto 1.5 m. |  |  |  |  | 628.2045 | M3 | P/M3 | 123.9 | 77834.5375
3/ 15.2.1 | Demolishing cement concrete manually/by mechanical means including disposal of material within 50 metres lead as per direction of Engineer - in - charge. | [8 empty] | 24248.2275
1:3:6 or richer mix
|  | 555 | 0.3 | 0.15 | = | 24.975 | M3 | P/M3 | 970.9
4/ 4.1.3 | Providing and laying in position cement concrete of specified grade excluding the cost of centering and shuttering all work upto plinth |  |  |  |  | 24.975 | M3 | P/M3 | 3998.1 | 99852.5475 | 4969
1:2:4 (1 cement: 2 coarse sand : 4 graded stone aggregate 40mm nominal size)
5 | Carriage of the following materials from quarry to work site including loading, unloading and staking at work site as per specification & direction of E/I.
| Coarse Sand (44Km Pucca & 1Km Kaccha Carriage) |  |  |  |  | 11.4885 | M3 | P/M3 | 1160.62 | 13333.7829
| Stone chips (195Km Pucca & 5Km unsurafced Carriage) |  |  |  |  | 22.977 | M3 | P/M3 | 4291.17 | 98598.2131
6A/ 18.12 | Providing and fixing G.I.Pipes complete with G.I. Fittings including trenching and refilling etc.
18.12.6 | 50mm dia G.I.Pipe from T/well to PVC Tank |  |  |  |  | 14 | M | P/M | 572.6 | 8016.4 |  |  |  | 611.3975
18.12.8 | 80mm dia G.I.Pipe from PVC Tank to Distribution main |  |  |  |  | 14 | M | P/M | 818.2 | 11454.8
18.12.7 | 65mm dia G.I.Pipe for wash out |  |  |  |  | 12 | M | P/M | 667.7 | 8012.4
7A/ 18.31.1.1 | P/F C.I sluice Valve (with Cap) complete with bolts,nuts,rubber insertions etc
6B/ | Providing and fixing brass gate valve with C.I. wheel of approved quality (screwed end).
| 80mm dia Pipe |  |  |  |  | 2 | Nos. | Each | 2227.6 | 4455.2
| 65mm dia Pipe |  |  |  |  | 1 | Nos. | Each | 1490.7 | 1490.7
| 50mm dia Pipe |  |  |  |  | 1 | Nos. | Each | 878.2 | 878.2
7/ 18.33 | Constructing masonry Chamber 60x60x75 cm inside, in brick work in cement mortar 1:4 (1 cement : 4 coarse sand) for sluice valve,with C.I. surface box 100mm top diameter, 160 mm bottom diameter and 180 mm deep ( inside) with chained lid and RCC top slab 1:2:4 mix (1 cement : 2 coarse sand : 4 graded stone aggregate 20mm nominal size ) , necessary excavation, foundation concrete 1:5:10(1 cement : 5 fine sand : 10 graded stone aggregate 40 mm nominalsize) and inside plastering with cement mortar 1:3 (1 cement : 3coarse sand) 12 mm thick, finished with a floating coat of neat cement complete as per standard specifications & direction of E/I. |  |  |  |  | 4 | Nos. | Each | 7210.6 | 28842.4
| Work for additional depth | [10 empty] | 4.9933
Brick work (1:4) in foundation
| 2 | 1.1 | 0.25 | 0.35 | 0.1925
| 2 | 0.6 | 0.25 | 0.35 | 0.105
6.1.12 |  |  |  |  | 0.2975 | 1.19 | M3 | P/M3 | 5017.9 | 5971.301
13.11.1 | Plaster (1:3)
| 8 | 1.1 |  | 0.35 | 3.08 | 12.32 | M2 | P/M2 | 164.3 | 2024.176
8 | Carriage 10% of item 9 | [8 empty] | 3683.7877
9A/ 18.48 | Providing and placing on terrace (at all floor levels) polyethylene water storage tank, ISI : 12701 marked, with cover and suitable locking arrangement and making necessary holes for inlet, outlet and overflow pipes but without fittings and the base support for tank. |  |  |  |  | 10000 | Ltrs. | P/Ltr. | 9.7 | 97000
9B | Providing and fixing MS clamp consisting of 32mm X 5mm thick two no. rings spaced suitably distance apart. | [7 empty] | LS | 3000
10A | Supplying all materials labours & fixing 50mm dia. G.I pipe for using as filling station etc. All as per direction of E/I
| 50mm dia. Pipe from distribution main |  |  |  |  | 3.5 | M | P/M | 572.6 | 2004.1
10B | Providing and fixing G.I fittings
| 80mmx80mmx50mm dia Tee |  |  |  |  | 1 | No | Each | 225 | 225
| 50mm dia bend |  |  |  |  | 3 | No | Each | 175 | 525
| Providing and fixing gun metal gate valve with C.I. wheel of approved quality (screwed end) :50mm nominal dia. |  |  |  |  | 1 | N | Each | 811.4 | 811.4
10C | Providing designation of 100 A brick Flat soling joints filled with local sand including cost of watering, taxes & royalty all complete as per specification & direction of E/I.
|  | 1 | 0.45 | 0.45 |  | 0.2025 | m2 | p/m2 | 283.3 | 57.3683
11 | Providing and fixing PTMT extension nipple for water tank pipe, fittings of approved quality and colour.
| 50mm dia |  |  |  |  | 2 | Nos. | each | 300 | 600
| 63mm dia |  |  |  |  | 1 | No. | each | 350 | 350
| 80 mm dia |  |  |  |  | 1 | No. | each | 550 | 550
| Sub Total of Part - I | [8 empty] | 0
Part - II
12 | Providing and laying High Density Polyethyene pipe (HDPE pipe) of 20 mm to 225 mm OD and pressure 6.0 Kg/cm2 and 10 Kg/cm2 sutable for water supply which is available in all standard, like ISI-4984/1995 and various grades like PE-80, PE-100 including required specials. Rates are inclusive of , all taxes and duties (Exise duty @12.50% &CST @2% against Form 'C'), labour cess, contractor profit and overhead charges all complete as per direction of Engineer-in-charge.
12A | HDPE pipe of materials grade PE100- PN10 (dia in mm)
| 110mm dia Pipe |  |  |  |  | 0 | M | P/M | 646.25 | 0
| 90mm dia Pipe |  |  |  |  | 150 | M | P/M | 437.96 | 65694
| 75mm dia Pipe |  |  |  |  | 500 | M | P/M | 306.31 | 153155
| 63mm dia Pipe |  |  |  |  | 550 | M | P/M | 218.62 | 120241
13B | HDPE pipe of materials grade PE100- PN8 (dia in mm)
| 50 mm dia Pipe |  |  |  |  | 350 | M | P/M | 116.25 | 40687.5
| 40mm dia Pipe |  |  |  |  | 300 | M | P/M | 76.53 | 22959
13C | Providing all materials labours tools, fittings , specials and tackles for fitting, jointing and connecting HDPE pipes. (5% of the cost of the HDPE pipe .) | [8 empty] | 20136.825
| Sub Total Of Part (II) | [8 empty] | 0
| Grand Total | [8 empty] | 1147910.584
JE |  |  |  | AE |  |  |  |  | Executive Engineer
P. H. Division, Hajipur.

## Rahimapur10B&11B (hidden)
Sub Estimate no. - 3C
Rahimapur WARD NO. :-10B&11B
WATER SUPPLY DISTRIBUTION SYSTEM
S.N. | Particulars |  |  |  |  | Quantity |  | Unit | Rate | Amount
1/ 2.8 | Earthwork in excavation over areas (exceeding 30 cm in depth 1.5 in width as well as 10 sqm on plan) including disposal of excavated earth lead upto 50m and lift upto 1.5m, disposal earth to be levelled and neatly dressed.
| 110mm dia Pipe | 0 | 0.3 | 1.1 | = | 0 | [6 empty] | 152000
| 90mm dia Pipe | 100 | 0.3 | 1.1 | = | 33 | [6 empty] | 152000
| 75mm dia Pipe | 300 | 0.3 | 1.1 | = | 99
| 63mm dia Pipe | 250 | 0.3 | 1.1 | = | 82.5 | [6 empty] | 152000
| 50 mm dia Pipe | 200 | 0.3 | 1.1 | = | 66
| 40mm dia Pipe | 250 | 0.3 | 1.1 | = | 82.5
|  | 1100 |  |  |  | 363 | M3
| Add 5% extra for fittings = |  |  |  |  | 18.15 | M3
[6 empty] | 381.15 | M3 | P/M3 | 360.7 | 137480.805
2/ 2.26 | Filling available excavated earth (excluding rock) in trenches, plinth, sides of foundations etc. in layers not exceeding 20cm in depth, consolidating each deposited layer by ramming and watering, lead up to 50 m and lift upto 1.5 m. |  |  |  |  | 373.527 | M3 | P/M3 | 123.9 | 46279.9953
3/ 15.2.1 | Demolishing cement concrete manually/by mechanical means including disposal of material within 50 metres lead as per direction of Engineer - in - charge. | [8 empty] | 14417.865
1:3:6 or richer mix
|  | 330 | 0.3 | 0.15 | = | 14.85 | M3 | P/M3 | 970.9
4/ 4.1.3 | Providing and laying in position cement concrete of specified grade excluding the cost of centering and shuttering all work upto plinth |  |  |  |  | 14.85 | M3 | P/M3 | 3998.1 | 59371.785 | 4969
1:2:4 (1 cement: 2 coarse sand : 4 graded stone aggregate 40mm nominal size)
5 | Carriage of the following materials from quarry to work site including loading, unloading and staking at work site as per specification & direction of E/I.
| Coarse Sand (44Km Pucca & 1Km Kaccha Carriage) |  |  |  |  | 6.831 | M3 | P/M3 | 1160.62 | 7928.1952
| Stone chips (195Km Pucca & 5Km unsurafced Carriage) |  |  |  |  | 13.662 | M3 | P/M3 | 4291.17 | 58625.9645
6A/ 18.12 | Providing and fixing G.I.Pipes complete with G.I. Fittings including trenching and refilling etc.
18.12.6 | 50mm dia G.I.Pipe from T/well to PVC Tank |  |  |  |  | 14 | M | P/M | 572.6 | 8016.4 |  |  |  | 611.3975
18.12.8 | 80mm dia G.I.Pipe from PVC Tank to Distribution main |  |  |  |  | 14 | M | P/M | 818.2 | 11454.8
18.12.7 | 65mm dia G.I.Pipe for wash out |  |  |  |  | 12 | M | P/M | 667.7 | 8012.4
7A/ 18.31.1.1 | P/F C.I sluice Valve (with Cap) complete with bolts,nuts,rubber insertions etc
6B/ | Providing and fixing brass gate valve with C.I. wheel of approved quality (screwed end).
| 80mm dia Pipe |  |  |  |  | 2 | Nos. | Each | 2227.6 | 4455.2
| 65mm dia Pipe |  |  |  |  | 1 | Nos. | Each | 1490.7 | 1490.7
| 50mm dia Pipe |  |  |  |  | 1 | Nos. | Each | 878.2 | 878.2
7/ 18.33 | Constructing masonry Chamber 60x60x75 cm inside, in brick work in cement mortar 1:4 (1 cement : 4 coarse sand) for sluice valve,with C.I. surface box 100mm top diameter, 160 mm bottom diameter and 180 mm deep ( inside) with chained lid and RCC top slab 1:2:4 mix (1 cement : 2 coarse sand : 4 graded stone aggregate 20mm nominal size ) , necessary excavation, foundation concrete 1:5:10(1 cement : 5 fine sand : 10 graded stone aggregate 40 mm nominalsize) and inside plastering with cement mortar 1:3 (1 cement : 3coarse sand) 12 mm thick, finished with a floating coat of neat cement complete as per standard specifications & direction of E/I. |  |  |  |  | 4 | Nos. | Each | 7210.6 | 28842.4
| Work for additional depth | [10 empty] | 4.9933
Brick work (1:4) in foundation
| 2 | 1.1 | 0.25 | 0.35 | 0.1925
| 2 | 0.6 | 0.25 | 0.35 | 0.105
6.1.12 |  |  |  |  | 0.2975 | 1.19 | M3 | P/M3 | 5017.9 | 5971.301
13.11.1 | Plaster (1:3)
| 8 | 1.1 |  | 0.35 | 3.08 | 12.32 | M2 | P/M2 | 164.3 | 2024.176
8 | Carriage 10% of item 9 | [8 empty] | 3683.7877
9A/ 18.48 | Providing and placing on terrace (at all floor levels) polyethylene water storage tank, ISI : 12701 marked, with cover and suitable locking arrangement and making necessary holes for inlet, outlet and overflow pipes but without fittings and the base support for tank. |  |  |  |  | 10000 | Ltrs. | P/Ltr. | 9.7 | 97000
9B | Providing and fixing MS clamp consisting of 32mm X 5mm thick two no. rings spaced suitably distance apart. | [7 empty] | LS | 3000
10A | Supplying all materials labours & fixing 50mm dia. G.I pipe for using as filling station etc. All as per direction of E/I
| 50mm dia. Pipe from distribution main |  |  |  |  | 3.5 | M | P/M | 572.6 | 2004.1
10B | Providing and fixing G.I fittings
| 80mmx80mmx50mm dia Tee |  |  |  |  | 1 | No | Each | 225 | 225
| 50mm dia bend |  |  |  |  | 3 | No | Each | 175 | 525
| Providing and fixing gun metal gate valve with C.I. wheel of approved quality (screwed end) :50mm nominal dia. |  |  |  |  | 1 | N | Each | 811.4 | 811.4
10C | Providing designation of 100 A brick Flat soling joints filled with local sand including cost of watering, taxes & royalty all complete as per specification & direction of E/I.
|  | 1 | 0.45 | 0.45 |  | 0.2025 | m2 | p/m2 | 283.3 | 57.3683
11 | Providing and fixing PTMT extension nipple for water tank pipe, fittings of approved quality and colour.
| 50mm dia |  |  |  |  | 2 | Nos. | each | 300 | 600
| 63mm dia |  |  |  |  | 1 | No. | each | 350 | 350
| 80 mm dia |  |  |  |  | 1 | No. | each | 550 | 550
| Sub Total of Part - I | [8 empty] | 0
Part - II
12 | Providing and laying High Density Polyethyene pipe (HDPE pipe) of 20 mm to 225 mm OD and pressure 6.0 Kg/cm2 and 10 Kg/cm2 sutable for water supply which is available in all standard, like ISI-4984/1995 and various grades like PE-80, PE-100 including required specials. Rates are inclusive of , all taxes and duties (Exise duty @12.50% &CST @2% against Form 'C'), labour cess, contractor profit and overhead charges all complete as per direction of Engineer-in-charge.
12A | HDPE pipe of materials grade PE100- PN10 (dia in mm)
| 110mm dia Pipe |  |  |  |  | 0 | M | P/M | 646.25 | 0
| 90mm dia Pipe |  |  |  |  | 100 | M | P/M | 437.96 | 43796
| 75mm dia Pipe |  |  |  |  | 300 | M | P/M | 306.31 | 91893
| 63mm dia Pipe |  |  |  |  | 250 | M | P/M | 218.62 | 54655
13B | HDPE pipe of materials grade PE100- PN8 (dia in mm)
| 50 mm dia Pipe |  |  |  |  | 200 | M | P/M | 116.25 | 23250
| 40mm dia Pipe |  |  |  |  | 250 | M | P/M | 76.53 | 19132.5
13C | Providing all materials labours tools, fittings , specials and tackles for fitting, jointing and connecting HDPE pipes. (5% of the cost of the HDPE pipe .) | [8 empty] | 11636.325
| Sub Total Of Part (II) | [8 empty] | 0
| Grand Total | [8 empty] | 748419.668
JE |  |  |  | AE |  |  |  |  | Executive Engineer
P. H. Division, Hajipur.

## Sahdullahpur Dhabaul 11B (hidden)
Sub Estimate no. - 3A
Sahdullahpur Dhabaul Ward no. :- 11B
WATER SUPPLY DISTRIBUTION SYSTEM
S.N. | Particulars |  |  |  |  | Quantity |  | Unit | Rate | Amount
1/ 2.8 | Earthwork in excavation over areas (exceeding 30 cm in depth 1.5 in width as well as 10 sqm on plan) including disposal of excavated earth lead upto 50m and lift upto 1.5m, disposal earth to be levelled and neatly dressed.
| 110mm dia Pipe | 0 | 0.3 | 1.1 | = | 0 | [6 empty] | 152000
| 90mm dia Pipe | 100 | 0.3 | 1.1 | = | 33 | [6 empty] | 152000
| 75mm dia Pipe | 200 | 0.3 | 1.1 | = | 66
| 63mm dia Pipe | 300 | 0.3 | 1.1 | = | 99 | [6 empty] | 152000
| 50 mm dia Pipe | 350 | 0.3 | 1.1 | = | 115.5
| 40mm dia Pipe | 250 | 0.3 | 1.1 | = | 82.5
|  | 1200 |  |  |  | 396 | M3
| Add 5% extra for fittings = |  |  |  |  | 19.8 | M3
[6 empty] | 415.8 | M3 | P/M3 | 360.7 | 149979.06
2/ 2.26 | Filling available excavated earth (excluding rock) in trenches, plinth, sides of foundations etc. in layers not exceeding 20cm in depth, consolidating each deposited layer by ramming and watering, lead up to 50 m and lift upto 1.5 m. |  |  |  |  | 407.484 | M3 | P/M3 | 123.9 | 50487.2676
3/ 15.2.1 | Demolishing cement concrete manually/by mechanical means including disposal of material within 50 metres lead as per direction of Engineer - in - charge. | [8 empty] | 15728.58
1:3:6 or richer mix
|  | 360 | 0.3 | 0.15 | = | 16.2 | M3 | P/M3 | 970.9
4/ 4.1.3 | Providing and laying in position cement concrete of specified grade excluding the cost of centering and shuttering all work upto plinth |  |  |  |  | 16.2 | M3 | P/M3 | 3998.1 | 64769.22 | 4969
1:2:4 (1 cement: 2 coarse sand : 4 graded stone aggregate 40mm nominal size)
5 | Carriage of the following materials from quarry to work site including loading, unloading and staking at work site as per specification & direction of E/I.
| Coarse Sand (44Km Pucca & 1Km Kaccha Carriage) |  |  |  |  | 7.452 | M3 | P/M3 | 1160.62 | 8648.9402
| Stone chips (195Km Pucca & 5Km unsurafced Carriage) |  |  |  |  | 14.904 | M3 | P/M3 | 4291.17 | 63955.5977
6A/ 18.12 | Providing and fixing G.I.Pipes complete with G.I. Fittings including trenching and refilling etc.
18.12.6 | 50mm dia G.I.Pipe from T/well to PVC Tank |  |  |  |  | 14 | M | P/M | 572.6 | 8016.4 |  |  |  | 611.3975
18.12.8 | 80mm dia G.I.Pipe from PVC Tank to Distribution main |  |  |  |  | 14 | M | P/M | 818.2 | 11454.8
18.12.7 | 65mm dia G.I.Pipe for wash out |  |  |  |  | 12 | M | P/M | 667.7 | 8012.4
7A/ 18.31.1.1 | P/F C.I sluice Valve (with Cap) complete with bolts,nuts,rubber insertions etc
6B/ | Providing and fixing brass gate valve with C.I. wheel of approved quality (screwed end).
| 80mm dia Pipe |  |  |  |  | 2 | Nos. | Each | 2227.6 | 4455.2
| 65mm dia Pipe |  |  |  |  | 1 | Nos. | Each | 1490.7 | 1490.7
| 50mm dia Pipe |  |  |  |  | 1 | Nos. | Each | 878.2 | 878.2
7/ 18.33 | Constructing masonry Chamber 60x60x75 cm inside, in brick work in cement mortar 1:4 (1 cement : 4 coarse sand) for sluice valve,with C.I. surface box 100mm top diameter, 160 mm bottom diameter and 180 mm deep ( inside) with chained lid and RCC top slab 1:2:4 mix (1 cement : 2 coarse sand : 4 graded stone aggregate 20mm nominal size ) , necessary excavation, foundation concrete 1:5:10(1 cement : 5 fine sand : 10 graded stone aggregate 40 mm nominalsize) and inside plastering with cement mortar 1:3 (1 cement : 3coarse sand) 12 mm thick, finished with a floating coat of neat cement complete as per standard specifications & direction of E/I. |  |  |  |  | 4 | Nos. | Each | 7210.6 | 28842.4
| Work for additional depth | [10 empty] | 4.9933
Brick work (1:4) in foundation
| 2 | 1.1 | 0.25 | 0.35 | 0.1925
| 2 | 0.6 | 0.25 | 0.35 | 0.105
6.1.12 |  |  |  |  | 0.2975 | 1.19 | M3 | P/M3 | 5017.9 | 5971.301
13.11.1 | Plaster (1:3)
| 8 | 1.1 |  | 0.35 | 3.08 | 12.32 | M2 | P/M2 | 164.3 | 2024.176
8 | Carriage 10% of item 9 | [8 empty] | 3683.7877
9A/ 18.48 | Providing and placing on terrace (at all floor levels) polyethylene water storage tank, ISI : 12701 marked, with cover and suitable locking arrangement and making necessary holes for inlet, outlet and overflow pipes but without fittings and the base support for tank. |  |  |  |  | 10000 | Ltrs. | P/Ltr. | 9.7 | 97000
9B | Providing and fixing MS clamp consisting of 32mm X 5mm thick two no. rings spaced suitably distance apart. | [7 empty] | LS | 3000
10A | Supplying all materials labours & fixing 50mm dia. G.I pipe for using as filling station etc. All as per direction of E/I
| 50mm dia. Pipe from distribution main |  |  |  |  | 3.5 | M | P/M | 572.6 | 2004.1
10B | Providing and fixing G.I fittings
| 80mmx80mmx50mm dia Tee |  |  |  |  | 1 | No | Each | 225 | 225
| 50mm dia bend |  |  |  |  | 3 | No | Each | 175 | 525
| Providing and fixing gun metal gate valve with C.I. wheel of approved quality (screwed end) :50mm nominal dia. |  |  |  |  | 1 | N | Each | 811.4 | 811.4
10C | Providing designation of 100 A brick Flat soling joints filled with local sand including cost of watering, taxes & royalty all complete as per specification & direction of E/I.
|  | 1 | 0.45 | 0.45 |  | 0.2025 | m2 | p/m2 | 283.3 | 57.3683
11 | Providing and fixing PTMT extension nipple for water tank pipe, fittings of approved quality and colour.
| 50mm dia |  |  |  |  | 2 | Nos. | each | 300 | 600
| 63mm dia |  |  |  |  | 1 | No. | each | 350 | 350
| 80 mm dia |  |  |  |  | 1 | No. | each | 550 | 550
| Sub Total of Part - I | [8 empty] | 0
Part - II
12 | Providing and laying High Density Polyethyene pipe (HDPE pipe) of 20 mm to 225 mm OD and pressure 6.0 Kg/cm2 and 10 Kg/cm2 sutable for water supply which is available in all standard, like ISI-4984/1995 and various grades like PE-80, PE-100 including required specials. Rates are inclusive of , all taxes and duties (Exise duty @12.50% &CST @2% against Form 'C'), labour cess, contractor profit and overhead charges all complete as per direction of Engineer-in-charge.
12A | HDPE pipe of materials grade PE100- PN10 (dia in mm)
| 110mm dia Pipe |  |  |  |  | 0 | M | P/M | 646.25 | 0
| 90mm dia Pipe |  |  |  |  | 100 | M | P/M | 437.96 | 43796
| 75mm dia Pipe |  |  |  |  | 200 | M | P/M | 306.31 | 61262
| 63mm dia Pipe |  |  |  |  | 300 | M | P/M | 218.62 | 65586
13B | HDPE pipe of materials grade PE100- PN8 (dia in mm)
| 50 mm dia Pipe |  |  |  |  | 350 | M | P/M | 116.25 | 40687.5
| 40mm dia Pipe |  |  |  |  | 250 | M | P/M | 76.53 | 19132.5
13C | Providing all materials labours tools, fittings , specials and tackles for fitting, jointing and connecting HDPE pipes. (5% of the cost of the HDPE pipe .) | [8 empty] | 11523.2
| Sub Total Of Part (II) | [8 empty] | 0
| Grand Total | [8 empty] | 775508.0985
JE |  |  |  | AE |  |  |  |  | Executive Engineer
P. H. Division, Hajipur.

## Sahdullahpur Dhabaul & Majhauli (hidden)
Sub Estimate no. - 3B
Sahdullahpur Dhabaul & Majhauli Siman Ward no. :- 05B&05B
WATER SUPPLY DISTRIBUTION SYSTEM
S.N. | Particulars |  |  |  |  | Quantity |  | Unit | Rate | Amount
1/ 2.8 | Earthwork in excavation over areas (exceeding 30 cm in depth 1.5 in width as well as 10 sqm on plan) including disposal of excavated earth lead upto 50m and lift upto 1.5m, disposal earth to be levelled and neatly dressed.
| 110mm dia Pipe | 0 | 0.3 | 1.1 | = | 0 | [6 empty] | 152000
| 90mm dia Pipe | 100 | 0.3 | 1.1 | = | 33 | [6 empty] | 152000
| 75mm dia Pipe | 200 | 0.3 | 1.1 | = | 66
| 63mm dia Pipe | 250 | 0.3 | 1.1 | = | 82.5 | [6 empty] | 152000
| 50 mm dia Pipe | 250 | 0.3 | 1.1 | = | 82.5
| 40mm dia Pipe | 200 | 0.3 | 1.1 | = | 66
|  | 1000 |  |  |  | 330 | M3
| Add 5% extra for fittings = |  |  |  |  | 16.5 | M3
[6 empty] | 346.5 | M3 | P/M3 | 360.7 | 124982.55
2/ 2.26 | Filling available excavated earth (excluding rock) in trenches, plinth, sides of foundations etc. in layers not exceeding 20cm in depth, consolidating each deposited layer by ramming and watering, lead up to 50 m and lift upto 1.5 m. |  |  |  |  | 339.57 | M3 | P/M3 | 123.9 | 42072.723
3/ 15.2.1 | Demolishing cement concrete manually/by mechanical means including disposal of material within 50 metres lead as per direction of Engineer - in - charge. | [8 empty] | 13107.15
1:3:6 or richer mix
|  | 300 | 0.3 | 0.15 | = | 13.5 | M3 | P/M3 | 970.9
4/ 4.1.3 | Providing and laying in position cement concrete of specified grade excluding the cost of centering and shuttering all work upto plinth |  |  |  |  | 13.5 | M3 | P/M3 | 3998.1 | 53974.35 | 4969
1:2:4 (1 cement: 2 coarse sand : 4 graded stone aggregate 40mm nominal size)
5 | Carriage of the following materials from quarry to work site including loading, unloading and staking at work site as per specification & direction of E/I.
| Coarse Sand (44Km Pucca & 1Km Kaccha Carriage) |  |  |  |  | 6.21 | M3 | P/M3 | 1160.62 | 7207.4502
| Stone chips (195Km Pucca & 5Km unsurafced Carriage) |  |  |  |  | 12.42 | M3 | P/M3 | 4291.17 | 53296.3314
6A/ 18.12 | Providing and fixing G.I.Pipes complete with G.I. Fittings including trenching and refilling etc.
18.12.6 | 50mm dia G.I.Pipe from T/well to PVC Tank |  |  |  |  | 14 | M | P/M | 572.6 | 8016.4 |  |  |  | 611.3975
18.12.8 | 80mm dia G.I.Pipe from PVC Tank to Distribution main |  |  |  |  | 14 | M | P/M | 818.2 | 11454.8
18.12.7 | 65mm dia G.I.Pipe for wash out |  |  |  |  | 12 | M | P/M | 667.7 | 8012.4
7A/ 18.31.1.1 | P/F C.I sluice Valve (with Cap) complete with bolts,nuts,rubber insertions etc
6B/ | Providing and fixing brass gate valve with C.I. wheel of approved quality (screwed end).
| 80mm dia Pipe |  |  |  |  | 2 | Nos. | Each | 2227.6 | 4455.2
| 65mm dia Pipe |  |  |  |  | 1 | Nos. | Each | 1490.7 | 1490.7
| 50mm dia Pipe |  |  |  |  | 1 | Nos. | Each | 878.2 | 878.2
7/ 18.33 | Constructing masonry Chamber 60x60x75 cm inside, in brick work in cement mortar 1:4 (1 cement : 4 coarse sand) for sluice valve,with C.I. surface box 100mm top diameter, 160 mm bottom diameter and 180 mm deep ( inside) with chained lid and RCC top slab 1:2:4 mix (1 cement : 2 coarse sand : 4 graded stone aggregate 20mm nominal size ) , necessary excavation, foundation concrete 1:5:10(1 cement : 5 fine sand : 10 graded stone aggregate 40 mm nominalsize) and inside plastering with cement mortar 1:3 (1 cement : 3coarse sand) 12 mm thick, finished with a floating coat of neat cement complete as per standard specifications & direction of E/I. |  |  |  |  | 4 | Nos. | Each | 7210.6 | 28842.4
| Work for additional depth | [10 empty] | 4.9933
Brick work (1:4) in foundation
| 2 | 1.1 | 0.25 | 0.35 | 0.1925
| 2 | 0.6 | 0.25 | 0.35 | 0.105
6.1.12 |  |  |  |  | 0.2975 | 1.19 | M3 | P/M3 | 5017.9 | 5971.301
13.11.1 | Plaster (1:3)
| 8 | 1.1 |  | 0.35 | 3.08 | 12.32 | M2 | P/M2 | 164.3 | 2024.176
8 | Carriage 10% of item 9 | [8 empty] | 3683.7877
9A/ 18.48 | Providing and placing on terrace (at all floor levels) polyethylene water storage tank, ISI : 12701 marked, with cover and suitable locking arrangement and making necessary holes for inlet, outlet and overflow pipes but without fittings and the base support for tank. |  |  |  |  | 10000 | Ltrs. | P/Ltr. | 9.7 | 97000
9B | Providing and fixing MS clamp consisting of 32mm X 5mm thick two no. rings spaced suitably distance apart. | [7 empty] | LS | 3000
10A | Supplying all materials labours & fixing 50mm dia. G.I pipe for using as filling station etc. All as per direction of E/I
| 50mm dia. Pipe from distribution main |  |  |  |  | 3.5 | M | P/M | 572.6 | 2004.1
10B | Providing and fixing G.I fittings
| 80mmx80mmx50mm dia Tee |  |  |  |  | 1 | No | Each | 225 | 225
| 50mm dia bend |  |  |  |  | 3 | No | Each | 175 | 525
| Providing and fixing gun metal gate valve with C.I. wheel of approved quality (screwed end) :50mm nominal dia. |  |  |  |  | 1 | N | Each | 811.4 | 811.4
10C | Providing designation of 100 A brick Flat soling joints filled with local sand including cost of watering, taxes & royalty all complete as per specification & direction of E/I.
|  | 1 | 0.45 | 0.45 |  | 0.2025 | m2 | p/m2 | 283.3 | 57.3683
11 | Providing and fixing PTMT extension nipple for water tank pipe, fittings of approved quality and colour.
| 50mm dia |  |  |  |  | 2 | Nos. | each | 300 | 600
| 63mm dia |  |  |  |  | 1 | No. | each | 350 | 350
| 80 mm dia |  |  |  |  | 1 | No. | each | 550 | 550
| Sub Total of Part - I | [8 empty] | 0
Part - II
12 | Providing and laying High Density Polyethyene pipe (HDPE pipe) of 20 mm to 225 mm OD and pressure 6.0 Kg/cm2 and 10 Kg/cm2 sutable for water supply which is available in all standard, like ISI-4984/1995 and various grades like PE-80, PE-100 including required specials. Rates are inclusive of , all taxes and duties (Exise duty @12.50% &CST @2% against Form 'C'), labour cess, contractor profit and overhead charges all complete as per direction of Engineer-in-charge.
12A | HDPE pipe of materials grade PE100- PN10 (dia in mm)
| 110mm dia Pipe |  |  |  |  | 0 | M | P/M | 646.25 | 0
| 90mm dia Pipe |  |  |  |  | 100 | M | P/M | 437.96 | 43796
| 75mm dia Pipe |  |  |  |  | 200 | M | P/M | 306.31 | 61262
| 63mm dia Pipe |  |  |  |  | 250 | M | P/M | 218.62 | 54655
13B | HDPE pipe of materials grade PE100- PN8 (dia in mm)
| 50 mm dia Pipe |  |  |  |  | 250 | M | P/M | 116.25 | 29062.5
| 40mm dia Pipe |  |  |  |  | 200 | M | P/M | 76.53 | 15306
13C | Providing all materials labours tools, fittings , specials and tackles for fitting, jointing and connecting HDPE pipes. (5% of the cost of the HDPE pipe .) | [8 empty] | 10204.075
| Sub Total Of Part (II) | [8 empty] | 0
| Grand Total | [8 empty] | 688878.3625
JE |  |  |  | AE |  |  |  |  | Executive Engineer
P. H. Division, Hajipur.

## Majlispur 05b (hidden)
Sub Estimate no. - 3
Majlispur Ward No. :-05B
WATER SUPPLY DISTRIBUTION SYSTEM
S.N. | Particulars |  |  |  |  | Quantity |  | Unit | Rate | Amount
1/ 2.8 | Earthwork in excavation over areas (exceeding 30 cm in depth 1.5 in width as well as 10 sqm on plan) including disposal of excavated earth lead upto 50m and lift upto 1.5m, disposal earth to be levelled and neatly dressed.
| 110mm dia Pipe | 0 | 0.3 | 1.1 | = | 0 | [6 empty] | 152000
| 90mm dia Pipe | 100 | 0.3 | 1.1 | = | 33 | [6 empty] | 152000
| 75mm dia Pipe | 200 | 0.3 | 1.1 | = | 66
| 63mm dia Pipe | 300 | 0.3 | 1.1 | = | 99 | [6 empty] | 152000
| 50 mm dia Pipe | 300 | 0.3 | 1.1 | = | 99
| 40mm dia Pipe | 300 | 0.3 | 1.1 | = | 99
|  | 1200 |  |  |  | 396 | M3
| Add 5% extra for fittings = |  |  |  |  | 19.8 | M3
[6 empty] | 415.8 | M3 | P/M3 | 360.7 | 149979.06
2/ 2.26 | Filling available excavated earth (excluding rock) in trenches, plinth, sides of foundations etc. in layers not exceeding 20cm in depth, consolidating each deposited layer by ramming and watering, lead up to 50 m and lift upto 1.5 m. |  |  |  |  | 407.484 | M3 | P/M3 | 123.9 | 50487.2676
3/ 15.2.1 | Demolishing cement concrete manually/by mechanical means including disposal of material within 50 metres lead as per direction of Engineer - in - charge. | [8 empty] | 15728.58
1:3:6 or richer mix
|  | 360 | 0.3 | 0.15 | = | 16.2 | M3 | P/M3 | 970.9
4/ 4.1.3 | Providing and laying in position cement concrete of specified grade excluding the cost of centering and shuttering all work upto plinth |  |  |  |  | 16.2 | M3 | P/M3 | 3998.1 | 64769.22 | 4969
1:2:4 (1 cement: 2 coarse sand : 4 graded stone aggregate 40mm nominal size)
5 | Carriage of the following materials from quarry to work site including loading, unloading and staking at work site as per specification & direction of E/I.
| Coarse Sand (44Km Pucca & 1Km Kaccha Carriage) |  |  |  |  | 7.452 | M3 | P/M3 | 1160.62 | 8648.9402
| Stone chips (195Km Pucca & 5Km unsurafced Carriage) |  |  |  |  | 14.904 | M3 | P/M3 | 4291.17 | 63955.5977
6A/ 18.12 | Providing and fixing G.I.Pipes complete with G.I. Fittings including trenching and refilling etc.
18.12.6 | 50mm dia G.I.Pipe from T/well to PVC Tank |  |  |  |  | 14 | M | P/M | 572.6 | 8016.4 |  |  |  | 611.3975
18.12.8 | 80mm dia G.I.Pipe from PVC Tank to Distribution main |  |  |  |  | 14 | M | P/M | 818.2 | 11454.8
18.12.7 | 65mm dia G.I.Pipe for wash out |  |  |  |  | 12 | M | P/M | 667.7 | 8012.4
7A/ 18.31.1.1 | P/F C.I sluice Valve (with Cap) complete with bolts,nuts,rubber insertions etc
6B/ | Providing and fixing brass gate valve with C.I. wheel of approved quality (screwed end).
| 80mm dia Pipe |  |  |  |  | 2 | Nos. | Each | 2227.6 | 4455.2
| 65mm dia Pipe |  |  |  |  | 1 | Nos. | Each | 1490.7 | 1490.7
| 50mm dia Pipe |  |  |  |  | 1 | Nos. | Each | 878.2 | 878.2
7/ 18.33 | Constructing masonry Chamber 60x60x75 cm inside, in brick work in cement mortar 1:4 (1 cement : 4 coarse sand) for sluice valve,with C.I. surface box 100mm top diameter, 160 mm bottom diameter and 180 mm deep ( inside) with chained lid and RCC top slab 1:2:4 mix (1 cement : 2 coarse sand : 4 graded stone aggregate 20mm nominal size ) , necessary excavation, foundation concrete 1:5:10(1 cement : 5 fine sand : 10 graded stone aggregate 40 mm nominalsize) and inside plastering with cement mortar 1:3 (1 cement : 3coarse sand) 12 mm thick, finished with a floating coat of neat cement complete as per standard specifications & direction of E/I. |  |  |  |  | 4 | Nos. | Each | 7210.6 | 28842.4
| Work for additional depth | [10 empty] | 4.9933
Brick work (1:4) in foundation
| 2 | 1.1 | 0.25 | 0.35 | 0.1925
| 2 | 0.6 | 0.25 | 0.35 | 0.105
6.1.12 |  |  |  |  | 0.2975 | 1.19 | M3 | P/M3 | 5017.9 | 5971.301
13.11.1 | Plaster (1:3)
| 8 | 1.1 |  | 0.35 | 3.08 | 12.32 | M2 | P/M2 | 164.3 | 2024.176
8 | Carriage 10% of item 9 | [8 empty] | 3683.7877
9A/ 18.48 | Providing and placing on terrace (at all floor levels) polyethylene water storage tank, ISI : 12701 marked, with cover and suitable locking arrangement and making necessary holes for inlet, outlet and overflow pipes but without fittings and the base support for tank. |  |  |  |  | 10000 | Ltrs. | P/Ltr. | 9.7 | 97000
9B | Providing and fixing MS clamp consisting of 32mm X 5mm thick two no. rings spaced suitably distance apart. | [7 empty] | LS | 3000
10A | Supplying all materials labours & fixing 50mm dia. G.I pipe for using as filling station etc. All as per direction of E/I
| 50mm dia. Pipe from distribution main |  |  |  |  | 3.5 | M | P/M | 572.6 | 2004.1
10B | Providing and fixing G.I fittings
| 80mmx80mmx50mm dia Tee |  |  |  |  | 1 | No | Each | 225 | 225
| 50mm dia bend |  |  |  |  | 3 | No | Each | 175 | 525
| Providing and fixing gun metal gate valve with C.I. wheel of approved quality (screwed end) :50mm nominal dia. |  |  |  |  | 1 | N | Each | 811.4 | 811.4
10C | Providing designation of 100 A brick Flat soling joints filled with local sand including cost of watering, taxes & royalty all complete as per specification & direction of E/I.
|  | 1 | 0.45 | 0.45 |  | 0.2025 | m2 | p/m2 | 283.3 | 57.3683
11 | Providing and fixing PTMT extension nipple for water tank pipe, fittings of approved quality and colour.
| 50mm dia |  |  |  |  | 2 | Nos. | each | 300 | 600
| 63mm dia |  |  |  |  | 1 | No. | each | 350 | 350
| 80 mm dia |  |  |  |  | 1 | No. | each | 550 | 550
| Sub Total of Part - I | [8 empty] | 0
Part - II
12 | Providing and laying High Density Polyethyene pipe (HDPE pipe) of 20 mm to 225 mm OD and pressure 6.0 Kg/cm2 and 10 Kg/cm2 sutable for water supply which is available in all standard, like ISI-4984/1995 and various grades like PE-80, PE-100 including required specials. Rates are inclusive of , all taxes and duties (Exise duty @12.50% &CST @2% against Form 'C'), labour cess, contractor profit and overhead charges all complete as per direction of Engineer-in-charge.
12A | HDPE pipe of materials grade PE100- PN10 (dia in mm)
| 110mm dia Pipe |  |  |  |  | 0 | M | P/M | 646.25 | 0
| 90mm dia Pipe |  |  |  |  | 100 | M | P/M | 437.96 | 43796
| 75mm dia Pipe |  |  |  |  | 200 | M | P/M | 306.31 | 61262
| 63mm dia Pipe |  |  |  |  | 300 | M | P/M | 218.62 | 65586
13B | HDPE pipe of materials grade PE100- PN8 (dia in mm)
| 50 mm dia Pipe |  |  |  |  | 300 | M | P/M | 116.25 | 34875
| 40mm dia Pipe |  |  |  |  | 300 | M | P/M | 76.53 | 22959
13C | Providing all materials labours tools, fittings , specials and tackles for fitting, jointing and connecting HDPE pipes. (5% of the cost of the HDPE pipe .) | [8 empty] | 11423.9
| Sub Total Of Part (II) | [8 empty] | 0
| Grand Total | [8 empty] | 773422.7985
JE |  |  |  | AE |  |  |  |  | Executive Engineer
P. H. Division, Hajipur.

## Jurawanpur 10B (hidden)
Sub Estimate no. - 03
Jurawanpur Ward No. :- 10B
WATER SUPPLY DISTRIBUTION SYSTEM
S.N. | Particulars |  |  |  |  | Quantity |  | Unit | Rate | Amount
1/ 2.8 | Earthwork in excavation over areas (exceeding 30 cm in depth 1.5 in width as well as 10 sqm on plan) including disposal of excavated earth lead upto 50m and lift upto 1.5m, disposal earth to be levelled and neatly dressed.
| 110mm dia Pipe | 0 | 0.3 | 1.1 | = | 0 | [6 empty] | 152000
| 90mm dia Pipe | 200 | 0.3 | 1.1 | = | 66 | [6 empty] | 152000
| 75mm dia Pipe | 400 | 0.3 | 1.1 | = | 132
| 63mm dia Pipe | 500 | 0.3 | 1.1 | = | 165 | [6 empty] | 152000
| 50 mm dia Pipe | 450 | 0.3 | 1.1 | = | 148.5
| 40mm dia Pipe | 450 | 0.3 | 1.1 | = | 148.5
|  | 2000 |  |  |  | 660 | M3
| Add 5% extra for fittings = |  |  |  |  | 33 | M3
[6 empty] | 693 | M3 | P/M3 | 360.7 | 249965.1
2/ 2.26 | Filling available excavated earth (excluding rock) in trenches, plinth, sides of foundations etc. in layers not exceeding 20cm in depth, consolidating each deposited layer by ramming and watering, lead up to 50 m and lift upto 1.5 m. |  |  |  |  | 679.14 | M3 | P/M3 | 123.9 | 84145.446
3/ 15.2.1 | Demolishing cement concrete manually/by mechanical means including disposal of material within 50 metres lead as per direction of Engineer - in - charge. | [8 empty] | 26214.3
1:3:6 or richer mix
|  | 600 | 0.3 | 0.15 | = | 27 | M3 | P/M3 | 970.9
4/ 4.1.3 | Providing and laying in position cement concrete of specified grade excluding the cost of centering and shuttering all work upto plinth |  |  |  |  | 27 | M3 | P/M3 | 3998.1 | 107948.7 | 4969
1:2:4 (1 cement: 2 coarse sand : 4 graded stone aggregate 40mm nominal size)
5 | Carriage of the following materials from quarry to work site including loading, unloading and staking at work site as per specification & direction of E/I.
| Coarse Sand (44Km Pucca & 1Km Kaccha Carriage) |  |  |  |  | 12.42 | M3 | P/M3 | 1160.62 | 14414.9004
| Stone chips (195Km Pucca & 5Km unsurafced Carriage) |  |  |  |  | 24.84 | M3 | P/M3 | 4291.17 | 106592.6628
6A/ 18.12 | Providing and fixing G.I.Pipes complete with G.I. Fittings including trenching and refilling etc.
18.12.6 | 50mm dia G.I.Pipe from T/well to PVC Tank |  |  |  |  | 14 | M | P/M | 572.6 | 8016.4 |  |  |  | 611.3975
18.12.8 | 80mm dia G.I.Pipe from PVC Tank to Distribution main |  |  |  |  | 14 | M | P/M | 818.2 | 11454.8
18.12.7 | 65mm dia G.I.Pipe for wash out |  |  |  |  | 12 | M | P/M | 667.7 | 8012.4
7A/ 18.31.1.1 | P/F C.I sluice Valve (with Cap) complete with bolts,nuts,rubber insertions etc
6B/ | Providing and fixing brass gate valve with C.I. wheel of approved quality (screwed end).
| 80mm dia Pipe |  |  |  |  | 2 | Nos. | Each | 2227.6 | 4455.2
| 65mm dia Pipe |  |  |  |  | 1 | Nos. | Each | 1490.7 | 1490.7
| 50mm dia Pipe |  |  |  |  | 1 | Nos. | Each | 878.2 | 878.2
7/ 18.33 | Constructing masonry Chamber 60x60x75 cm inside, in brick work in cement mortar 1:4 (1 cement : 4 coarse sand) for sluice valve,with C.I. surface box 100mm top diameter, 160 mm bottom diameter and 180 mm deep ( inside) with chained lid and RCC top slab 1:2:4 mix (1 cement : 2 coarse sand : 4 graded stone aggregate 20mm nominal size ) , necessary excavation, foundation concrete 1:5:10(1 cement : 5 fine sand : 10 graded stone aggregate 40 mm nominalsize) and inside plastering with cement mortar 1:3 (1 cement : 3coarse sand) 12 mm thick, finished with a floating coat of neat cement complete as per standard specifications & direction of E/I. |  |  |  |  | 4 | Nos. | Each | 7210.6 | 28842.4
| Work for additional depth | [10 empty] | 4.9933
Brick work (1:4) in foundation
| 2 | 1.1 | 0.25 | 0.35 | 0.1925
| 2 | 0.6 | 0.25 | 0.35 | 0.105
6.1.12 |  |  |  |  | 0.2975 | 1.19 | M3 | P/M3 | 5017.9 | 5971.301
13.11.1 | Plaster (1:3)
| 8 | 1.1 |  | 0.35 | 3.08 | 12.32 | M2 | P/M2 | 164.3 | 2024.176
8 | Carriage 10% of item 9 | [8 empty] | 3683.7877
9A/ 18.48 | Providing and placing on terrace (at all floor levels) polyethylene water storage tank, ISI : 12701 marked, with cover and suitable locking arrangement and making necessary holes for inlet, outlet and overflow pipes but without fittings and the base support for tank. |  |  |  |  | 10000 | Ltrs. | P/Ltr. | 9.7 | 97000
9B | Providing and fixing MS clamp consisting of 32mm X 5mm thick two no. rings spaced suitably distance apart. | [7 empty] | LS | 3000
10A | Supplying all materials labours & fixing 50mm dia. G.I pipe for using as filling station etc. All as per direction of E/I
| 50mm dia. Pipe from distribution main |  |  |  |  | 3.5 | M | P/M | 572.6 | 2004.1
10B | Providing and fixing G.I fittings
| 80mmx80mmx50mm dia Tee |  |  |  |  | 1 | No | Each | 225 | 225
| 50mm dia bend |  |  |  |  | 3 | No | Each | 175 | 525
| Providing and fixing gun metal gate valve with C.I. wheel of approved quality (screwed end) :50mm nominal dia. |  |  |  |  | 1 | N | Each | 811.4 | 811.4
10C | Providing designation of 100 A brick Flat soling joints filled with local sand including cost of watering, taxes & royalty all complete as per specification & direction of E/I.
|  | 1 | 0.45 | 0.45 |  | 0.2025 | m2 | p/m2 | 283.3 | 57.3683
11 | Providing and fixing PTMT extension nipple for water tank pipe, fittings of approved quality and colour.
| 50mm dia |  |  |  |  | 2 | Nos. | each | 300 | 600
| 63mm dia |  |  |  |  | 1 | No. | each | 350 | 350
| 80 mm dia |  |  |  |  | 1 | No. | each | 550 | 550
| Sub Total of Part - I | [8 empty] | 0
Part - II
12 | Providing and laying High Density Polyethyene pipe (HDPE pipe) of 20 mm to 225 mm OD and pressure 6.0 Kg/cm2 and 10 Kg/cm2 sutable for water supply which is available in all standard, like ISI-4984/1995 and various grades like PE-80, PE-100 including required specials. Rates are inclusive of , all taxes and duties (Exise duty @12.50% &CST @2% against Form 'C'), labour cess, contractor profit and overhead charges all complete as per direction of Engineer-in-charge.
12A | HDPE pipe of materials grade PE100- PN10 (dia in mm)
| 110mm dia Pipe |  |  |  |  | 0 | M | P/M | 646.25 | 0
| 90mm dia Pipe |  |  |  |  | 200 | M | P/M | 437.96 | 87592
| 75mm dia Pipe |  |  |  |  | 400 | M | P/M | 306.31 | 122524
| 63mm dia Pipe |  |  |  |  | 500 | M | P/M | 218.62 | 109310
13B | HDPE pipe of materials grade PE100- PN8 (dia in mm)
| 50 mm dia Pipe |  |  |  |  | 450 | M | P/M | 116.25 | 52312.5
| 40mm dia Pipe |  |  |  |  | 450 | M | P/M | 76.53 | 34438.5
13C | Providing all materials labours tools, fittings , specials and tackles for fitting, jointing and connecting HDPE pipes. (5% of the cost of the HDPE pipe .) | [8 empty] | 20308.85
| Sub Total Of Part (II) | [8 empty] | 0
| Grand Total | [8 empty] | 1195719.1922
JE |  |  |  | AE |  |  |  |  | Executive Engineer
P. H. Division, Hajipur.

## Jurawanpur 12b (hidden)
Sub Estimate no. - 03
Jurawanpur Ward No. :- 12B
WATER SUPPLY DISTRIBUTION SYSTEM
S.N. | Particulars |  |  |  |  | Quantity |  | Unit | Rate | Amount
1/ 2.8 | Earthwork in excavation over areas (exceeding 30 cm in depth 1.5 in width as well as 10 sqm on plan) including disposal of excavated earth lead upto 50m and lift upto 1.5m, disposal earth to be levelled and neatly dressed.
| 110mm dia Pipe | 0 | 0.3 | 1.1 | = | 0 | [6 empty] | 152000
| 90mm dia Pipe | 200 | 0.3 | 1.1 | = | 66 | [6 empty] | 152000
| 75mm dia Pipe | 400 | 0.3 | 1.1 | = | 132
| 63mm dia Pipe | 500 | 0.3 | 1.1 | = | 165 | [6 empty] | 152000
| 50 mm dia Pipe | 450 | 0.3 | 1.1 | = | 148.5
| 40mm dia Pipe | 450 | 0.3 | 1.1 | = | 148.5
|  | 2000 |  |  |  | 660 | M3
| Add 5% extra for fittings = |  |  |  |  | 33 | M3
[6 empty] | 693 | M3 | P/M3 | 360.7 | 249965.1
2/ 2.26 | Filling available excavated earth (excluding rock) in trenches, plinth, sides of foundations etc. in layers not exceeding 20cm in depth, consolidating each deposited layer by ramming and watering, lead up to 50 m and lift upto 1.5 m. |  |  |  |  | 679.14 | M3 | P/M3 | 123.9 | 84145.446
3/ 15.2.1 | Demolishing cement concrete manually/by mechanical means including disposal of material within 50 metres lead as per direction of Engineer - in - charge. | [8 empty] | 26214.3
1:3:6 or richer mix
|  | 600 | 0.3 | 0.15 | = | 27 | M3 | P/M3 | 970.9
4/ 4.1.3 | Providing and laying in position cement concrete of specified grade excluding the cost of centering and shuttering all work upto plinth |  |  |  |  | 27 | M3 | P/M3 | 3998.1 | 107948.7 | 4969
1:2:4 (1 cement: 2 coarse sand : 4 graded stone aggregate 40mm nominal size)
5 | Carriage of the following materials from quarry to work site including loading, unloading and staking at work site as per specification & direction of E/I.
| Coarse Sand (44Km Pucca & 1Km Kaccha Carriage) |  |  |  |  | 12.42 | M3 | P/M3 | 1160.62 | 14414.9004
| Stone chips (195Km Pucca & 5Km unsurafced Carriage) |  |  |  |  | 24.84 | M3 | P/M3 | 4291.17 | 106592.6628
6A/ 18.12 | Providing and fixing G.I.Pipes complete with G.I. Fittings including trenching and refilling etc.
18.12.6 | 50mm dia G.I.Pipe from T/well to PVC Tank |  |  |  |  | 14 | M | P/M | 572.6 | 8016.4 |  |  |  | 611.3975
18.12.8 | 80mm dia G.I.Pipe from PVC Tank to Distribution main |  |  |  |  | 14 | M | P/M | 818.2 | 11454.8
18.12.7 | 65mm dia G.I.Pipe for wash out |  |  |  |  | 12 | M | P/M | 667.7 | 8012.4
7A/ 18.31.1.1 | P/F C.I sluice Valve (with Cap) complete with bolts,nuts,rubber insertions etc
6B/ | Providing and fixing brass gate valve with C.I. wheel of approved quality (screwed end).
| 80mm dia Pipe |  |  |  |  | 2 | Nos. | Each | 2227.6 | 4455.2
| 65mm dia Pipe |  |  |  |  | 1 | Nos. | Each | 1490.7 | 1490.7
| 50mm dia Pipe |  |  |  |  | 1 | Nos. | Each | 878.2 | 878.2
7/ 18.33 | Constructing masonry Chamber 60x60x75 cm inside, in brick work in cement mortar 1:4 (1 cement : 4 coarse sand) for sluice valve,with C.I. surface box 100mm top diameter, 160 mm bottom diameter and 180 mm deep ( inside) with chained lid and RCC top slab 1:2:4 mix (1 cement : 2 coarse sand : 4 graded stone aggregate 20mm nominal size ) , necessary excavation, foundation concrete 1:5:10(1 cement : 5 fine sand : 10 graded stone aggregate 40 mm nominalsize) and inside plastering with cement mortar 1:3 (1 cement : 3coarse sand) 12 mm thick, finished with a floating coat of neat cement complete as per standard specifications & direction of E/I. |  |  |  |  | 4 | Nos. | Each | 7210.6 | 28842.4
| Work for additional depth | [10 empty] | 4.9933
Brick work (1:4) in foundation
| 2 | 1.1 | 0.25 | 0.35 | 0.1925
| 2 | 0.6 | 0.25 | 0.35 | 0.105
6.1.12 |  |  |  |  | 0.2975 | 1.19 | M3 | P/M3 | 5017.9 | 5971.301
13.11.1 | Plaster (1:3)
| 8 | 1.1 |  | 0.35 | 3.08 | 12.32 | M2 | P/M2 | 164.3 | 2024.176
8 | Carriage 10% of item 9 | [8 empty] | 3683.7877
9A/ 18.48 | Providing and placing on terrace (at all floor levels) polyethylene water storage tank, ISI : 12701 marked, with cover and suitable locking arrangement and making necessary holes for inlet, outlet and overflow pipes but without fittings and the base support for tank. |  |  |  |  | 10000 | Ltrs. | P/Ltr. | 9.7 | 97000
9B | Providing and fixing MS clamp consisting of 32mm X 5mm thick two no. rings spaced suitably distance apart. | [7 empty] | LS | 3000
10A | Supplying all materials labours & fixing 50mm dia. G.I pipe for using as filling station etc. All as per direction of E/I
| 50mm dia. Pipe from distribution main |  |  |  |  | 3.5 | M | P/M | 572.6 | 2004.1
10B | Providing and fixing G.I fittings
| 80mmx80mmx50mm dia Tee |  |  |  |  | 1 | No | Each | 225 | 225
| 50mm dia bend |  |  |  |  | 3 | No | Each | 175 | 525
| Providing and fixing gun metal gate valve with C.I. wheel of approved quality (screwed end) :50mm nominal dia. |  |  |  |  | 1 | N | Each | 811.4 | 811.4
10C | Providing designation of 100 A brick Flat soling joints filled with local sand including cost of watering, taxes & royalty all complete as per specification & direction of E/I.
|  | 1 | 0.45 | 0.45 |  | 0.2025 | m2 | p/m2 | 283.3 | 57.3683
11 | Providing and fixing PTMT extension nipple for water tank pipe, fittings of approved quality and colour.
| 50mm dia |  |  |  |  | 2 | Nos. | each | 300 | 600
| 63mm dia |  |  |  |  | 1 | No. | each | 350 | 350
| 80 mm dia |  |  |  |  | 1 | No. | each | 550 | 550
| Sub Total of Part - I | [8 empty] | 0
Part - II
12 | Providing and laying High Density Polyethyene pipe (HDPE pipe) of 20 mm to 225 mm OD and pressure 6.0 Kg/cm2 and 10 Kg/cm2 sutable for water supply which is available in all standard, like ISI-4984/1995 and various grades like PE-80, PE-100 including required specials. Rates are inclusive of , all taxes and duties (Exise duty @12.50% &CST @2% against Form 'C'), labour cess, contractor profit and overhead charges all complete as per direction of Engineer-in-charge.
12A | HDPE pipe of materials grade PE100- PN10 (dia in mm)
| 110mm dia Pipe |  |  |  |  | 0 | M | P/M | 646.25 | 0
| 90mm dia Pipe |  |  |  |  | 200 | M | P/M | 437.96 | 87592
| 75mm dia Pipe |  |  |  |  | 400 | M | P/M | 306.31 | 122524
| 63mm dia Pipe |  |  |  |  | 500 | M | P/M | 218.62 | 109310
13B | HDPE pipe of materials grade PE100- PN8 (dia in mm)
| 50 mm dia Pipe |  |  |  |  | 450 | M | P/M | 116.25 | 52312.5
| 40mm dia Pipe |  |  |  |  | 450 | M | P/M | 76.53 | 34438.5
13C | Providing all materials labours tools, fittings , specials and tackles for fitting, jointing and connecting HDPE pipes. (5% of the cost of the HDPE pipe .) | [8 empty] | 20308.85
| Sub Total Of Part (II) | [8 empty] | 0
| Grand Total | [8 empty] | 1195719.1922
JE |  |  |  | AE |  |  |  |  | Executive Engineer
P. H. Division, Hajipur.

## Jurawanpur 13B (hidden)
Sub Estimate no. - 03
Jurawanpur Ward No. :- 13B
WATER SUPPLY DISTRIBUTION SYSTEM
S.N. | Particulars |  |  |  |  | Quantity |  | Unit | Rate | Amount
1/ 2.8 | Earthwork in excavation over areas (exceeding 30 cm in depth 1.5 in width as well as 10 sqm on plan) including disposal of excavated earth lead upto 50m and lift upto 1.5m, disposal earth to be levelled and neatly dressed.
| 110mm dia Pipe | 0 | 0.3 | 1.1 | = | 0 | [6 empty] | 152000
| 90mm dia Pipe | 200 | 0.3 | 1.1 | = | 66 | [6 empty] | 152000
| 75mm dia Pipe | 500 | 0.3 | 1.1 | = | 165
| 63mm dia Pipe | 600 | 0.3 | 1.1 | = | 198 | [6 empty] | 152000
| 50 mm dia Pipe | 450 | 0.3 | 1.1 | = | 148.5
| 40mm dia Pipe | 450 | 0.3 | 1.1 | = | 148.5
|  | 2200 |  |  |  | 726 | M3
| Add 5% extra for fittings = |  |  |  |  | 36.3 | M3
[6 empty] | 762.3 | M3 | P/M3 | 360.7 | 274961.61
2/ 2.26 | Filling available excavated earth (excluding rock) in trenches, plinth, sides of foundations etc. in layers not exceeding 20cm in depth, consolidating each deposited layer by ramming and watering, lead up to 50 m and lift upto 1.5 m. |  |  |  |  | 747.054 | M3 | P/M3 | 123.9 | 92559.9906
3/ 15.2.1 | Demolishing cement concrete manually/by mechanical means including disposal of material within 50 metres lead as per direction of Engineer - in - charge. | [8 empty] | 28835.73
1:3:6 or richer mix
|  | 660 | 0.3 | 0.15 | = | 29.7 | M3 | P/M3 | 970.9
4/ 4.1.3 | Providing and laying in position cement concrete of specified grade excluding the cost of centering and shuttering all work upto plinth |  |  |  |  | 29.7 | M3 | P/M3 | 3998.1 | 118743.57 | 4969
1:2:4 (1 cement: 2 coarse sand : 4 graded stone aggregate 40mm nominal size)
5 | Carriage of the following materials from quarry to work site including loading, unloading and staking at work site as per specification & direction of E/I.
| Coarse Sand (44Km Pucca & 1Km Kaccha Carriage) |  |  |  |  | 13.662 | M3 | P/M3 | 1160.62 | 15856.3904
| Stone chips (195Km Pucca & 5Km unsurafced Carriage) |  |  |  |  | 27.324 | M3 | P/M3 | 4291.17 | 117251.9291
6A/ 18.12 | Providing and fixing G.I.Pipes complete with G.I. Fittings including trenching and refilling etc.
18.12.6 | 50mm dia G.I.Pipe from T/well to PVC Tank |  |  |  |  | 14 | M | P/M | 572.6 | 8016.4 |  |  |  | 611.3975
18.12.8 | 80mm dia G.I.Pipe from PVC Tank to Distribution main |  |  |  |  | 14 | M | P/M | 818.2 | 11454.8
18.12.7 | 65mm dia G.I.Pipe for wash out |  |  |  |  | 12 | M | P/M | 667.7 | 8012.4
7A/ 18.31.1.1 | P/F C.I sluice Valve (with Cap) complete with bolts,nuts,rubber insertions etc
6B/ | Providing and fixing brass gate valve with C.I. wheel of approved quality (screwed end).
| 80mm dia Pipe |  |  |  |  | 2 | Nos. | Each | 2227.6 | 4455.2
| 65mm dia Pipe |  |  |  |  | 1 | Nos. | Each | 1490.7 | 1490.7
| 50mm dia Pipe |  |  |  |  | 1 | Nos. | Each | 878.2 | 878.2
7/ 18.33 | Constructing masonry Chamber 60x60x75 cm inside, in brick work in cement mortar 1:4 (1 cement : 4 coarse sand) for sluice valve,with C.I. surface box 100mm top diameter, 160 mm bottom diameter and 180 mm deep ( inside) with chained lid and RCC top slab 1:2:4 mix (1 cement : 2 coarse sand : 4 graded stone aggregate 20mm nominal size ) , necessary excavation, foundation concrete 1:5:10(1 cement : 5 fine sand : 10 graded stone aggregate 40 mm nominalsize) and inside plastering with cement mortar 1:3 (1 cement : 3coarse sand) 12 mm thick, finished with a floating coat of neat cement complete as per standard specifications & direction of E/I. |  |  |  |  | 4 | Nos. | Each | 7210.6 | 28842.4
| Work for additional depth | [10 empty] | 4.9933
Brick work (1:4) in foundation
| 2 | 1.1 | 0.25 | 0.35 | 0.1925
| 2 | 0.6 | 0.25 | 0.35 | 0.105
6.1.12 |  |  |  |  | 0.2975 | 1.19 | M3 | P/M3 | 5017.9 | 5971.301
13.11.1 | Plaster (1:3)
| 8 | 1.1 |  | 0.35 | 3.08 | 12.32 | M2 | P/M2 | 164.3 | 2024.176
8 | Carriage 10% of item 9 | [8 empty] | 3683.7877
9A/ 18.48 | Providing and placing on terrace (at all floor levels) polyethylene water storage tank, ISI : 12701 marked, with cover and suitable locking arrangement and making necessary holes for inlet, outlet and overflow pipes but without fittings and the base support for tank. |  |  |  |  | 10000 | Ltrs. | P/Ltr. | 9.7 | 97000
9B | Providing and fixing MS clamp consisting of 32mm X 5mm thick two no. rings spaced suitably distance apart. | [7 empty] | LS | 3000
10A | Supplying all materials labours & fixing 50mm dia. G.I pipe for using as filling station etc. All as per direction of E/I
| 50mm dia. Pipe from distribution main |  |  |  |  | 3.5 | M | P/M | 572.6 | 2004.1
10B | Providing and fixing G.I fittings
| 80mmx80mmx50mm dia Tee |  |  |  |  | 1 | No | Each | 225 | 225
| 50mm dia bend |  |  |  |  | 3 | No | Each | 175 | 525
| Providing and fixing gun metal gate valve with C.I. wheel of approved quality (screwed end) :50mm nominal dia. |  |  |  |  | 1 | N | Each | 811.4 | 811.4
10C | Providing designation of 100 A brick Flat soling joints filled with local sand including cost of watering, taxes & royalty all complete as per specification & direction of E/I.
|  | 1 | 0.45 | 0.45 |  | 0.2025 | m2 | p/m2 | 283.3 | 57.3683
11 | Providing and fixing PTMT extension nipple for water tank pipe, fittings of approved quality and colour.
| 50mm dia |  |  |  |  | 2 | Nos. | each | 300 | 600
| 63mm dia |  |  |  |  | 1 | No. | each | 350 | 350
| 80 mm dia |  |  |  |  | 1 | No. | each | 550 | 550
| Sub Total of Part - I | [8 empty] | 0
Part - II
12 | Providing and laying High Density Polyethyene pipe (HDPE pipe) of 20 mm to 225 mm OD and pressure 6.0 Kg/cm2 and 10 Kg/cm2 sutable for water supply which is available in all standard, like ISI-4984/1995 and various grades like PE-80, PE-100 including required specials. Rates are inclusive of , all taxes and duties (Exise duty @12.50% &CST @2% against Form 'C'), labour cess, contractor profit and overhead charges all complete as per direction of Engineer-in-charge.
12A | HDPE pipe of materials grade PE100- PN10 (dia in mm)
| 110mm dia Pipe |  |  |  |  | 0 | M | P/M | 646.25 | 0
| 90mm dia Pipe |  |  |  |  | 200 | M | P/M | 437.96 | 87592
| 75mm dia Pipe |  |  |  |  | 500 | M | P/M | 306.31 | 153155
| 63mm dia Pipe |  |  |  |  | 600 | M | P/M | 218.62 | 131172
13B | HDPE pipe of materials grade PE100- PN8 (dia in mm)
| 50 mm dia Pipe |  |  |  |  | 450 | M | P/M | 116.25 | 52312.5
| 40mm dia Pipe |  |  |  |  | 450 | M | P/M | 76.53 | 34438.5
13C | Providing all materials labours tools, fittings , specials and tackles for fitting, jointing and connecting HDPE pipes. (5% of the cost of the HDPE pipe .) | [8 empty] | 22933.5
| Sub Total Of Part (II) | [8 empty] | 0
| Grand Total | [8 empty] | 1309764.9531
JE |  |  |  | AE |  |  |  |  | Executive Engineer
P. H. Division, Hajipur.

## Boring1
(Sub Estimate - 1)
For HH-200, 225, 250
CONSTRUCTION OF 150MM X 100MM DIA & 125M DEEP TUBE WELL
S.No. | Description | Qty. |  | Unit | Rate | Amount
1 | Boring/drilling bore well of required dia for casing/strainer pipe, by suitable method prescribed in IS: 2800 (part I), including collecting samples from different strata, preparing and submitting strata chart/ bore log, including hire & running charges of all equipments, tools, plants & machineries required for the job, all complete as per direction of Engineer -in-charge, upto 150 metre depth below ground level. (All types of soil)
24.1.1.2 | (a) 350mm dia bore from G.L. to 30.0M | 30 | M | P/M | 532.4 | 15972
24.1.1.1 | (b) 300mm dia bore from 30.0 m to 60.0M | 30 | M | P/M | 486.8 | 14604
| (c) 300mm dia bore from 60M to 90.0M | 30 | M | P/M | 486.8 | 14604
24.2.1 | (d) 300mm dia bore from 90.0M to 150.0M | 35 | M | P/M | 567.9 | 19876.5
2A | Supplying, assembling, lowering and fixing in vertical position in bore well, unplasticized PVC (UPVC) medium well casing (CM) pipe of required dia, conforming to IS: 12818, including required hire and labour charges, fittings & accessories etc. all complete, for all depths, as per direction of Engineer -in-charge.
24.3.2 | (a) 150 mm nominal size dia | 30 | M | P/M | 660.1 | 19803
24.3.1 | (b) 100 mm nominal size dia | 60 | M | P/M | 546.1 | 32766
2B | Supplying, assembling, lowering and fixing in vertical position in bore well unplasticized PVC (UPVC) medium well screen (RMS) pipes with ribs, conforming to IS: 12818, including hire & labour charges, fittings & accessories etc. all complete, for all depths, as per direction of Engineer-in-charge.
24.4.1 | 100 mm nominal size dia | 30 | M | P/M | 573.1 | 17193
3 | Supplying the following fittings & fixing the same in position as per approved lowering assembly and strata chart including providing all equipments and welding the same on process of lowering the assay etc. all complete as per S/D of E/I.
24.13.2 | (a) 150 mm dia well cap | 1 | No. | Each | 210.7 | 210.7
24.14.2 | (b) 150 mm dia M.S. Clamp 1.6 M long (one Pair) | 1 | No. | Each | 1531.4 | 1531.4
Rate as per cost index @15.06% | (c) 150 mm dia center guide | 4 | Nos. | Each | 150 | 600
| (d) 100 mm dia center guide | 6 | Nos. | Each | 100 | 600
| (e) 150 mm x 100 mm dia 6mm wall thickness MS reducer | 1 | No. | Each | 500 | 500
24.15.1 | (f) 100mm dia & 6mm thick M.S. well shoe plug | 1 | No. | Each | 228.3 | 228.3
4a 24.8 | Gravel packing in tubewell construction in accordance with IS:4097,including providing gravel fine/ medium/ coarse, in required grading & sizes as per actual requirement, all complete as per direction of Engineer-in-charge. | 9 | M3 | P/M3 | 1343.2 | 12088.8
4b | Carriage of Pea Gravel from Dalbhumigarh to Patna (taken av distance 395+ 5km.) {8/5 (395 x 11.2+ 5 X 27.2) + 195.1}*1.01 | 9 | M3 | P/M3 | 10062.31 | 90560.79 | 7566.011 | 2496.3 | 7566.011
5 24.12 | Development of tube well in accordance with IS : 2800 (part I) and IS: 11189, to establish maximum rate of usable water yield without sand content (beyond permissible limit), with required capacity air compressor, running the compressor for required time till well is fully develo ped, measuring yield of well by "V" notch method or any other approved method, measuring static level & draw down etc. by step draw down method, collecting water sampl &getting tested in approved laboratory, disinfection of tubewell, all complete,including hire & labour charges of air compressor, tools & accessories etc., all as per requirement and direction of Engineer-in-charge. | 24 | Hrs. | P/H | 916.8 | 22003.2
6 Rate as per cost index @15.06% | Transportation of drilling plants, developing equipments & all other required tools and M/c by and suitable mechanical means including all cost of loading, unloading, placing at work site and back after completion of work as per S/D of E/I | 1 | No. | Each | 9200 | 9200
7 Rate as per cost index @15.06% | Supplying all materials and labours for arrangement for additional water required during the drilling period for 70 Hrs & site clearance & leveling etc. And providing the soap duster etc. to staff engaged in drilling etc. all complete work as per specification & direction of E.I. | 1 | No. | Each | 7000 | 7000
|  | TOTAL |  |  |  | 279341.69
[5 empty] | say | 279342
| JE AE | Executive Engineer,
P. H. Division, Hajipur.

## Chamber TW
(Sub Estimate - 2)
Chamber for TW
Supplying materials, labours and constructing chamber of following dimension having 250mm thick wall in C.M. (1:4) in cluding 12mm C.P. (1:3) with punning inside, R.C.C. cover slab with C.I. Surface box , 20mm dia foot rest at 150mm interval 10mm dia lifting ring etc. all complete.
| SIZE | 1 | M | x | 1 | M | x | 0.75 | M deep
S.O.R. No. | Particulars | No. | L | W | H | Qty. |  | Unit | Rate | Amount
1 | Earth work in excavation | 1 | 1.75 | 1.75 | 1 | 3.0625 | M3 | P/M3 | 360.7 | 1104.6437 | 1104.6437 | 0 | 360.7
2.8 | [11 empty] | 0
2 | Sand filling | 1 | 1.75 | 1.75 | 0.075 | 0.22969 | M3 | P/M3 | 287.3 | 65.9892 | 65.9892 | 0 | 287.3
2.28 | [11 empty] | 0
3 | Brick flat soling | 1 | 1.75 | 1.75 |  | 3.0625 | M2 | P/M2 | 283.3 | 867.6063 | 867.6063 | 0 | 283.3
11.72 | [11 empty] | 0
4 | P.C.C. (1:2:4) in foundation | 1 | 1.75 | 1.75 | 0.1 | 0.30625 | M3 |  |  |  |  | 0
4.1.3 | [11 empty] | 0
[6 empty] | 0.30625 | M3 | P/M3 | 3998.1 | 1224.4181 | 1224.4181 | 0 | 3998.1
5 | B/Work in (1:4) C.M. | 2 | 2.5 | 0.25 | 0.75 | 0.9375 | M3 | P/M3 | 5017.9 | 4704.2812 | 4704.2812 | 0 | 5017.9
6.1.12/1 | [11 empty] | 0
6 | R.C.C. Cover slab(1:1.5:3) | 1 | 1.5 | 1.5 | 0.15 | 0.3375 | M3 | P/M3 | 5670 | 1913.625 | 1913.625 | 0 | 5670
5.2.2 & 5.9.3 | [11 empty] | 0
| shuttering | 2 | 1.5 | 1.5 | 0.15 | 0.9 | M2 | P/M2 | 437.5 | 393.75 | 1378.125 | -984.375 | 437.5
7 | C.P. (1:3) with 5% Cico & neat cement | [10 empty] | 0
13.17.1 | Internal face | 2 | 1 | 1 | 1 | 4 | M2 |  |  |  |  | 0
| Bed surface | 1 | 1 | 1 |  | 1 | M2 |  |  |  |  | 0
+13.36.1 | [5 empty] | 5 | M2 | P/M2 | 203.6 | 1018 | 1063 | -45 | 212.6
0
8 | C.P. (1:4) out side of wall | 2 | 1.5 | 1.5 | 0.75 | 0.9 | M2 | P/M2 | 152.9 | 137.61 | 688.05 | -550.44 | 152.9
. 13.11.2 | [11 empty] | 0
9 | 8mm dia T.S. Rod | [10 empty] | 0
5.22.7A | [11 empty] | 0
|  | 0.3375 | M3 x | 70 | Kg/ M3 | 23.625 | Kg. | P/Kg | 94.5 | 2232.5625 | 2232.5625 | 0 | 94.5
10 | Lifting Ring of 10mm dia Rod |  |  |  |  | 4 | No. | Each | 45 | 180 | 240 | -60 | 60
[9 empty] | Total | 13842.4861 | 13977.4861 | -135
11 | Carriage of materials 5% | [8 empty] | 692.1243 | 698.8743 | -6.75
| Total | [8 empty] | 14534.6104 | 14676.3604 | -141.75
| Say | [8 empty] | 14535 | 15463 | -928
| JE |  |  | AE |  |  |  | Executive Engineer
P. H. Division, Hajipur

## moter new
Sub Est. No. 4
Estimate for supply, installation & commissioning of single phase 3 H.P submersible motor pump set with all accessories including extension of L.T. line from nearest source up-to pumping station.
Sl. No. | Particulars | Quantity |  | Unit | Rate | Amount
1 | 2 | 3 |  | 4 | 5 | 6 |  | 1.1506
1 | Supply Installation, commissioning and testing of single phase 3 H.P. submersible pump set having discharging capacity 3.35 lps at a total head of 35 meter(approx) of KSB/ Kirloskar or equivalent make with all accessories & fittings etc including loading unloading and transportation of the pump set to the work site with all required labour, materials, tools and tackles installation, testing & commissioning as per standards specifications and direction of E/I. | 1 | (one) job | p/job | 50250 | 50250
| (i) 50 mm dia x 3 mtrs long medium class G.I column pipe both end thread and one end socketed- 6(six)nos | [5 empty] | 42700 | 49130.62
| (ii) 1x3x2.5 mm2 flat copper conductor submersible cable -40 (forty) mtrs. | [6 empty] | 0
| (iii) 50 mm dia union socket- 1(one) no. | [6 empty] | 0
| (iv) 65 mm dia x 250 mm long G.I. nipple- 1 (one) no. | [6 empty] | 0
| (v) 50 mm dia G.I Elbow—1(One) no. | [6 empty] | 0
| (vi) 50 mm dia M.S. clamps—2(Two) Pairs. | [6 empty] | 0
| (vii) 50 mmx 250 mm long G.I nipple- 1(One) no. | [6 empty] | 0
| (viii) Tube well cap for T/Well – 1(one) no. | [6 empty] | 0
| (ix) 50 mm dia x 65 mm dia reducer socket –1(one) no. | [6 empty] | 0
2 | Supply Installation, commissioning and testing of floor mounted outdoor type L.T feeder pillar single phase starter controll pannel operated on 220 V, 3 phase , 50 c/s for 3 HP Submersible pump set made of MS sheet (minimum 2 mm thick) duly spray power coated painting with following accessories made of M.S sheet (minimum 2mm thick) duly spray powder coated painting with following accessories | [6 empty] | 0 | Supply Installation, commissioning and testing of floor mounted outdoor type L.T feeder pillar single phase starter controll pannel operated on 220 V, 3 phase , 50 c/s for 3 HP Submersible pump set made of MS sheet (minimum 2 mm thick) duly spray power coated painting with following accessories made of M.S sheet (minimum 2mm thick) duly spray powder coated painting with following accessories
| (i) 90-220 V range single phase7. 5 KVA automatic voltage stabilizer make- Sen & Pandit/ Vertex/ISI marked If any. 1 No. | [6 empty] | 0
| (ii) Suitable single phase starter control panel for above motor of BCH /L&Tmake – 1(one) no. | 1 | (one) job | p/job | 49000 | 49000 |  | 0
3 | Supplying & fitting 2.5 mm2 copper service cable from power point from nearest source up-to pumping station. | 20 | mtrs | P/Mt | 130 | 2600 | 45500 | 52352.3
4 | Providing all materials and labour required for doing earthing station with G.I earth pipe of 40 mm dia x 4.5 mtrs 20fts. long G.I pipe including accessories excavation of earth , providing masonry enclosure with cover plate having locking arrangement and watering pipe etc.with salt, charcoal,etc.as per IE & IS specification. | 1 | job | p/job | 3150 | 3150 | 130 | 149.578
[5 empty] | Total Rs. | 105000 | 2803 | 3225.1318
| Junior Engineer Assistant Engineer |  |  |  | Executive Engineer
P.H. Division, Hajipur

## Motor 3HP (hidden)
Sub Estimate no. - 04
Estimate for supply, installation & commissioning of single phase 3 H.P submersible motor pump set with all accessories including extension of L.T.line from nearest source up-to pumping station.(Included GST @ 18%)
S.N | Particulars | Qntity |  | Unit | Rate | Amount
1A | Supply Installation, commissioning and testing of single phase 3H.P. submersible pump set having discharging capacity 3 Ips at a total head of 30 meter(approx) of KSBj Kirloskaror equivalent make with all accessories& fittings etc including loading unloading and transportation of the pump set to the work site with all required labour, materials, tools and tackles installation, testing & (i) 50 mm dia x 3 mtrs long medium classG.I column pipe both end thread and one end socketed- 6(six)nos (ii) lx3x2,5 mm' flat copper conductor submersible cable -40 (forty) mtrs. (iii) 50 mm dia union socketlIonel no. (iv) 65 mm dia x 250 mm long G.!. nipple- 1(one) no. (v) 50 mm dia G.I Elbow-l(One) no. (vi) 50 mm dia M.S, clamps-2(Two) Pairs. (vii) 50 mmx 250 mm long G.I nipple- lIOnel no. (viii) Tube well cap for T/WelllIonel no. (ix) 50 ":l~ia x 65 mm dia | 1 | No | Each | 123900 | 123900
1B | Supply Installation, commissioning and testing of floor mounted outdoor type loT feeder pillar single phasestarter controll pannel operated on 220V, 3 phase, 50 cis for 3 HP Submersiblepump set made of MSsheet (minimum 2 mm thick) duly spray power coated painting with following accessoriesmade of M.Ssheet ( minimum 2mm thick) duly spray powder coated painting with following accessories (i) 90-220 V range single phase7. 5 KVA automatic voltage stabilizer make- Sen& Pandit/ Vertex/lSI marked If any. 1No. (ii) Suitablesinglephasestarter control panelfor abovemotor of BCH /L& Tmake-1(one) no. | 1 | No
1C | Supplying& fitting 2.5 mm' copper service cable from power point from nearest source up-toIpumping station .. | 20 | m
1D | Providing all materials and labour required lor doing earthing station with G.I earth pipe of 40 mm dia x 4.5 mtrs 20fts. long G.I pipe including accessories excavation of earth , providing masonry enclosure with Coverplate having locking arrangementand watering pipe etc.with salt, charcoal,etc.as per IE & IS specification | 1 | No |  |  |  | 10.2199
| Total |  |  |  |  | 123900
Executive Engineer P.H. Division, Hajipur

## House Connection
Sub Est. No. 5
Estimate for the work - New House service connection with Retrofitting
S.n | Description | Qty. | Unit | Rate | Amount
1 | Providing and fixing MDPE (PE 80 Grade compound) pipes PN-12.5 (12.5/sqcm) as per ISO 4427 and specification for water application rates are inclusive of taxes and duties (Exise duty @ 12.5% & CST @ 2% against form "C" labour cess contractor profot and over head charges all complete as per direction of Engineer in-charge
| MDPE pipe 20mm dia nominal bore | 6 | PM | 28.31 | 169.86
1-B | Providing and fixing G.I. pipes complete with G.I. fittings and clamps, i/c cutting and making good the walls etc. Internal work - Exposed on wall
18.10.1 | 15mm dia nominal bore | 1.7 | PM | 227.7 | 387.09
1-C | Providing and faying cement concreate in kerbs, steps and the like at or near ground level excluding the cost of centring, shuttering and finishing
4.4.1 | 1:2:4 (1 Cement :2 coarse sand :4 grade stone aggregate 20 mm nominal size)
| .25x.25x.10+0.100x0.100x1.70=0.023 | 0.023 | P/Cum | 3998.1 | 91.9563
12.78.2 | Providing and fixing of square pvc pipe with PHED engraved on wall of 100mm dia | 1.1 | PM | 257.5 | 283.25
2 | Earth work in excavation in foundation trenches or drains(not exceeding 1.5 m in width or 10 sqm on plan) including dressing of sides and ramming of bottoms, lift upto 1.5 m . including getting out the excavatedsoil and disposal of surplus excavated soil as directed, within a lead of 50 m.
2.8.1 | 6.00X.30X.60+0.30x0.30x0.60=1.134 | 1.134 | P/Cum | 360.7 | 409.0338
3 2.26 | Filling available excavated earth (excluding rock) in trenches, plinth, sides of foundations etc. in layers not exceeding 20 cm in depth: consolidating each deposited layer by ramming and watering lead | 1.06 | P/Cum | 123.9 | 131.334
4 | Providing and fixing brass ferrule with C.I. mouth cover including boring and tapping the main :
18.20.1 | 15mm nominal bore | 1 | Each | 301.6 | 301.6
(a) | Providing & fixing p.p clamp service saddle (Brass threaded) | 1 | Each | 400 | 400
(b) | Providing & fixing female adopter for adjoining the ferrule to MDPE pipe | 1 | Each | 75 | 75
(c) | Providing & fixing female elbow adopter for adjoining the ferrule to MDPE pipe to G.I pipe | 1 | Each | 50 | 50
5 | Providing and fixing brass bib cock of approved quality :
18.15.1 | 15 mm nominal bore | 1 | Each | 303.8 | 303.8
| Total Rs. |  |  |  | 2602.9241
| Say Rs. |  |  |  | 2600
| JE AE |  | Executive Engineer,
P. H. Division, Hajipur.

## HC_Hdpe (hidden)
Sub Est. No. 5
Estimate for the work - House service connection
SUB-ESTIMATE
S.No. | Description |  |  |  | Qty | Unit | Rate | Amount
1A | Providing and fixing MDPE (PE 80 GradeCompound) pipes PN-12.5 (12.5kg/Sqcm) as per ISO 4427 and specification for waterapplication rates are inclusive of , taxes and duties (Exise duty @12.50% &CST @2% against Form 'C'), labour cess, contractor profit and overhead charges all complete asper direction of Engineer-in-charge.complete.
| MDPE Pipe 20mm dia nominal bore |  |  |  | 6 | PM | 27.42 | 164.52
1B | Providing and fixing G.I. pipes complete with G.I. fittings and clamps, i/c cutting and making good the walls etc.Internal work - Exposed on wall
18.10.1 | 15 mm dia nominal bore |  |  |  | 1.1 | PM | 227.7 | 250.47
1C | Providing and faying cement concreate in kerbs, steps and the like at or near ground level excluding the cost of centring, shuttering and finishing.
4.4.1 | 1:2:4 (1 Cement :2 coarse sand :4 grade stone aggregate 20 mm nominal size)
Providing SWR pipe as support with concrete work to the standing GI Pipe
| 22/28 x 0.10m x .10m x 1.0M= |  |  |  | 0.009 | P/M3 | 3998.1 | 35.9829
12.78.2 | Providing & fixing of SWR Pipe of 110mm dia= |  |  |  | 1 | PM | 257.5 | 257.5
2 | Earth work in excavation in foundation trenches or drains(not exceeding 1.5 m in width or 10 sqm on plan) including dressing of sides and amming of bottoms, lift upto 1.5 m . including getting out the excavated soil and disposal of surplus excavated soil as directed, within a lead of 50 m. All kinds of soil
2.8.1 | 6 | 0.3 | 0.6 | 1.08 | 1.08 | CuM | 360.7 | 389.556
3 2.26 | Filling available excavated earth (excluding rock) in trenches, plinth, sides of foundations etc. in layers not exceeding 20 cm in depth: consolidating each deposited layer by ramming and watering lead |  |  |  | 1.06 | CuM | 123.9 | 131.334
4 | Providing and fixing brass ferrule with CI mouth cover incuding boring and tapping the main:
18.20.1 | 15mm nominal bore |  |  |  | 1 | Each | 301.6 | 301.6
(a) | Providing and fixing P.P. Clamp service Saddle (Brass threaded) |  |  |  | 1 | Each | 400 | 400
(b) | Providing and fixing female Adopter for adjoining the ferrule to MDPE pipe |  |  |  | 1 | Each | 75 | 75
(c) | Providing and fixing female elbow Adopter for adjoining the MDPE pipe to GI Pipe |  |  |  | 1 | Each | 50 | 50
5 | Providing and fixing CP brass bib cock of approved quality conforming to IS :8931
18.49 | 15 mm nominal bore |  |  |  | 1 | Each | 434.2 | 434.2
| Total | [6 empty] | 2490.1629
| Say | [6 empty] | 2490
For total no of Household | [6 empty] | 75 | 186750
Executive Engineer,
P. H. Division, Hajipur.

## STAGING
Sub Est. No. 6A
8 M HIGH STEEL STRUCTURE STAGING FOR 10000 LITER PVC TANK
S.N. | Particulars | [5 empty] | Quantity |  | Unit | Rate | Amount
1 10.32.1 | Structural steel work riveted or bolted in built up sections, trusess and framed work, including cutting,hoisting,fixing in position and applying a priming coat of approved primer all complete
| for 8M high staging with ladder of ISA65x65x6 and 16mm dia MS bar as trade @ 400mm c/c and GI enclosure to house electric switch panel & treatment unit (where required) of suitably designed MS section of angle, channel, etc. as per drawing attached. | [5 empty] | 4240 | Kg | P/Kg | 104 | 440960
2 2.8.1 | Earth work in excavation in foundation trenches or drains(not exceeding 1.5 m in width or 10 sqm on plan) including ressing of sides and ramming of bottoms, lift upto 1.5 m . including getting out the excavated soil and disposal of surplus excavated soil as directed, within a lead of 50 m. All Kinds of soil
base of footing
| 4 | 1.95 | 1.95 | 1.35 | = | 20.5335
Under Tie beam
| 2 | 2.3 | 0.25 | 0.275 | = | 0.31625
| 2 | 1.3 | 0.25 | 0.275 | = | 0.17875
[6 empty] | 21.0285 | 21.0285 | M3 | P/M3 | 360.7 | 7584.9799
3- 2.28 | Supplying and filling in plinth with local sand and under floors including watering, ramming consolidating and dressing complete.
base of footing
| 4 | 1.95 | 1.95 | 0.1 | = | 1.521
Under Tie beam
| 2 | 3.95 | 0.25 | 0.1 | = | 0.1975
| 2 | 2.95 | 0.25 | 0.1 | = | 0.1475
Floor
| 1 | 4 | 3 | 0.1 | = | 1.2
[6 empty] | 3.066 | 3.066 | M3 | P/M3 | 287.3 | 880.8618
4- 11.72 | Providing designation of 100A Brick flat Soling joints filled with local sand including cost of watering, taxes & royalty all complete as per specification & direction of E/I.
base of footing
| 4 | 1.95 | 1.95 |  | = | 15.21
Under Tie beam
| 2 | 3.95 | 0.25 |  | = | 1.975
| 2 | 2.95 | 0.25 |  | = | 1.475
Floor
| 1 | 4 | 3 |  | = | 12
[6 empty] | 30.66 | 30.66 | M2 | P/M2 | 283.3 | 8685.978
5 4.1.2 | Providing and laying in position cement concrete of specified grade exluding the cost of centring and shuttering-all work upto plinth level.
1:1.5:3(1 Cement :1.5 coarse sand:3 graded stone aggregate 20 mm nominal size)
base of footing
| 4 | 1.95 | 1.95 | 0.075 | = | 1.1407
Floor
| 1 | 4 | 3 | 0.1 | = | 1.2
[6 empty] | 2.3407 | 2.3407 | M3 | P/M3 | 4420.8 | 10347.9876
6 5.1.2 | Providing and laying in position specified grade of reinforced cement concrete excluding the cost of entring,shuttering,finishing and reinforcement-All work puto plinth level
1:1:5:3 (1 cement: 1.5 coarse sand:3 graded stone aggregate 20 mm nominal size)
Tie beam
| 2 | 3.8 | 0.25 | 0.25 | = | 0.475
| 2 | 2.8 | 0.25 | 0.25 | = | 0.35
base of footing
| 4 | 1.8 | 1.8 | 0.3 | = | 3.888
| 4 | 0.6 | 0.6 | 0.15 | = | 0.216
Column below GL
| 4 | 0.45 | 0.45 | 0.65 | = | 0.5265
Column above GL
| 4 | 0.45 | 0.45 | 0.15 | = | 0.1215
[6 empty] | 5.577 | 5.577 | M3 | P/M3 | 4688.3 | 26146.6491
7- 5.9.1 | Centring and shuttering including strutting,propping etc. and removal of form for.
| 4 | 3.8 | 0.25 |  | = | 3.8
| 4 | 2.8 | 0.25 |  | = | 2.8
| 16 | 1.8 | 0.3 |  | = | 8.64
| 16 | 0.6 | 0.15 |  | = | 1.44
| 16 | 0.45 | 0.65 |  | = | 4.68
| 16 | 0.45 | 0.15 |  | = | 1.08
[6 empty] | 22.44 | 22.44 | M2 | P/M2 | 211.6 | 4748.304
8- 5.22 | Reinforcement for R.C.C. work including straightening, cutting, bending, placing in position and binding all complete.
8 mm to 16 mm tor steel
| Total Reinforcement. @1.25% of Vol. Of Concrete (Kg/cuM) |  |  |  |  | = | 446.24 | Kg. | P/Kg. | 94.5 | 42169.68
9 2.26 | Filling available excavated earth (excluding rock) in trenches, plinth, sides of oundations etc. in layers not exceeding 20 cm in depth: consolidating each deposited layer by ramming and watering lead (50% of E/W in excavation) | [5 empty] | 10.5143 | M3 | P/M3 | 123.9 | 1302.7156
10 13.26 | Neat cement punning
| 1 | 4 | 3 |  | = | 12 | 12 | M2 | P/M2 | 40.5 | 486
11- 10.7.1 | Providing and fixing 1mm thick M.S. sheet door with frame of 40x40x6mm angle iron and 3mm M.S. gusset plates at the junctions and corners, all necessary fittings complete, including applying a priming coat of approved steel primer.
Using flats 30x6 mm for diagonal braces and central cross piece.
Door
| 1 | 0.9 | 2.1 |  | = | 1.89
Window
| 1 | 1.2 | 0.9 |  | = | 1.08
|  |  |  | Total | = | 2.97 | 2.97 | M3 | P/M3 | 3653 | 10849.41
12- 12.1.4 | Providing corrugated G.S. sheet roofing fixed with G.I.J. or hooks, bolts and nuts 8 mm diameter with bitumen and G. I. limpet washers or with G.I. limpet washers filled with white lead and including a coat of approved steel primer and two coats of approved paint on over lapping of sheets complete (upto a pitch of 60°) excluding the cost or purlins, rafters and trusses.
0.8mm thick with zinc coating not less than 275 gm/mz
Roof
| 1 | 4.5 | 3.5 |  | = | 15.75
Wall
| 1 | 16 | 3 |  | = | 48
63.75
Deduct for door & window
| 1 | 0.9 | 2.1 |  | = | 1.89
| 1 | 1.2 | 0.9 |  | = | 1.08
2.97
| Net Qty |  |  |  | = | 60.78 | 60.78 | M2 | M2 | 1501.3 | 91249.014
13 10.19 | Providing and fixing anchor bolt of 20 mm dia and 0.60 Mtr length (bolt, washer & double nut) embedded in R.C.C pedestal all complete as per direction of Engineer in charge. @4x4x1.60kg | [5 empty] | 25.6 | Kg | P/kg | 82.7 | 2117.12
14- 13.82.1 | Painting with ready mixed paint of approved brand and manufacture in all shades to give an even shade:
New steel work (two or more coats)
Frame work
| 0.5 | 16 | 8 |  | = | 64
| 0.5 | 5 | 4 |  | = | 10
Roof sheet
| 2 | 4.5 | 3.5 |  | = | 31.5
Top sheet
| 2 | 5 | 4 |  | = | 40
GI sheet wall
| 2 | 16 | 3 |  | = | 96
[6 empty] | 241.5 | 241.5 | M2 | M2 | 83.5 | 20165.25
15 | Carriage of the following materials from quarry to work site including loading, unloading and staking at work site as per specification & direction of E/I.
| (a) Bricks ( 7 Km. Pucca & 1 Km. Kaccha lead) | [5 empty] | 990 | Nos. | %0 nos. | 873.2 | 864.468 | 2094.8814
| (b) Coarse sand (44 Km pucca & 1 km kaccha Carriage) | [5 empty] | 3.44 | M3 | P/M3 | 2094.8814 | 7206.392 | 2999.8414
| (c) Stone Chips (195 Km pucca & 5 km unsurafced Carriage) | [5 empty] | 6.695 | M3 | P/M3 | 2999.8414 | 20083.9382 | 328.9166
| (d) Local Sand ( 2 Km. lead & 1km Kachaa lead) | [5 empty] | 3.53 | M3 | P/M3 | 328.9166 | 1161.0756
[10 empty] | TOTAL | 697009.8238
[10 empty] | say | 697000
|  | JE |  |  |  | AE |  |  | Executive Engineer,
P. H. Division, Hajipur.

## IRP (8) (hidden)
Sub Estimate no.- 9A
Estimate for Iron Treatment Plant (Included GST @ 18%)
S.N. | Particulars | Quantity |  | Unit | Rate (In Rs.) | Amount (In Rs.)
1 | Design, supply, erection, installation, testing and commissioning of Iron removal plant based on aeration/ filteration/ activated carbon treatemnt units or any other suitable treatmnet process of ISO 9001 certified reputed make housed in MS/FRP vessel suitable for required flow rate with iron concentration upto 10 ppm in raw water to deliver treated water quality confirming to IS 10500( latest revision) including all necessary civil works, accessories,taxes and duties etc. all complete as per directions of Engineer-in-Charge.
| 8 KLPH Capacity | 1 | No. | Each | 489605 | 489605
TOTAL : - | [5 empty] | 489605
[5 empty] | Say | 489605
Executive Engineer P.H. Division, Hajipur

## IRP (16) (hidden)
Sub Estimate no.- 9B
Estimate for Iron Treatment Plant (Included GST @ 18%)
S.N. | Particulars | Quantity |  | Unit | Rate (In Rs.) | Amount (In Rs.)
1 | Design, supply, erection, installation, testing and commissioning of Iron removal plant based on aeration/ filteration/ activated carbon treatemnt units or any other suitable treatmnet process of ISO 9001 certified reputed make housed in MS/FRP vessel suitable for required flow rate with iron concentration upto 10 ppm in raw water to deliver treated water quality confirming to IS 10500( latest revision) including all necessary civil works, accessories,taxes and duties etc. all complete as per directions of Engineer-in-Charge.
| 16 KLPH Capacity | 1 | No. | Each | 600880 | 600880
TOTAL : - | [5 empty] | 600880
[5 empty] | Say | 600880
Executive Engineer P.H. Division, Hajipur

## IRP 12 (hidden)
Sub Estimate no.- 9B
Estimate for Iron Treatment Plant (Included GST @ 18%)
S.N. | Particulars | Quantity |  | Unit | Rate (In Rs.) | Amount (In Rs.)
1 | Design, supply, erection, installation, testing and commissioning of Iron removal plant based on aeration/ filteration/ activated carbon treatemnt units or any other suitable treatmnet process of ISO 9001 certified reputed make housed in MS/FRP vessel suitable for required flow rate with iron concentration upto 10 ppm in raw water to deliver treated water quality confirming to IS 10500( latest revision) including all necessary civil works, accessories,taxes and duties etc. all complete as per directions of Engineer-in-Charge.
| 12 KLPH Capacity | 1 | No. | Each | 545245 | 545245
TOTAL : - | [5 empty] | 545245
[5 empty] | Say | 545245
Executive Engineer P.H. Division, Hajipur

## Pit (hidden)
SUB ESTIMATE NO -6
Detailed Estimate for construction of chamber for waste water disposal 1.00Mx 2.00M x 1.50M deep (with fly proof galvanized M.S. wire covering)
1 |  | Earth work in excavation
| 2.8 | 1.50m x 2.50m x 1.00M = | 3.75 | M3 | P/M3 | 360.7 | 1352.625
2 | 2.28 | Supplying & filling in plinth with local sand under floors including watering, ramming consolidating and dressing complete.
|  | 1.50m x 2.50m x 0.10M = | 0.375 | M3 | P/M3 | 287.3 | 107.7375
3 | 11.72 | Providing designation 100 A one brick flat soling joints filled with local sand including cost of watering, taxes, royalty all complete as per building specification and direction of E/l.
|  | 1.50m x 2.50m = | 3.75 | M2 | P/M2 | 283.3 | 1062.375
4 | (SOR 4.1.4) | Providing & laying in position cement concrete of specified grade excluding the cost of centring & shuttering etc. all work up to plinth level.
1:2:4 (1 cement : 2 coarse sand : 4 graded stone aggregate 20 mm nominal size)
|  | 1.50m x 2.50m x 0.08M = | 0.3 | M3 | P/M3 | 3879.4 | 1163.82
5 | (SOR 6.1.14A) | Brick work with bricks of class designation 100A in foundation and plinth in
Cement mortar 1:4 (1 cement : 4 coarse sand)
|  | L. W. = 2 x 2.50 x 0.25 x 1.5 = | 1.875
|  | S. W. = 2 x 1.00 x 0.25 x 1.5 = | 0.375
|  |  | 2.25 | M3 | P/M3 | 4819.9 | 10844.775
6 | (SOR 13.17.1) | 12 mm cement plaster 1:3 (1 cement: 3 coarse sand) finished with a floating coat of near cement
In side
|  | L. W. = 2 x 2.00 x 1.5 = | 6
|  | S. W. = 2 x 1.00 x 1.5 = | 3
|  | Bottom = 2.0 x 1.0 = | 2
|  |  | 11 | M2 | P/M2 | 203.6 | 2239.6
7 | (SOR 13.11.2 & 13.26) | Providing 12mm cement plaster (1:4)
out side with neat cement punning
|  | L. W. = 2 x 2.5 x 0.75 = | 3.75 |  |  | 152.9
|  | S. W. = 2 x 1.50 x 0.75 = | 2.25 |  |  | 40.5
|  |  | 6 | M2 | P/M2 | 193.4 | 1160.4
8 | (SOR 9.51.2) | Providing and fixing fly proof galvanized M.S. wire gauze to windows and clerestory window using galvanized M.S. wire gage with average width of aperture 1.4 mm in both directions with wire of dia.0.63 mm.
with mild steel U beading
|  | 2.5m x 1.5m = | 3.75 | M2 | P/M2 | 639.9 | 2399.625
10 |  | Carriage of materials.
|  | (a) Bricks ( 7 Km. Pucca & 1 Km. Kachha lead) | 1037 | No. | P/%0 | 1429.6 | 1482.4952
|  | (b) Coarse Sand (100 Km. lead) | 1.09 | M3 | P/M3 | 1015.1 | 1106.459
|  | (c) Stone Chips (150 Km. lead) | 0.27 | M3 | P/M3 | 1690.7 | 456.489
|  | (d) Local Sand ( 2 Km. Pucca & 1 Km. Kachha lead) | 0.43 | M3 | P/M3 | 407.1 | 175.053
|  | Total |  |  |  |  | 23551.4537
|  | Say |  |  |  |  | 23551
Executive Engineer P.H. Division, Hajipur

## Switch Room (hidden)
SUB ESTIMATE-6B
Construction of 2.10x2.40mx2.40 m high of Attendent Cum Chlorinator room
Sl. No. | Particulars | [6 empty] | Qtty. |  | Unit | Rate | Amount
1 | Earth work in excavation in foundation trenches or drains(not exceeding 1.5 m in width or 10 sqm on plan) including ressing of sides and ramming of bottoms, lift upto 1.5 m . including getting out the excavated soil and disposal of surplus excavated soil as directed, within a lead of 50 m. All Kinds of soil
| base of footing | 4 | 0.5 | 0.5 | 1.2 | = | 1.2
| Under Tie beam | 2 | 1.9 | 0.25 | 0.275 | = | 0.26125
|  | 2 | 1.7 | 0.25 | 0.275 | = | 0.23375
2.8 | [6 empty] | 1.695 | 1.695 | M3 | P/M3 | 360.7 | 611.3865
2 | Supplying and filling in plinth with local sand and under floors including watering, ramming consolidating and dressing complete.
| base of footing | 4 | 0.5 | 0.5 | 0.1 | = | 0.1
| Under Tie beam | 2 | 1.9 | 0.25 | 0.1 | = | 0.095
|  | 2 | 1.7 | 0.25 | 0.1 | = | 0.085
| Floor | 1 | 2.4 | 2.1 | 0.5 | = | 2.52
2.28 | [6 empty] | 2.8 | 2.8 | M3 | P/M3 | 287.3 | 804.44
3 | Providing designation of 100A Brick flat Soling joints filled with local sand including cost of watering, taxes & royalty all complete as per specification & direction of E/I.
| base of footing | 4 | 0.5 | 0.5 |  | = | 1
| Under Tie beam | 2 | 1.9 | 0.25 |  | = | 0.95
|  | 2 | 1.7 | 0.25 |  | = | 0.85
| Floor | 1 | 2.4 | 2.1 |  | = | 5.04
11.72 | [6 empty] | 7.84 | 7.84 | M2 | P/M2 | 283.3 | 2221.072
4 | Providing and laying in position cement concrete of specified grade exluding the cost of centring and shuttering-all work upto plinth level 1:1.5:3(1 Cement :1.5 coarse sand:3 graded stone aggregate 20 mm nominal size)
| base of footing | 4 | 0.5 | 0.5 | 0.1 | = | 0.1
| Floor | 1 | 2.4 | 2.1 | 0.075 | = | 0.378
4.1.2 | [6 empty] | 0.478 | 0.478 | M3 | P/M3 | 4420.8 | 2113.1424
5 | Providing and laying in position Reinforcement cement concrete of specified grade exluding the cost of centring and shuttering-all work upto plinth level 1:1.5:3(1 Cement :1.5 coarse sand:3 graded stone aggregate 20 mm nominal size)
| Tie beam | 2 | 2.15 | 0.25 | 0.15 | = | 0.16125
|  | 2 | 1.85 | 0.25 | 0.15 | = | 0.13875
| roof | 1 | 2.55 | 2.25 | 0.12 | = | 0.6885
| chhajja | 2 | 1.6 | 0.45 | 0.063 | = | 0.09072
| base of footing | 4 | 0.25 | 0.25 | 3.25 | = | 0.8125
5.2.2 | [6 empty] | 1.8917 | 1.8917 | M3 | P/M3 | 5670 | 10726.0524
6 | Centring and shuttering including strutting, propping etc. and removal of form for.
|  | 1 | 2.55 | 2.25 |  | = | 5.7375
|  | 4 | 0.25 | 3.25 |  | = | 3.25
|  | 2 | 2.15 | 0.25 |  | = | 1.075
|  | 2 | 1.85 | 0.25 |  | = | 0.925
5.9.3 | [6 empty] | 10.9875 | 10.9875 | M2 | P/M2 | 437.5 | 4807.0312
7 | Reinforcement for R.C.C. work including straightening, cutting, bending, placing in position and binding all complete.
8 mm to 16 mm tor steel
5.22 | Total Reinforcement @80 of vol. of Concrete (Kg/cuM) | [6 empty] | 151.3376 | Kg. | P/Kg. | 97.1 | 14694.881
8 2.26 | Filling available excavated earth (excluding rock) in trenches, plinth, sides of oundations etc. in layers not exceeding 20 cm in depth: consolidating each deposited layer by ramming and watering lead (50% of E/W in excavation) | [6 empty] | 0.8475 | M3 | P/M3 | 123.9 | 105.0052
9 | 12mm thick C.P. (1:4) in floor with Neat cement punning
13.26+13.11.2 | Floor | 1 | 2.4 | 2.1 |  | = | 5.04 | 5.04 | M2 | P/M2 | 193.4 | 974.736
| Iner wall | 2 | 2.4 | 2.4 |  | = | 11.52
|  | 2 | 2.1 | 2.4 |  | = | 10.08
| Outer wall | 2 | 2.9 | 2.55 |  | = | 14.79
|  | 2 | 2.6 | 2.55 |  | = | 13.26
13.11.4 |  |  |  |  | Total | = | 49.65 | 49.65 | M2 | P/M2 | 141.5 | 7025.475
10 | Providing and fixing 1mm thick M.S. sheet door with frame of 40x40x6mm angle iron and 3mm M.S. gusset plates at the junctions and corners, all necessary fittings complete, including applying a priming coat of approved steel primer Using flats 30x6 mm for diagonal braces and central cross piece.
| Door | 1 | 0.9 | 2.1 |  | = | 1.89
| Window | 2 | 1.2 | 0.9 |  | = | 2.16
10.5.1 |  |  |  |  | Total | = | 4.05 | 4.05 | M3 | P/M3 | 3653 | 14794.65
11 | Brick work with bricks of class designation 100A in Cement mortar 1:6 in foundations and plinth in extra for Brick work in superstructure above plinth level upto floor V
|  | 2 | 2.4 | 2.4 | 0.25 | = | 2.88
|  | 2 | 2.1 | 2.4 | 0.25 | = | 2.52
5.4
Deduct for door & window
|  | 1 | 0.9 | 2.1 | 0.25 | = | 0.4725
|  | 2 | 0.9 | 1.2 | 0.25 | = | 0.54
6.3A | [6 empty] | 1.0125
6.1.14A | Net Qty |  |  |  |  | = | 4.3875 | 4.3875 | M3 | P/M3 | 5662.1 | 24842.4638
12 13.79.1 | Painting on walls with water proofing cement paint of approved brand and manufacture in all shades to give an even shade New surface wall (two or more coats) | [6 empty] | 49.65 | M2 | P/M2 | 81.2 | 4031.58
13 | Painting with ready mixed paint of approved brand and manufacture in all shades to give an even shade New steel work (two or more coats)
13.82.1 | door & window | 1 | 9.1125 |  |  | = | 9.1125 | 9.1125 | M2 | P/M2 | 83.5 | 760.8938
14 | Carriage of the following materials from quarry to work site including loading, unloading and staking at work site as per specification & direction of E/I.
| (a) Bricks (7 Km. Pucca & 1 Km. Kachha lead) | [6 empty] | 2420.3282 | Nos. | P/‰ | 1317.49 | 3188.7582
| (b) Coarse Sand (44 Km. Pucca & 1 Km. Kachha lead) | [6 empty] | 3.3436 | M3 | P/M3 | 1028.77 | 3439.7747
| (c) Stone chips (110 Km. Pucca & 5 Km. Kachha lead) | [6 empty] | 2.0949 | M3 | P/M3 | 2260.03 | 4734.5676
| (d) Local Sand (2 Km. Pucca + 1 Km. Kachha lead) | [6 empty] | 2.9764 | M3 | P/M3 | 288.45 | 858.5426
[11 empty] | TOTAL | 100734.4524
[7 empty] | Add 6% GST (Multiplying factor=0.0536) |  |  |  |  | 5399.3666
[11 empty] | G. TOTAL | 106133.819
[11 empty] | Say | 106140
| JE |  |  |  |  | AE |  | Executive Engineer P.H. Division, Hajipur

## Clorinator
Sub Estimate no.- 7
Electronically Regulated Doser Type Chlorinator
Sl. No. | Particulars |  | Quantity |  | Unit | Rate (In Rs.) | Amount (In Rs.)
1 | Providing cost of electronically regulated Doser type chlorinator using sodium Hypo Chlorite (NaOCl ) and installation including all cost and necessary fittings and connections as required and carriage cost etc. all complete as per direction of E/I.
|  |  | 1 | No. | Each | 23515 | 23515
TOTAL : - | [6 empty] | 23515
| JE | AE |  | Executive Engineer P.H. Division, Hajipur

## Sheet1
SL. NO. | BLOCK | NO. OF SCHEME | MAP SUBMITTED
1 | HAJIPUR | 66 | 48
2 | BIDUPUR | 18 | 0
3 | RAGHOPUR | 18 | 18
4 | RAJAPAKAR | 13 | 0
5 | LALGANJ | 5 | 0
6 | PATEDHI BELSAR | 12 | 0
7 | VAISHALI | 2 | 2
8 | GORAUL | 6 | 0
9 | BHAGWANPUR | 3 | 3
10 | MAHUA | 27 | 0
11 | CHEHRAKALA | 14 | 14
12 | MAHNAR | 1 | 0
13 | SAHDAI BUJURG | 2 | 0
14 | PATEPUR | 3 | 0
15 | JANDAHA | 9 | 0
| TOTAL | 199 | 85

## COM Quantity (2) (hidden)
P. H. DIVISION, HAJIPUR
WORK DETAIL Of Quantity For Distribution System
DETAILS OF Pipeline Distribution System Of Different Schemes
Block :-
Sl. No. | Panchayat | Ward No | Scheme Name | Different Size Of HDPE pipe (In Mtrs.) | [6 empty] | PVC Tank in Liter | Brass gate valve with C.I. wheel |  |  | Nos. of connections
|  |  |  | 110 mm | 90 mm | 75 mm | 63 mm | 50 mm | 40 mm | Total |  | 80 mm | 65 mm | 50 mm
JE |  |  |  |  | AE | [9 empty] | EE

## elec (hidden)
Sub Estimate No.- 8B
energy Charges for 5 year
PUBLIC HEALTH DIVISION, HAJIPUR.
S.N. | Description |  | Quantity | Rate | Unit | Amount
1 | Cost of Energy charges
| HP of pump =3HP |  | 3
| 3 | HP | = | 2.238 | KKW
| Opreating Hour Average running |  |  | 8 | Hours/Day
| Unit Expenditure per year=HP*0.746*8*365*1.1 |  |  | 7253.8056 | Unit
| Energy Charges @ |  |  | 2.6 | per Unit | 18859.8946
| Fixed charges (3HPx100x365/30) |  | 3 | 100 | Per HP per month | 3650
| duty charges @ 6% of energy charges |  |  |  |  | 1131.5937
| Total |  |  |  |  | 23641.4882
23641.4882
| Therefore Annual Maintenance for one Year |  |  |  |  | 23641.4882
| Therefore Maintenance for five Year |  |  |  |  | 118207.4412
| Say |  |  |  |  | 118207
Executive Engineer
P.H. Division, Hajipur

## popforcast (hidden)
Population Forcast
1 | Block | HAJIPUR | Scheme | 02B CHAKBHATANDI | 75
| Panchayat | PAHETIYA
The Population of three decades are as under
Population
|  |  | 1991 | 2001 | 2011 | 2018
|  |  | 200.6579 | 266.4474 | 328.9474 | 375
|  |  | 200.6579 | 266.4474 | 328.9474 | 375
DESIGN OF POPULATION
The Population Forecast by
1- | Calculation by Arithmetic Increase Method
S.N. | Year | Population | Increase in Population = X
1 | 1991 | 200.6579
65.7895
2 | 2001 | 266.4474
62.5
3 | 2011 | 328.9474
| Total |  | 128.2895
| Average increase per decade = X = |  | 64.1447
| The future population are computed by using | [5 empty] | Value of
|  | PN | = | Population in forecast year |  | in 2022 | N = | 0.7 | 328.9474 | 44.9013 | 373.8487
| PN = PO+ (N x X ) | Po | = | Population in Last Census |  | in 2037 | N = | 2.2 | 328.9474 | 141.1184 | 470.0658
|  | N | = | No. of next decade |  | in 2052 | N = | 3.7 | 328.9474 | 237.3355 | 566.2829
|  | X | = | Average increase per decade
| Population in base Year | in 2022 | = | 373.8487
| Population in intermediate Year | in 2037 | = | 470.0658
| Population in ultimate Year | in 2052 | = | 566.2829
2- | Calculation by Geometric Mean Method
S.N. | Year | Population | Increase in Population = X | Percentage increase in Population = R
1 | 1991 | 200.6579
|  |  | 65.7895 | 0.32787
2 | 2001 | 266.4474 |  |  | 0.27732
|  |  | 62.5 | 0.23457
3 | 2011 | 328.9474
The Geometric Growth rate = R = 2√ (a) x (b)
|  | = | 27.7322 | % Per Decade
|  | PN | = | Population in forecast year |  | in 2022 | N = | 0.7 | 328.9474 | 1.2773 | 1.1869 | 390.4242
| PN = PO (1 + R/100)N | Po | = | Population in Last Census |  | in 2037 | N = | 2.2 | 328.9474 | 1.2773 | 1.7134 | 563.6212
|  | N | = | No. of next decade |  | in 2052 | N = | 3.7 | 328.9474 | 1.2773 | 2.4735 | 813.6505
|  | R | = | Percentage increase in Population
| Population in base Year | in 2022 | = | 390.4242
| Population in intermediate Year | in 2037 | = | 563.6212
| Population in ultimate Year | in 2052 | = | 813.6505
3- | Calculation by Incremental Increase Method
S.N. | Year | Population | Increase = X | Incremental Increase = Y
1 | 1991 | 200.6579
65.7895
2 | 2001 | 266.4474
|  |  | 62.5 | -3.2895
3 | 2011 | 328.9474
|  |  | 128.2895 | -3.2895 |  |  |  |  | Po | N * X | N(N+1) *Y/2 | PN = PO + N*X + N (N+1) Y / 2
|  | PN | = | Population in forecast year |  | in 2022 | N = | 0.7 | 328.9474 | 44.9013 | -1.9572 | 371.8914
| PN = PO + N*X + N (N+1) Y / 2 | Po | = | Population in Last Census |  | in 2037 | N = | 2.2 | 328.9474 | 141.1184 | -11.5789 | 458.4868
|  | X | = | 64.1447 |  | in 2052 | N = | 3.7 | 328.9474 | 237.3355 | -28.602 | 537.6809
|  | Y | = | -3.2895
| Population in base Year | in 2022 | = | 371.8914
| Population in intermediate Year | in 2037 | = | 458.4868
| Population in ultimate Year | in 2052 | = | 537.6809
4 | Calculation by Decadal Increase Method
| Year | Population | Increase in Population | Decadal Increase
| 1991 | 200.6579 |  | in %
| 2001 | 266.4474 | 65.7895 | 32.7869
| 2011 | 328.9474 | 62.5 | 23.4568
| Total Increase: |  | 128.2895
Hence average increase per decade |  |  | 64 | 28.1218 | 2.8122 | % Increase
|  |  |  | %per year | % Increase
| Population in base Year | (Population 2011 + (Average increase per decade x 0.6)) |  |  | 367.3474 | 10.4533
| Population in intermediate Year | (Population 2011 + (Average increase per decade x 2.1)) |  |  | 463.3474 | 29.0063
| Population in ultimate Year | (Population 2011 + (Average increase per decade x 3.6)) |  |  | 559.3474 | 41.1909
AVERAGE OF ALL METHODS
S.N. | Methods of Forecast |  | Expected Population in
|  | Base Year | Intermediate Year | Ultimate Year | Percentage of Increase from 2011
|  | in 2022 | in 2037 | in 2052
1 | Arithmetic Increase Method | 373.8487 | 470.0658 | 566.2829 | 72.15 | 20.0417
2 | Geometric Mean Method | 390.4242 | 563.6212 | 813.6505 | 147.3498 | 40.9305
3 | Incremental Increase Method | 371.8914 | 458.4868 | 537.6809 | 63.455 | 17.6264
4 | Decadal Increase Method | 367.3474 | 463.3474 | 559.3474 | 70.0416 | 19.456
| Average of all methods | 375.8779 | 488.8803 | 619.2404 | 88.2491 | 24.5136
AVERAGE OF THREE METHODS
S.N. | Methods of Forecast |  | Expected Population in
|  | Base Year | Intermediate Year | Ultimate Year | Percentage of Increase from 2011
|  | in 2022 | in 2037 | in 2052
1 | Arithmetic Increase Method | 373.8487 | 470.0658 | 566.2829 | 72.15 | 20.0417
2 | Geometric Mean Method | 390.4242 | 563.6212 | 813.6505 | 147.3498 | 40.9305
3 | Incremental Increase Method | 371.8914 | 458.4868 | 537.6809 | 63.455 | 17.6264
| Average of three methods | 378.7214 | 497.3913 | 639.2048 | 94.3183 | 26.1995
Population of the Village is increasing rapidally. The Average Population Growth rate of 22.35 % per decade comes through Average of three methods which is very near to Average Growth rate of Bihar (22.49), is adapted here for Population Forecasting.
Sl. | Year |  | Population
1 | Initial Year | in 2022 | 378.7214
2 | Prospective Year | in 2037 | 497.3913
3 | Ultimate Year | in 2052 | 639.2048
POPULATION ADOPTED FOR DESIGN |  |  |  | Percentage of increase
1 | Population in Census Year | in 2011 | 328.9474 | From 2011
2 | Population in Base Year | in 2022 | 378.7214 | 15.1313 | % Increased | 49.7741 | 2.5219 | 3
3 | Population in Intermediate Year | in 2037 | 497.3913 | 51.2069 | % Increased | 168.4439 | 2.4384 | 2
4 | Population in Ultimate Year | in 2052 | 639.2048 | 94.3183 | % Increased | 310.2574 | 2.62 | 3
As per norms the population is to be fed through house connection @70 lpcd including 15% Uaccounted flow of water. Demand of water for initial, intermediate and ultimate stages are as under:
| Year | Population |  |  | Demand
@81 LPCD in MLD
| in 2011 | 328.9474 |  |  | 0.026645 | 26644.7368
| in 2022 | 378.7214 |  |  | 0.030676 | 30676.4362
| in 2037 | 497.3913 |  |  | 0.040289 | 40288.6928
| in 2052 | 639.2048 |  |  | 0.051776 | 51775.5871
Executive Engineer P.H. Division, Hajipur