## 11 kV / √3 / 110 V / √3 VOLTS SEALED OUTDOOR BUSH TYPE CT-PT COMBINED METERING UNIT

- SCOPE :

The specification provides for manufacture, testing before dispatch, supply and delivery of  11KV/√3/110V/√3 Current and Potential Transformers combined metering unit of class of accuracy 0.2S  suitable for outdoor application. Metering Unit should be suitable for of 3 phase non- effectively earthed system. The unit should consist of one 3 phase star connected PT (unearthed) and three single phase Current transformers (CT’s) housed in a common hermetically sealed steel tank.

- REFERENCE STANDARDS

## The equipment shall comply with the latest amendments of the following standards:

- IS 16227 (Part 1 to 4 ):Specification for  Instrument Transformers

- IS 335: 2018 Transformer Oil

- IS 2099: Bushings for Alternating Voltages

- IS 3347: Dimensions for Porcelain Transformer Bushings

- IS 2633: Galvanization:

- IS 10601: Primary Terminals: IS 10601

- CLIMATIC CONDITIONS

The combined CT & PT metering unit shall operate satisfactorily under the following climatic conditions as per IS 16227 (Part 1):

- Maximum temperature of air in sun: 50°C

- Maximum temperature of air in shade: 45°C

- Minimum temperature of air in shade: 0°C

- Maximum ambient temperature: 45°C

- Maximum rainfall per annum: 2000 mm

- Average rainfall per annum: 1500 mm

- Maximum humidity: 100%

- Average thunderstorm days/year: 70 days

- Average dust storm days/year: 20 days

- Wind pressure: 200 kg/m²

- Altitude: ≤ 1000 m

- TYPE : The metering transformer equipment should be of pole mounting type for outdoor use. They are to be used in 11KV Three phase with solidly earthed neutral and suitable for 3 phase 3 wire 50 cycles networks. The equipment is required for operation of trivector meters and should be oil cooled.

The CTPT sets shall have the following ratings:-

i. Rated Voltage:11KV

ii. Highest systems voltage: 12KV

iii. Insulation level: 12KV

iv. Standard impulse withstand voltage: 75KV

v. One minute power frequency withstand voltage

a. primary: 28KV

b. Secondary: 3KV

vi. Short time thermal current and its duration: 13.1  KA for 1sec  CTPT sets

vii. Class of accuracy: 0.2S

viii. Rated burden per phase

1. For CTs: The rated burden for CTs is 15VA per phase

2. For PTs: The rated burden for PTs shall be 50VA per phase.

IX. Frequency: 50HZ

- DESIGN :

a) The equipment shall be designed to ensure satisfactory operation under all conditions of service to facilitate easy inspection, cleaning and repairs.

b) The design shall incorporate every reasonable precaution and provisions for safety of all those concerned in the operation and maintenance of the equipment.

c) All out-door apparatus shall be so designed that water cannot be collected at any point and enter the CT/PT set. The top cover of the bank, secondary terminal cover, cable box and inspection cover are suitably bent at the edges so that gaskets are not exposed to moisture.

d) All connections and terminals shall be of sufficient size for carrying the specified currents continuously without undue heating.

e) On outdoor equipment all bolts, nuts, washers in contact with non-ferrous parts shall be of brass.

f) All ferrous parts including bolts & nuts liable to corrosion, forming integral parts of the equipment shall be smoothly and continuously hot dip galvanized.

g) The secondary terminal box, inspection cover and oil gauge shall be arranged as shown in the drawing.

h) The core shall be high grade non-ageing electrical silicon laminated steel of low hysteresis loss and high permeability to ensure high accuracy, at both normal and over current/voltage.

i) All winding shall be of insulated high grade electrolytic copper wire and the manufacturing of the units shall be done in completely closed and air-conditioned room otherwise fiber glass insulation sleeves are to be provided for primary winding.Details of winding and core shall be furnished.

j) The CTPT set should have three CTs and one three phase PT with star/star connection.

- SEALING :

Provision for sealing at 4 points (corners) each on the secondary terminal box, inspection cover, the top cover of the tank and cable box shall be made. This may be made by providing a hole of adequate size to pass the sealing wire, of above 14 SWG. A hole on tail of corner bolts shall be provided.

- FLUCTUATION IN VOLTAGE AND FREQUENCY :

For continuous operation, entire equipment shall be subjected to variation of voltage upto plus 20% and -30% and frequency of plus or minus 5 percent.

- INSTRUMENT TRANSFORMERS :

a) The voltage and current transformers shall have normal continuous rating as per the schedule of requirement. Voltage transformer shall be provided with bridged current limiting resistance fuses on the high voltage side.

b) The voltage transformer shall be so designed that the increased magnetising currents due to any persisting over voltage does not produce injurious over  heating. Phase barriers shall be provided.

c) The peak value of the rated dynamic current shall not be less than 2.5 times the rated short time thermal current unless stated otherwise(IS 16227 Part I –IV with latest amendment (IEC:61869:2007) with latest amendment) .

d) Modified polyster enamel copper wire is to be used for winding and it shall conform to IS-4800/Part-V (latest version).

e) The terminals of the current and voltage transformer parts of combined instrument transformers shall be marked in the same way as for individual transformers as specified in 6.13.201 of IEC 61869-2 : 2012 and 6.13.301 of IEC 61869-3 : 2011.

f) The winding shall be neatly laid and anchored.

g) The metering set tank and other metal parts shall be galvanized, as per latest IS applicable.

9.TERMINALS :

(a) Primary Terminals

Primary terminals shall be made of high conductivity electrical grade Copper suitable for outdoor service conditions and overhead ACSR conductor connection. The terminals shall be threaded and shall project minimum 100 mm from the edge of the bushing for ease of connection and maintenance.

The size of the terminal shall be adequate to carry continuously at least 120% of the rated current without excessive temperature rise. Suitable bi-metallic terminal connectors/clamps shall be provided for connection of specified size ACSR conductor.

Each terminal shall be provided with:

- 3 Nos. hexagonal Brass nuts (2 main nuts and 1 check nut)

- 2 Nos. bi-metallic plain washers

The minimum dimensions shall be as follows:

- Hexagonal Nut : Outside Diameter (OD) ≥ 2D and thickness ≥ 1D

- Washer : OD > 2D and thickness ≥ 2 mm

(where “D” is the diameter of the primary terminal stud)

All Brass components shall be of corrosion resistant high conductivity brass. Bi-metallic washers/connectors shall be suitable for Copper to Aluminum/ACSR connection to prevent galvanic corrosion.

Primary Terminal Size:

- 12 mm diameter for CT ratios 10/5A and 25/5A

- 16 mm diameter for CT ratios 50/5A and 100/5A

The bushing and stud assembly shall be robust, properly sealed, and completely leak-proof to ensure reliable outdoor service performance.

(b) Secondary Terminals & Terminal Box Arrangement

All secondary terminals shall be of minimum M6 size and made of electrical grade brass. Each terminal shall be provided with main and check hexagonal nuts along with suitable washers to ensure reliable, secure, and maintenance-free connections.

The secondary terminals shall be of 6 mm diameter with 25 mm stem length. Each terminal shall be provided with 2 flat washers and 3 hexagonal nuts of brass material. The terminals shall be provided at least 70 mm above the incoming hole, and adequate clearances shall be maintained as per relevant IS standards to avoid any risk of short-circuiting due to secondary wiring conduits.

The secondary terminal box incoming entry hole shall be 25 mm in diameter and positioned at a height of 330 mm ± 5 mm from the bottom of the unit. This arrangement shall ensure that replacement or modification of secondary wiring conduits is not required during replacement of the CT/PT set.

The secondary terminals shall be brought out in a single non-detachable compartment located on the smaller side of the metering unit, positioned at right angle to the HT compartment.

The terminal box shall be provided with a double compression brass cable gland at the bottom. The gland shall have an internal diameter suitable for accommodating a 12-core, 2.5 sq. mm copper armoured control cable.

The terminal box shall be provided with a removable cover fitted with a colourless transparent glass window and a suitable locking arrangement such that the glass cannot be removed after sealing.

The terminal box, with cover closed and cable in position, shall conform to a degree of protection of IP54.

Provision shall be made for proper sealing of the terminal box. Two sealing studs shall be provided for this purpose.

The spacing of secondary terminals shall be adequate to ensure maximum clearance for safe and easy termination of control wiring, in accordance with relevant IS standards.

### 10.Terminal Connectors

Power connectors shall be provided with each primary terminal. The connectors shall be made of virgin aluminium and suitable for ACSR/AAAC Dog conductor.The connectors shall conform to IS: 5561 (1970) and shall be suitable for reliable electrical and mechanical performance under outdoor service conditions.Drawings and samples of the connectors shall be submitted by the supplier for approval of NBPDCL/SBPDCL prior to manufacturing and supply.

### 11.Lifting Lugs

Four (4) lifting lugs shall be provided on the equipment tank with sufficient mechanical strength to safely handle the complete assembly. The lifting lugs shall be properly designed to withstand the total weight of the unit with adequate safety margin.

The lugs shall be located at the four top corners of the tank to ensure balanced lifting and stability during handling and installation.

### 12.Hardware (Bolts, Nuts & Washers)

All bolts, nuts, and washers used in the equipment assembly shall be made of mild steel (MS) and shall be treated with yellow passivation to ensure protection against corrosion.All hardware shall be of high quality, properly finished, and suitable for long-term outdoor service conditions.

13.Bushing:- The porcelain portion of HT bushings shall be of standard make and conform to IS-2099/1996.The dimensions of the bushings shall conform to IS- 3347/Part.III/1972. The minimum phase-to-phase clearance shall be as per IS.The tests as per IS-2099/1962 shall be conducted on the transformer bushings as detailed below:

a) Dry flash over voltage

b) Wet flash over voltage.

c) Dry 1 Minute withstand voltage.

d) Impulse withstand voltage (1.2/50 Micro Seconds –ve wave)

e) Manufacturer’s test certification may be furnished for every lot of offer.

14.STEEL TANK:

a) The Oil filled container incorporating the voltage transformers and current transformers should be fitted with incoming and outgoing primary terminals and secondary terminal box. The secondary terminal box shall be arranged on sides.

b) The tank shall be built with plate of 5 mm thick top & Bottom  and 3.15 mm sides and with all fittings shall be capable of withstanding without leakage or distortion at the standard test pressure. All joints of the tank and fittings shall be hot oil tight and no leaking should occur during service.

c) It shall be provided with an oil gauge. The oil gauge glass shall be fixed appropriately.

The tank shall be provided with necessary lifting lugs.

d) The secondary terminal box cover, tank cover and inspection cover and other vertical joints where gaskets are used shall be suitably bent with necessary sealing arrangement. This will have to safeguard against seepage of water into tank in case of damaged gasket.

e) The Gasket shall be dovetailed without joints to prevent moisture entry. In case of dovetailed joint, they shall not be more than two. The Gasket shall be of good quality Neoprene or rubberized gasket.

f) EARTHING: Two earthing terminals shall be adequate size protected against corrosion and metallically clean and identified by means of the sign marked in a legible and indelible manner on or adjacent to the terminals.

g) All bolts should be provided with 2 flat washers and a spring washer with a nut.

h) Conservator should not be provided for these CTPT sets.

i) The following details of equipment shall be provided on a name plate with at least 10 mm letters. The name plate is to be welded to the tank after galvanization.

1.Make 2. Ratio 3. Class of accuracy 4.Serial No: 5. Month & year of manufacturing.

j) ---- months guarantee embossed plate shall be welded opposite side of name plate.

k) MOUNTING ARRANGEMENT : The under base of all CTPT sets shall be provided with two 75x40 mm GI channels and foundation dimensions shall be as per enclosed drawing and uniform for all sets with only +/- 2 mm tolerance, to avoid modification of structure/ plinth, whenever CTPT set is replaced (Drawing enclosed).

l) Pressure Release Device (PRD) and Nitrogen valve shall be provided.

15. OIL: The insulation oil used in the tank shall comply with the requirements specified in

latest relevant IS-335/2018 as per Annexure I.

16. GUARANTEED TECHNICAL PARTICULARS: The technical particulars as specified in IS shall be guaranteed. Every tenderer should furnish the particulars required without fail and guarantee the values so furnished for the supplies.

17.TESTS:

TYPE TESTS:

a) Temperature rise test.

b) Impulse voltage Test on primary terminals.

c) Wet test for outdoor type transformers.

d) Test for accuracy

e) Verification of the degree of protection by enclosures

f) Short-time current tests

g) Short- circuit withstand capability test

ACCEPTANCE AND ROUTINE TESTS for combined CTPT sets :

The applicable following shall be conducted as per upgraded IS:16227 Part I to IV with latest

amendment (IEC:61869:2007) with latest amendment

a) Power frequency voltage withstand Tests on primary terminals.

b) Partial discharge measurement

c) Power frequency voltage withstand Tests between two sections

d) Power frequency voltage withstand Tests on secondary terminals.

e) Test for accuracy

f) Verification of markings

g) Pressure test for the enclosure

h) Determination of the secondary winding resistance

i) Inter-turn overvoltage test

Accuracy test (Determination of errors) shall be conducted on 100% offered quantity

in the presence of Discom representative.

18. Name Plate: The purchase order No. and Date of the purchase order, the words

“PROPERTY OF SBPDCL/NBPDCLL, ” should be etched on the Name plate.

The name plate is to be welded to the tank after galvanization.

19.Rating Plate marking : The specifications for the current transformer according to 6.13.202 of IEC 61869-2 : 2012 and the voltage transformer according to 6.13.302 of IEC 61869-3 : 2011 shall be marked separately on rating plate.

The voltage transformer shall carry on the rating plate the value of the voltage Ue induced by the r.m.s value of the rated short-time thermal current flowing through the current transformer when the primary winding of the voltage transformer is short circuited. The induced voltage is measured at the terminals of the secondary winding of the voltage transformer loaded with 50VA or the rated burden.

20.No fuse on HV and LV side of PT are to be provided in the equipment.

21.Bill of material

| Sl no | Item | Material Specification | Qty |
| --- | --- | --- | --- |
| 1 | Primary terminal | Tinned Copper, threaded type suitable for ACSR/AAAC termination | 6 nos |
| 2 | Oil Filling / Drain Port | MS, zinc plated with sealing arrangement | 1 no |
| 3 | Pressure Relief Valve | Brass, spring loaded type | 1 no |
| 4 | HT Bushing | Outdoor type porcelain | 6 nos. |
| 5 | Oil Level Indicator | Aluminium / tempered glass type with marking | 1 no |
| 6 | Secondary terminal box | MS sheet steel, weatherproof with sealing & IP54 protection | 1 no |
| 7 | Locking Arrangement (Cover / Helmet type locking) | MS, robust locking mechanism | 1 no |
| 8 | Lifting Lugs | MS, adequately rated for full equipment weight | 4 nos. |
| 9 | Secondary terminals | M6 size, nickel-plated brass with nuts & washers | As required |
| 10 | Secondary Terminal Box Cover | MS frame with transparent polycarbonate viewing window | 1 no |
| 11 | Rating & Connection Diagram Plate | Anodized aluminium, laser engraved | 1 no |
| 12 | Double Compression Cable Gland | Nickel-plated brass, suitable for 12-core 2.5 sq.mm armoured cable | 1 no |
| 13 | Main tank with cover | MS, welded, oil-tight, weatherproof construction | 1 no |
| 14 | Base mounting channel | MS, 75 × 40 × 6 mm structural steel | 2 no |
| 15 | Earthing terminal | MS, M12 × 40, corrosion protected | 2 no |

ANNEXURE – I

GUARANTEED TECHNICAL PARTICULARS FOR TRANSFORMER OIL

| Sl no | Property | Test method | As per IS 335/2018 Type-II U | To be furnished by the bidders |
| --- | --- | --- | --- | --- |
| 1. | Appearance |  | The oil shall be clear, free from sediment and suspended matte |  |
| 2. | Density | IS 1448 (part 16) | 0.895 g/ml at 20 deg. C (Max.) |  |
| 3. | Viscosity | IS 1448 (part 25) | 15 mm2/s, Max at 40 deg. C 1800 mm2/s, Max at 0 deg. C |  |
| 4. | Interfacial tension | ASTM D971 | No general requirement |  |
| 6. | Pour point | IS 1448 (part 10/Sec2) | - 10 deg. C, Max |  |
| 7. | Water content (Max) | IEC 60814 | 30 mg/kg (Bulk) 40 mg/kg (Drum), Max |  |
| 8. | Acidity | IEC 62021-1 | 0.01 mg KOH/g, Max |  |
| 9. | Total Sulphur Content | ISO 14596 or ASTM D4294 | No general requirement |  |
| 10. | Corrosive Sulphur | DIN 51353 | Not corrosive |  |
| 11. | Potentially Corrosive Sulphur | IS 16310 | Not corrosive |  |
| 12. | DBDS | IS 16499 (Part 1) | Not detectable(<5 mg/kg) |  |
| 13. | Inhibitors according to IS 13631/IEC 60666 | IS 13631 | (U) Uninhibited Oil: Not detectable (<0.01%) |  |
| 14. | Metal Passivator additives according to IS 13631/IEC 60666 | IS 13631 | Not detectable (<5 mg/kg) |  |
| 15 | Presence of oxidation inhibitor |  |  |  |
| 16 | Other Additives |  | Nil |  |
| 17 | 2-Furfural & related compounds content | IS 15668 | Not detectable (<0.05 mg/kg) for each individual compound |  |
| 18 | Electric strength (breakdown voltage | IS 6792 | 30 KV (Delivered) 70 KV (After Treatment), Min |  |
| 19. | Dielectric dissipation factor at 90 Deg. C | IS 16086 | 0.005, Max |  |
| 20 | Oxidation Stability |  |  |  |
|  | a) Total Acidity | 1.9.4 of IS 12422 | 1.2 mg KOH/g, Max |  |
|  | b) Total sludge | 1.9.1 of IS 12422 | 0.8%, Max. |  |
|  | c) DDF at 90 deg.C | 1.9.6 of IS 12422 | 0.500, Max |  |
| 21 | Gassing Tendency |  | No general requirement |  |
| 22 | ECT |  | No general requirement |  |
| 23 | Flash point | IS 1448 (Part 21) | 135 deg. C, Min |  |
| 24 | PCA Content | IP 346 | 3%. Max |  |
| 25 | PCB Content | IS 16082 | Not detectable(<2mg/kg) |  |

ANNEXURE – II

(TO BE FILLED IN BY THE TENDERER)

GUARANTEED TECHNICAL PARTICUALRS

(TO BE FURNISHED ALONG WITH THE TENDER)

VOLTAGE TRANSFORMERS :

| Sl no | Particular | To be furnished by the bidders |
| --- | --- | --- |
| 1. | Maker’s name and address |  |
| 2. | Manufacturer’s Type & Designation |  |
| 3 | Nature of service |  |
| 4 | Type of Cooling |  |
| 5 | Rated system Voltage |  |
| 6. | Highest system voltage |  |
| 7. | Ratio of the rated primary voltage to the corresponding rated secondary voltage. |  |
| 8. | System voltage expressed in symbolic notion. |  |
| 9. | Rated burden in volt-amperes per phase. |  |
| 10. | Rate frequency : Cycles per second. |  |
| 11 | Class designation : i.e. Accuracy |  |
| 12 | Limits of error : a) Ratio Error. b) Phase difference in minutes. |  |
| 13 | Rated Voltage Factor & Time |  |
| 14. | Maximum temperature rise. |  |
| 15. | Max. voltage that can be withstood by the primary for one minute :kv. |  |
| 16. | Insulation strength. |  |
| 17. | One-minute power frequency dry withstand test voltage on secondary winding. |  |
| 18 | Winding wire on Primary a. Diameter in mm b. Type/ grade of material C. Weight of winding |  |
| 19. | Winding wire on secondary a. Diameter in mm b. Type/ grade of material C. Weight of winding |  |
| 20. | Interlayer insulation. |  |
| 21. | Core material grade and details a. Weight of core |  |

CURRENT TRANSFORMERS

| Sl no | Particular | To be furnished by the bidders |
| --- | --- | --- |
| 1. | Maker’s name. |  |
| 2. | Type |  |
| 3. | Ratio of the rated primary current to the corresponding rated secondary current. |  |
| 4. | Rated burden in volt-amperes. |  |
| 5. | Rated frequency : Cycles per second. |  |
| 6. | Class designation : i.e. Accuracy |  |
| 7. | Over current factor and time |  |
| 8. | Limits of error : a) Ratio Error. b)Phase difference in minutes. |  |
| 10. | Maximum temperature rise. |  |
| 11. | Continuous percentage over load. |  |
| 12 | Impulse withstand test voltage KV (Peak) |  |
| 15. | Short circuit current and duration |  |
| 16 | Rated current dynamic (Peak value) |  |
| 17 | Whether over voltage protection for open circuit of secondary moulded if provided details to be furnished |  |
| 18 | Inter layer insulation |  |
| 19 | Resistance per Phase at 75 degC in Ohms |  |
| 20 | Turns on a. Primary b. Secondary |  |
| 21 | Core material grade and details a. Weight of core |  |
| 22 | Winding wire Primary a. Diameter in mm b. Type/ grade of material C. Weight of winding |  |
| 23 | Winding wire Secondary a. Diameter in mm b. Type/ grade of material C. Weight of winding |  |

III. Details of Roof Bushing:

| S.N. | Characteristics | Specification or as per IS |
| --- | --- | --- |
| i. | Type and Make | Ceramic, Longer height bushing for 11 KV Metering units with 3 no. petticoats. ISI marked from reputed manufacturer. |
| ii. | Dry Lightening impulse withstand voltage | As per IS 2099-1986 |
| iii. | Power freq. withstand voltage | As per IS 2099-1986 |

IV. OIL :

1. Grade of oil

2. Quantity of oil for first filling

a) Litres :

b) Kgs

V. TANK :

1. Dimension and thickness.

2. Standard pressure that can be withstand.

3. Weight of Tank (Empty & total).

VI. GENERAL :

1. The design shall incorporate every reasonable precaution and provisions for safety of all those concerned in the operation and maintenance of the equipment.

2. All outdoor apparatus shall be so designed that water cannot collect at any point.

3. On outdoor equipment, all bolts, nuts, washers in contact with non-ferrous parts shall be of phosphor bronze.

4. The oil gauge glass shall be fixed appropriately.

5. Insulation sheet barriers like bakelite or fiber glass shall be provided in between phases to over the length of bushing stud.

6. The gasket shall be dovetailed without joints to prevent moisture entry. In case of dovetailed joint, they shall not be more than two. The gasket shall be of good quality Neoprene or rubberized gasket.