## Sheet1
To enable entering data into the sheet, please click on 'Enable Editing'.
Please insert items from 12th row.
Every row will be considered as a distinct item.
The row, in which the two fields- 'Item Code' and 'Description' are blank, will not be considered.
If 'CREDIT ITEM' is not entered, default value '0' will be taken.
If 'Calc Field' is not entered, default value 'N' will be taken.
MAX ITEM LIMIT IN EACH EXCEL FILE IS 1000
Nit Schedule for LT & HT line Shifting & Electrification work in Raigarh-Kotra-Nandeli 5 km 4 Lane road under Sub-Division Raigarh Distt. Raigarh (C.G.)
The rates taken in the estimate are as per CGPWD,(E&M) SOR in-forced from 10-04-2026. | [7 empty] | PAC Amount 136.80 Lacs
Sr. No. | Department | SOR | Year | SOR No. | Description | Unit | Rate | Qty | Amount | Ref Serial No | CREDIT ITEM (0/1) | Calc Field(Y/N)
1 | PWD | ELECT | 2026 | 12.1 | Earthing with G.I. earth pipe 4.5 metre long, 40 mm dia including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe etc. with charcoal and salt as per specification and IS Code 3043: 1987(R 2016) | Set | 3243 | 74 | 239982 | 0 | 0 | N
2 | PWD | ELECT | 2026 | 12.12 | Supplying and laying 6 SWG G.I. wire at 0.50 metre below ground level for conductor earth electrode, including soldering, excavation and refilling the trench etc. as per specification. | Metre | 36 | 740 | 26640 | 0 | 0 | N
3 | PWD | ELECT | 2026 | 19.1 | Supply of "H" beam steel pole as per IS specifications in standard length for over head line work: 19.1.2-"H" beam steel pole 152x152x7x12 mm standard weight 37.1 kg /metre | metre | 2773 | 858 | 2379234 | 0 | 0 | N
4 | PWD | ELECT | 2026 | 19.10.5 | Erection of STEEL TUBULAR or "H" BEAM/ ISMB pole in cement concrete 1:3:6 (1 cement : 3 coarse sand : 6 graded stone aggregate 40 mm nominal size) foundation and cement concrete collar of size 0.4 metre dia and 0.50 metre height from ground level including excavation and refilling etc. as per specification of length: 11 metre to 12 metre | Each | 2894 | 121 | 350174 | 0 | 0 | N
5 | PWD | ELECT | 2026 | 20.2 | Supplying and erection of stay set complete (galvanized) with 19/20mm dia x 1.8 metre long stay rod, anchor plate of size 300mm x 300mm x 6.4 mm, thimble stay clamps, turn buckle (19/20mm x 600mm), strain insulator and specified G.I. stay wire etc. in cement concrete 1:3:6 (1 cement : 3 coarse sand : 6 graded stone aggregate 40 mm nominal size) foundation including excavation and refilling etc. as per specification. 20.2.2-With 7/3.15 mm dia G.I. stay wire | Each | 3277 | 176 | 576752 | 0 | 0 | N
6 | PWD | ELECT | 2026 | 20.6 | Supplying and erection of angle/channel iron cross arms/ bracket/ other fitting of approved size and shape including drilling of holes for insulator pins, bolts and nuts etc as per specification. | kg | 77 | 2180 | 167860 | 0 | 0 | N
7 | PWD | ELECT | 2026 | 20.10.1 | Supplying and erection of galvanized ‘D’ iron complete with shackle insulator, G.I. bolts and nuts, coach screw etc. as per specification. Shackle insulator size 75mm x 90mm | Set | 367 | 528 | 193776 | 0 | 0 | N
8 | PWD | ELECT | 2026 | 20.13 | Erection of shackle / pin insulator etc. as per specification. | Each | 23 | 528 | 12144 | 0 | 0 | N
9 | PWD | ELECT | 2026 | 20.15.3 | Supplying and fixing guard insulator or split insulator complete 50x50 mm | pair | 77 | 16 | 1232 | 0 | 0 | N
10 | PWD | ELECT | 2026 | 20.17 | Supplying and erection of MV horn gap lightening arrester. | Each | 347 | 48 | 16656 | 0 | 0 | N
11 | PWD | ELECT | 2026 | 20.20 | Supplying and erection of 11 KV gang operated air break switch on existing two pole structure with insulators and all other accessories complete including locking arangement as per specification. | Set | 6793 | 7 | 47551 | 0 | 0 | N
12 | PWD | ELECT | 2026 | 20.21 | Supplying and erection of 11 KV D.O. fuse unit on existing two pole structure with insulators and all other accessories complete including locking arangement as per specification. | Set | 4052 | 48 | 194496 | 0 | 0 | N
13 | PWD | ELECT | 2026 | 20.22 | Supplying and erection of three piece nonlinear resistor type lightning arrestor suitable for 3 wire, 11 KV overhead lines with rated voltage 9 KV (rms) with a nominal discharge current rating of 5 KA and complete with galvanised clamping arrangement, G.I. bolts, nuts, washers etc. as per specification. | Set | 5779 | 48 | 277392 | 0 | 0 | N
14 | PWD | ELECT | 2026 | 20.30 | Supplying and erection of G.I wire of size 8 SWG including binding etc. as per specification. | kg | 105 | 789 | 82845 | 0 | 0 | N
15 | PWD | ELECT | 2026 | 20.32 | Supply and erection standard ACSR (aluminium conductor steel reinforced) confirming to IS 398-1961 of approved make at existing insulator at height upto 14m from ground level including stringing, binding with insulator, jointing wherever required, jumpering, tearing off connection etc complete etc. as per specification including clearing off obstacle if any: 20.32.3-Rabbit 6/1/3.35mm dia with calculated aluminium area 52.88 sq.mm, weight 214 kg/ km (100 amps) | Km | 45355 | 28.1 | 1274475.5 | 0 | 0 | N | 136.8032
16 | PWD | ELECT | 2026 | 20.33 | Supplying and erection DANGER BOARD made MS sheet duly painted and maked as per IE rules and specification. | Each | 56 | 254 | 14224 | 0 | 0 | N
17 | PWD | ELECT | 2026 | 20.34.3 | Supply and errection of following Polymer Insulator with G.I. Bolt, Nuts and Straps etc. as per specification. 11 KV Disc Insulator | Each | 153 | 276 | 42228 | 0 | 0 | N
18 | PWD | ELECT | 2026 | 20.34.5 | 11 KV Pin Insulator with Pin | Each | 176 | 678 | 119328 | 0 | 0 | N
19 | PWD | ELECT | 2026 | 23.4.5 | Supplying and fixing of following sizes 'B' class G I pipe with welded steel flange of suitable size at both the end of every pipe length, fixing with submersible pump and lowering with the pump in the bore well including necessary rubber gasket, nuts & bolts etc. as per specification. 40 mm dia. | metre | 268 | 540 | 144720 | 0 | 0 | N
20 | PWD | ELECT | 2026 | 29.14 | Dismantling of steel pole, R. S. joist, girder pole from the cement concrete foundation with bracket, insulators, stay wires etc, refilling the pit upto ground level including shifting of dismantled material to department store. | Each | 784.7363 | 90 | 70626.27 | 0 | 0 | N
21 | PWD | ELECT | 2026 | 29.15 | Dismantling of stay set from the cement concrete foundation, refilling the pit upto ground level including shifting of dismantled material to department store. | Each | 398.4046 | 176 | 70119.2096 | 0 | 0 | N
22 | PWD | ELECT | 2026 | 30.1 | Earth work in all type soil except soft rock / hard rock with all lead and 1.5 metre lift, dressing, stacking excavated strata including refilling of excavated soil in trench / pit to ground level complete as per specification. | cum | 168 | 500 | 84000 | 0 | 0 | N
23 | PWD | ELECT | 2026 | 30.12 | Providing and laying Cast-in-situ cement concrete 1:2:4 (1 cement : 2 coarse sand : 4 graded stone aggregate 20mm including mixing with mechanical mixer, compacting with vibrator, finishing and currying etc. complete but excluding form work. | cum | 3426 | 98 | 335748 | 0 | 0 | N
24 | CSPDCL | ELECT | 2026 | Non SOR | PCC POLE 200 KG ; 9; 0 MTR LONG | Each | 5895 | 176 | 1037520 | 0 | 0 | N
25 | CSPDCL | ELECT | 2026 | Non SOR | Supply & Fixing of LT distribution Box with Cable For 63/100 kVA Transformer | Each | 2012 | 9 | 18108 | 0 | 0 | N
26 | CSPDCL | ELECT | 2026 | Non SOR | Painting and numbering etc including steel support | Each | 537 | 260 | 139620 | 0 | 0 | N
27 | CSPDCL | ELECT | 2026 | Non SOR | Handling and installation of transformer on structure 63KVA TRANSFORMER | Each | 2572 | 9 | 23148 | 0 | 0 | N
28 | CSPDCL | ELECT | 2026 | Non SOR | Handling and installation of transformer on structure 100KVA TRANSFORMER | Each | 4501 | 7 | 31507 | 0 | 0 | N
29 | CSPDCL | ELECT | 2026 | Non SOR | Supplying and Fixing of Transformer mounting 100 x 50 mm channel. | Set | 6366 | 16 | 101856 | 0 | 0 | N
30 | CSPDCL | ELECT | 2026 | Non SOR | Supplying of 11 KV Strain hardware fittings. (Strain H/W up to Rabbit.). | Each | 187 | 276 | 51612 | 0 | 0 | N
31 | CSPDCL | ELECT | 2026 | Non SOR | Supplying and Fixing of G.I. WIRES: - Barbed wire confirming to IS:2781978 | KG | 240 | 214 | 51360 | 0 | 0 | N
32 | CSPDCL | ELECT | 2026 | Non SOR | Supplying of Red oxide paint | lit. | 214 | 160 | 34240 | 0 | 0 | N
33 | CSPDCL | ELECT | 2026 | Non SOR | Supplying of Aluminium paint | lit. | 477 | 165 | 78705 | 0 | 0 | N
34 | CSPDCL | ELECT | 2026 | Non SOR | Supplying of Aluminium bobbin(Earth knob) | Each | 59 | 321 | 18939 | 0 | 0 | N
35 | CSPDCL | ELECT | 2026 | Non SOR | S/F of MS nuts and bolts 16x40mm | kg | 101 | 75 | 7575 | 0 | 0 | N
36 | CSPDCL | ELECT | 2026 | Non SOR | 16x65mm | kg | 100 | 126 | 12600 | 0 | 0 | N
37 | CSPDCL | ELECT | 2026 | Non SOR | 12x100 mm | kg | 101 | 45 | 4545 | 0 | 0 | N
38 | CSPDCL | ELECT | 2026 | Non SOR | 16x140mm | kg | 98 | 93 | 9114 | 0 | 0 | N
39 | CSPDCL | ELECT | 2026 | Non SOR | 16x200mm | kg | 98 | 94 | 9212 | 0 | 0 | N
40 | CSPDCL | ELECT | 2026 | Non SOR | Supplying and Fixing of D.O. / LA Mounting channel 75x40 mm. | No. | 2577 | 16 | 41232 | 0 | 0 | N
41 | CSPDCL | ELECT | 2026 | Non SOR | SUPPLYING OF ALUMINIUM CABLE 1C 50 SQ MM UNARMOURED LT PVC. | metre | 82.098 | 26781 | 2198666.538 | 0 | 0 | N
42 | CSPDCL | ELECT | 2026 | Non SOR | SUPPLYING OF ALUMINIUM CABLE 1C 70 SQ MM UNARMOURED LT PVC. | metre | 111.592 | 1965 | 219278.28 | 0 | 0 | N
43 | CSPDCL | ELECT | 2026 | Non SOR | SUPPLYING OF ALUMINIUM CABLE 1C 150 SQ MM UNARMOURED LT PVC. | metre | 220.434 | 1356 | 298908.504 | 0 | 0 | N
44 | CSPDCL | ELECT | 2026 | Non SOR | Supplying and Fixing of L.T. Distribution Box for 63 kVA X'mer (200 A, isolator & 6 SP MCCB of 100 A). | Each | 24329 | 9 | 218961 | 0 | 0 | N
45 | CSPDCL | ELECT | 2026 | Non SOR | Supply and Fixing L.T. Distribution Box for 100 kVA X'mer (200 A, isolator & 6 SP MCCB of 200 A). | Each | 29830 | 7 | 208810 | 0 | 0 | N
46 | CSPDCL | ELECT | 2026 | Non SOR | Supplying of 11 kV Top Clamp Angle type 65x65x6 mm. | No. | 377 | 378 | 142506 | 0 | 0 | N
47 | CSPDCL | ELECT | 2026 | Non SOR | Supplying and Fixing of 11 kV "V" Cross Arm Cleat type 75x40 mm. | No. | 1482 | 61 | 90402 | 0 | 0 | N
48 | CSPDCL | ELECT | 2026 | Non SOR | Stay clamp rail for H-beam(3kg+nut bolt) | nos | 422 | 161 | 67942 | 0 | 0 | N
49 | CSPDCL | ELECT | 2026 | Non SOR | SUPPLYING AND FIXING MS LT 5 PIN CROSS ARM SIZE 50X50X6 MM, WEIGHING 10.03 KG INCLUDING DRILLING OF HOLES FOR INSULATOR AND CLAMPING WITH NUTS AND BOLTS BUT EXCLUDING INSULATOR, CLAMP,NUTS AND BOLTS ETC. | Nos. | 1207 | 132 | 159324 | 0 | 0 | N
50 | CSPDCL | ELECT | 2026 | Non SOR | Supplying and Fixing of Single Pole Cut Point Fitting 100x50 mm (11 kV Cut point channel). | Set | 4133 | 31 | 128123 | 0 | 0 | N
51 | CSPDCL | ELECT | 2026 | Non SOR | Supplying of 11 kV M.S. Guarding Channel 100x50 mm 2210 mm long (1.1 MTR DPDC CROSS ARM) with 6 nos 18 mm dia holes for fixing of 16 mm Eye bolt and back clamp. | Set | 3182 | 16 | 50912 | 0 | 0 | N
52 | CSPDCL | ELECT | 2026 | Non SOR | Supplying and Fixing of D.C.Cross arm 4' Centre 100x50 mm Channel. | Set | 5579 | 7 | 39053 | 0 | 0 | N
53 | CSPDCL | ELECT | 2026 | Non SOR | BINDING WIRE | KG | 258 | 140 | 36120 | 0 | 0 | N
54 | CSPDCL | ELECT | 2026 | Non SOR | Supplying and Fixing of D.C.Cross arm 8' Centre 100x50 mm Channel 2 Nos. | Set | 6366 | 16 | 101856 | 0 | 0 | N
55 | CSPDCL | ELECT | 2026 | Non SOR | ROUND SHAPE RCC PLTE WITH 6 MM MS BAR | No | 201 | 220 | 44220 | 0 | 0 | N
56 | CSPDCL | ELECT | 2026 | Non SOR | I BOLT M 20 X128 MM THRED PORTION 50 MM 1 | No | 181 | 16 | 2896 | 0 | 0 | N
57 | CSPDCL | ELECT | 2026 | Non SOR | STAY CLAMP LT/ PAIR | No | 381 | 32 | 12192 | 0 | 0 | N
58 | CSPDCL | ELECT | 2026 | Non SOR | STAY CLAMP LT/ PAIR | No | 386 | 32 | 12352 | 0 | 0 | N
59 | CSPDCL | ELECT | 2026 | Non SOR | SLEEVE JOINTING AL. FOR 0.035 Q INC | No | 48 | 40 | 1920 | 0 | 0 | N
60 | CSPDCL | ELECT | 2026 | Non SOR | M S ANGLE 50X50X5 MM | No | 53 | 864 | 45792 | 0 | 0 | N
61 | CSPDCL | ELECT | 2026 | Non SOR | 11 KV ACSR COVERED CONDUCTOR 50 SQ MM | KM | 301427 | 3.99 | 1202693.73 | 0 | 0 | N
62 | CSPDCL | ELECT | 2026 | Non SOR | Supplying and Fixing of Distribution box 3 phase 5 connectors along with 2 Nos. Steel Strap & Buckles. (DISTRIBUTION BOX 3 PH 4 CONNECTOR). | No | 2147 | 2 | 4294 | 0 | 0 | N
|  |  |  | TOTAL RS OF SOR ITEM (A) |  |  |  |  | 6722202.9796
|  |  |  | TOTAL RS OF NON SOR ITEM (B) |  |  |  |  | 6958115.052
|  |  |  | GTOTAL (A+B) |  |  |  |  | 13680318.0316
|  |  |  | SAY RS |  |  |  |  | 136.8032
Sub Engineer Sub Divisional Officer Executive Engineer
P.W.D (E/M) Sub Division P.W.D (E/M) Sub Division P.W.D (E/M) Division
Raigarh (C.G.) Raigarh (C.G.) Raigarh (C.G.)