## MONO
PUBLIC WORKS DEPARTMENT (E&M) DIVISION RAIGARH (C.G.)
Estimate For Providing Road Lighting Works From Dhimrapur Chowk To Kotara Thana Chowk At Raigarh Block, District Raigarh (C.G.)
Head: 24/5054-04-337-0101-79773855
ESTIMATED COST Rs. - 141.32 Lacs only
GOVERNMENT OF CHHATTISGARH
EXECUTIVE ENGINEER
P.W.D. (E&M)
DIVISION RAIGARH (C.G.)

## FLY
Fly Sheet
Chhattisgarh State Public Works Department
1 | Name of Circle | :- | E/M P.W.D .Circle Bilaspur.
2 | Name of Division | :- | E/M P.W.D. Division Raigarh.
3 | Name of Sub – Din | :- | E/M P.W.D. Sub Division Raigarh.
4 | Head of Account | :- | 24/5054-04-337-0101-79773855
5 | Amount of Estimate | :- | ₹141.32 Lacs Only
6 | Name of Estimate | :- | Estimate For Providing Road Lighting Works From Dhimrapur Chowk To Kotara Thana Chowk At Raigarh Block, District Raigarh (C.G.)

## TECH
Technical Report & Specification
1 | Name of Work | :- | Estimate For Providing Road Lighting Works From Dhimrapur Chowk To Kotara Thana Chowk At Raigarh Block, District Raigarh (C.G.)
2 | Amount | :- | 141.32 | Lacs Only
3 | Authority | :- | Govt of Chhattisgarh
4 | Necessity | :- | Road Widening Work is proposed to be construct in Dhimrapur Chowk To Kotara Thana Chowk, At district Raigarh. So It is very important to get Road lighting work done in the proposed Aproach Road.
So the estimate has been prepared keeping in view the need of electrification work.
5 | Provision | :- | The following provision has been taken in this Estimate :-
|  |  | 1 | Internal Wiring with copper conducator in concealed PVC conduit with Modular Switch.
|  |  | 2 | Power Cable
|  |  | 3 | MAIN CUBICAL PANEL BOARD
6 | Rate | :- | Rates are as per S.O.R. for Electrical Works for P.W.D. inforce from 01-06-2020
7 | Specification | :- | The work will be carried out as per CGP WD Specification.
Sub-Engineer P.W.D. E/M Sub-Division Raigarh(C.G.)
S.D.O. P.W.D. E/M Sub-Division Raigarh(C.G.)
Executive Engineer P.W.D. E/M Division Raigarh(C.G.)

## D to UP Road
Estimate For Providing Road Lighting Works From Dhimrapur Chowk To Kotara Thana Chowk At Raigarh Block, District Raigarh (C.G.)
S.N. | S.O.R. | Particulars Of Item | Qty. | Unit | Rate | Amount
1 | 1.13 | Wiring for circuit/ sub main wiring along with earth wire with the following sizes of FRLS PVC insulated copper conductor, wire in concealed FRLS PVC conduit (heavy duty, thickness of pipe should be 2 mm) as per specification and IS: 694 (2010), IS: 9537 (2000 Part 5)
| 1.13.1 | 3 X 1.5 sq. mm in 20mm conduit | 5160 | Metre | 92 | 474720
2 | 6.28 | Supplying, installation, testing and commissioning of following 230/250 volts LED street light fitting with all accessories like driver, heat sink made of die cast aluminium with IP 66 protection and 15 KV surge protection on pole bracket, including connection, earthing, Separate housing for driver etc complete as per specification and P.F. should be greater than 0.9. LED chip efficacy ratio ≥ 120 lumens /watt.
| 6.28.14 | 250 watt | 344 | Each | 15846 | 5451024
3 | 7.1 | Supplying and fixing wall/ floor mounted metal board of welded construction, fabricated with minimum 50mmX 50mm X 6mm angle iron frame work, with horizontal and vertical intermediate members of suitable angle/flat iron for mounting of switch gears including painting etc. as per specification. | 5.76 | Sqm | 3025 | 17424
4 | 7.10 | Providing and fixing metal clad, TP&N switch fuse unit (re-wirable), 415/500 volts, with porcelain re-wireble fuses including drilling holes on the board, connections, earthing the body etc. as per specification. (Thimbeling shall be paid separately).
| 7.10.4 | 200 amps | 6 | Each | 5420 | 32520
5 | 7.18 | Providing and making interconnection in cubical panel between BBC and switchgears with following size copper strip of length upto 50cm as per specification (To be measured separately for each phase/ neutral).
| 7.18.1 | 20x3mm (100 amps) | 16 | Each | 173 | 2768
| 7.18.2 | 25x5mm (200 amps) | 8 | Each | 296 | 2368
6 | 7.19 | Fabrication, supply, installation, testing and commissioning of cubicle type compartmentalized wall/ floor mounted power cum control panel board of specified size and following depth made out of not less than 2 mm thick CRCA MS powder coated sheet with suitable size compartments for bus bars, switchgears and necessary cutouts for voltmeters, ammeters etc as per specifications including powder coating painting but without busbars, switchgears and other accessories etc complete as per specification.
| 7.19.1 | Upto 300 mm deep | 2.16 | Sqm | 6818 | 14726.88
| 7.19.2 | Above 300 mm and upto 450 mm deep | 3.6 | Sqm | 7525 | 27090
7 | 7.21 | Supply, installation, testing and commissioning of 4 pole (3 phase + neutral) copper (electric grade) bus bars in existing cubicle type compartmentalized wall/ floor mounted panel board along with suitable size and shape insulators, necessary bolts and nuts etc complete as per specification.
| 7.21.1 | 100 amp (20x3mm) | 9.6 | Metre | 1319 | 12662.4
| 7.21.2 | 200 amp (25x5mm) | 7.2 | Metre | 2382 | 17150.4
8 | 9.1 | Providing and fixing following rating and breaking capacity MCCB in existing cubicle panel board including drilling holes in cubicle panel, making connections, etc. as per specification, IS/ IEC: 60947-2 and Ics = 100 % Icu.
| 9.1.4 | 3 pole MCCB, 100A, Adjustable Thermal - Magnetic Release, 25KA | 8 | Each | 3734 | 29872
| 9.1.27 | 4 pole MCCB, 200A, Adjustable Thermal - Magnetic Release, 35KA | 2 | Each | 13051 | 26102
9 | 9.11 | Supplying and fixing SP MCB, 240 volts, 'C' curve, suitable for inductive load in the existing MCB DB complete with connections, testing and commissioning etc. as per specification.
| 9.11.2 | 6 amps to 32 amps | 344 | Each | 148 | 50912
10 | 9.14 | Supplying and fixing TP MCB, 440 volts, 'C' curve, suitable for lighting and other loads in the existing MCB DB complete with connections, testing and commissioning etc. as per specification.
| 9.14.5 | 63 amps | 4 | Each | 996 | 3984
11 | 9.27 | Supplying and fixing Low voltage (class -II) surge protection device (SPD) TP&N 440 volts, in the existing MCB DB complete with connections, testing and commissioning etc. as per specification. | 4 | Each | 8251 | 33004
12 | 10.14 | Providing and fixing 4 pole, 415/500 volts following rating (AC-1 Duty) power contactor in existing starter/ cubical panel including, connections, testing and commissioning etc. as per specification.
| 10.14.4 | 100 amps | 4 | Each | 7337 | 29348
13 | 10.17 | Providing and fixing penal mounting 230 volt LED type indicating lamp in existing cubical panel including, connections, testing and commissioning etc. as per specification. | 18 | Each | 94 | 1692
14 | 10.21 | Providing and fixing penal mounting selector switch in existing cubical panel including, connections, testing and commissioning etc. as per specification.
| 10.21.1 | For voltmeter | 18 | Each | 189 | 3402
| 10.21.2 | For ammeter | 18 | Each | 207 | 3726
15 | 10.22 | Providing and fixing following Time switch (timer) in existing panel including connection, testing and commissioning as per specification.
| 10.22.1 | Digital type | 4 | Each | 1901 | 7604
| 10.22.2 | Analoge type | 4 | Each | 2525 | 10100
16 | 10.23 | Providing and fixing panel mounting digital type VAF (Volt-amp-frequency combined) Multi Function meter of size 100x100 (NS) in existing cubical panel including connection, testing and commissioning etc. as per specification. | 4 | Each | 1201 | 4804
17 | 12.1 | Earthing with G.I. earth pipe 4.5 metre long, 40 mm dia including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe etc. with charcoal and salt as per specification and IS Code 3043: 1987(R 2016) | 168 | Set | 3243 | 544824
18 | 12.3 | Earthing with copper earth plate 600 mm X 600 mm X 3 mm thick including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe, with charcoal and salt as per specification and IS Code 3043: 1987(R 2016) | 8 | Set | 6209 | 49672
19 | 12.5 | Supplying and laying 25 mm X 5 mm copper strip at 0.50 metre below ground as strip earth electrode, including soldering, excavation and refilling the trench etc. as per specification. | 40 | Metre | 513 | 20520
20 | 12.12 | Supplying and laying 6 SWG G.I. wire at 0.50 metre below ground level for conductor earth electrode, including soldering, excavation and refilling the trench etc. as per specification. | 840 | Metre | 36 | 30240
21 | 12.16 | Providing and fixing 25 mm X 5 mm G.I. strip on surface or in recess for connections etc. as per specification. | 100 | Metre | 115 | 11500
22 | 12.19 | Providing maintenance free earthing with following size GI pipe including making bore pit of minimum 150mm dia, providing and laying approved make Earthing Electrode of Pipe-in-Pipe technology as per IS 3043(R 2016) -1987 made of corrosion free G.I. Pipes having outer pipe of 80mm dia and inner pipe of 50mm dia and filling with specified qty highly conductive compound around pipe and above that with soft soil in bore pit complete and providing masonry enclosure with cover plate having locking arrangement and watering pipe etc. as per specification:
| 12.19.1 | With 3 metre long GI Pipes and 50 kg back filling compound. | 4 | Each | 10955 | 43820
23 | 14.1 | Supplying and laying ISI marked double wall HDPE pipe (IS 14930 Part II) having corrugation on the outer wall and plan surface on inner wall in ground below road, path etc at a depth not less than 40 cm and upto 90 cm including excavation, dismantling of road if required and refilling the trench with excavated material, ramming and making the surface good etc. as per specification.
| 14.1.1 | 63 mm outer dia and 50 mm Inner dia | 2100 | Metre | 184 | 386400
| 14.1.4 | 120 mm outer dia and 103.5 mm Inner dia | 250 | Metre | 253 | 63250
24 | 14.3 | Supplying and laying following size medium class G.I. pipe in ground below road, path etc at a depth not less than 40 cm and upto 90 cm including excavation, dismantling of road if required and refilling the trench with excavated material, ramming and making the surface good etc. as per specification.
| 14.3.1 | 50 mm internal dia | 400 | Metre | 333 | 133200
25 | 15.1 | Supplying and laying following sizes one number FRLS PVC insulated/XLPE, PVC sheathed, steel armoured, aluminium conductor power cable of 1.1 KV grade direct in ground at a depth not less than 40 cm and upto 90 cm including excavtion, sand cushioning, protective covering and refilling the trench etc as per specification, IS: 1554 (1988, Part 1) / IS: 7098 (1988, Part 1).
| 15.1.11 | 3.5 x 25 sq. mm. | 4200 | Metre | 315 | 1323000
| 15.1.12 | 3.5 x 35 sq. mm. | 2100 | Metre | 316 | 663600
| 15.1.15 | 3.5 x 95 sq. mm. | 250 | Metre | 488 | 122000
26 | 15.28 | Supplying, fixing and cramping suitable size and all type aluminium ferule/ lugs to following size 1.1 KV grade power cable core / lead, pressed with high pressure cramping tool including connection to switch gear/ MCCB etc as per specification. .
| 15.28.4 | 25 sq. mm | 1344 | Each | 22 | 29568
| 15.28.5 | 35 sq. mm | 32 | Each | 20 | 640
| 15.28.8 | 95 sq. mm | 16 | Each | 26 | 416
27 | 19.8 | Supply of hot dipped galvanized (in single dip to minimum 75 micron) octogonal pole made of 3mm thick steel grade E-350 sheet having window and flush cover with locking arrangement at suitable height from base for cable termination block, pole suitably reinforced with welded steel section at window cut section to make the strength of pole unaffected, with following minimum specifications with 4 way terminal connector including 4mm thick anchor plate, 4 nos 24mm dia foundation bolts of EN8 grade, and as per IS 2062 & BS EN: 10025. (designed for wind speed upto 180km/hr, IS: 875 Part 3)
| 19.8.3 | 11 metre high, dia 210mm at bottom and 90mm at top, base plate size 300x300x20mm, foundation bolts 750mm long | 168 | Each | 20261 | 3403848
28 | 19.9 | Supply and fixing following street light pole bracket on existing pole made out of 50 mm dia MS "B" class pipe welded to 300 mm long MS pole canopy of suitable dia at a angle of 102.50 including having MS triangular stiffner of size 150 X 50 X 5 mm thick, making arrangement for tightening the bracket with pole by providing suitable size heavy duty nuts and bolts in canopy, painting with one coat of approved steel primer etc. as per specification.
| 19.9.8 | Double Over Hang 2.00 metre Long | 176 | Each | 2029 | 357104
29 | 19.11 | Erection of GI octogonal/ tubular/conical pole on existing cement concrete foundation having grouted bolts and nuts, aligning in true vertical position as per specification.
| 19.11.9 | 11 metre high | 168 | Each | 1125 | 189000
30 | 19.12 | Designing and providing suitable RCC foundation in Cement Concrete 1:2:4 (1 cement: 2 coarse sand: 4 graded stone aggregate 20 mm nominal size) for 3 mere to 12 metre high GI octagonal pole including steel reinforcement form work, embeding 2 nos 50mm dia PVC pipe for cable entry in each foundation, excavation disposal of surplus soil and curing etc. as per specification. | 59.535 | Cum | 5219 | 310713.165
31 | 30.1 | Earth work in all type soil except soft rock / hard rock with all lead and 1.5 metre lift, dressing, stacking excavated strata including refilling of excavated soil in trench / pit to ground level complete as per specification. | 1140 | Cum | 168 | 191520
| Total Amount |  |  |  |  | 14131838.845
| Say In Lacs |  |  |  |  | 141.3184
Sub-Engineer P.W.D. E/M Sub-Division Raigarh(C.G.)
S.D.O. P.W.D. E/M Sub-Division Raigarh(C.G.)
Executive Engineer P.W.D. E/M Division Raigarh(C.G.)

## NIT
To enable entering data into the sheet, please click on 'Enable Editing'.
Please insert items from 12th row.
Every row will be considered as a distinct item.
The row, in which the two fields- 'Item Code' and 'Description' are blank, will not be considered.
If 'CREDIT ITEM' is not entered, default value '0' will be taken.
If 'Calc Field' is not entered, default value 'N' will be taken.
MAX ITEM LIMIT IN EACH EXCEL FILE IS 1000
NIT SCHEDULE FOR PROVIDING Road Lighting Works From Dhimrapur Chowk To Kotara Thana Chowk At Raigarh Block, District Raigarh (C.G.)
The rates taken in the estimate are as per CGPWD,(E&M) SOR in-forced from 01-06-2020. | [7 empty] | PAC Amount 141.32 Lacs
Sr. No. | Department | SOR | Year | S.O.R. | Particulars Of Item | Qty. | Unit | Rate | Amount | Ref Serial No | CREDIT ITEM (0/1) | Calc Field(Y/N)
1 | PWD | ELECT | 2020 | 1.13.1 | Wiring for circuit/ sub main wiring along with earth wire with the following sizes of FRLS PVC insulated copper conductor, wire in concealed FRLS PVC conduit (heavy duty, thickness of pipe should be 2 mm) as per specification and IS: 694 (2010), IS: 9537 (2000 Part 5) 3 X 1.5 sq. mm in 20mm conduit | 5160 | Metre | 92 | 474720 | 0 | 0 | N
2 | PWD | ELECT | 2020 | 6.28.14 | Supplying, installation, testing and commissioning of following 230/250 volts LED street light fitting with all accessories like driver, heat sink made of die cast aluminium with IP 66 protection and 15 KV surge protection on pole bracket, including connection, earthing, Separate housing for driver etc complete as per specification and P.F. should be greater than 0.9. LED chip efficacy ratio ≥ 120 lumens /watt. 250 watt | 344 | Each | 15846 | 5451024 | 0 | 0 | N
3 | PWD | ELECT | 2020 | 7.1 | Supplying and fixing wall/ floor mounted metal board of welded construction, fabricated with minimum 50mmX 50mm X 6mm angle iron frame work, with horizontal and vertical intermediate members of suitable angle/flat iron for mounting of switch gears including painting etc. as per specification. | 5.76 | Sqm | 3025 | 17424 | 0 | 0 | N
4 | PWD | ELECT | 2020 | 7.10.4 | Providing and fixing metal clad, TP&N switch fuse unit (re-wirable), 415/500 volts, with porcelain re-wireble fuses including drilling holes on the board, connections, earthing the body etc. as per specification. (Thimbeling shall be paid separately). 200 amps | 6 | Each | 5420 | 32520 | 0 | 0 | N
5 | PWD | ELECT | 2020 | 7.18.1 | Providing and making interconnection in cubical panel between BBC and switchgears with following size copper strip of length upto 50cm as per specification (To be measured separately for each phase/ neutral).20x3mm (100 amps) | 16 | Each | 173 | 2768 | 0 | 0 | N
6 | PWD | ELECT | 2020 | 7.18.2 | 25x5mm (200 amps) | 8 | Each | 296 | 2368 | 0 | 0 | N
7 | PWD | ELECT | 2020 | 7.19.1 | Fabrication, supply, installation, testing and commissioning of cubicle type compartmentalized wall/ floor mounted power cum control panel board of specified size and following depth made out of not less than 2 mm thick CRCA MS powder coated sheet with suitable size compartments for bus bars, switchgears and necessary cutouts for voltmeters, ammeters etc as per specifications including powder coating painting but without busbars, switchgears and other accessories etc complete as per specification.Upto 300 mm deep | 2.16 | Sqm | 6818 | 14726.88 | 0 | 0 | N
8 | PWD | ELECT | 2020 | 7.19.2 | Above 300 mm and upto 450 mm deep | 3.6 | Sqm | 7525 | 27090 | 0 | 0 | N
9 | PWD | ELECT | 2020 | 7.21.1 | Supply, installation, testing and commissioning of 4 pole (3 phase + neutral) copper (electric grade) bus bars in existing cubicle type compartmentalized wall/ floor mounted panel board along with suitable size and shape insulators, necessary bolts and nuts etc complete as per specification.100 amp (20x3mm) | 9.6 | Metre | 1319 | 12662.4 | 0 | 0 | N
10 | PWD | ELECT | 2020 | 7.21.2 | 200 amp (25x5mm) | 7.2 | Metre | 2382 | 17150.4 | 0 | 0 | N
11 | PWD | ELECT | 2020 | 9.1.4 | Providing and fixing following rating and breaking capacity MCCB in existing cubicle panel board including drilling holes in cubicle panel, making connections, etc. as per specification, IS/ IEC: 60947-2 and Ics = 100 % Icu. 3 pole MCCB, 100A, Adjustable Thermal - Magnetic Release, 25KA | 8 | Each | 3734 | 29872 | 0 | 0 | N
12 | PWD | ELECT | 2020 | 9.1.27 | 4 pole MCCB, 200A, Adjustable Thermal - Magnetic Release, 35KA | 2 | Each | 13051 | 26102 | 0 | 0 | N
13 | PWD | ELECT | 2020 | 9.11.2 | Supplying and fixing SP MCB, 240 volts, 'C' curve, suitable for inductive load in the existing MCB DB complete with connections, testing and commissioning etc. as per specification.6 amps to 32 amps | 344 | Each | 148 | 50912 | 0 | 0 | N
14 | PWD | ELECT | 2020 | 9.14.5 | Supplying and fixing TP MCB, 440 volts, 'C' curve, suitable for lighting and other loads in the existing MCB DB complete with connections, testing and commissioning etc. as per specification. 63 amps | 4 | Each | 996 | 3984 | 0 | 0 | N
15 | PWD | ELECT | 2020 | 9.27 | Supplying and fixing Low voltage (class -II) surge protection device (SPD) TP&N 440 volts, in the existing MCB DB complete with connections, testing and commissioning etc. as per specification. | 4 | Each | 8251 | 33004 | 0 | 0 | N
16 | PWD | ELECT | 2020 | 10.14.4 | Providing and fixing 4 pole, 415/500 volts following rating (AC-1 Duty) power contactor in existing starter/ cubical panel including, connections, testing and commissioning etc. as per specification. 100 amps | 4 | Each | 7337 | 29348 | 0 | 0 | N
17 | PWD | ELECT | 2020 | 10.17 | Providing and fixing penal mounting 230 volt LED type indicating lamp in existing cubical panel including, connections, testing and commissioning etc. as per specification. | 18 | Each | 94 | 1692 | 0 | 0 | N
18 | PWD | ELECT | 2020 | 10.21.1 | Providing and fixing penal mounting selector switch in existing cubical panel including, connections, testing and commissioning etc. as per specification. For voltmeter | 18 | Each | 189 | 3402 | 0 | 0 | N
19 | PWD | ELECT | 2020 | 10.21.2 | For ammeter | 18 | Each | 207 | 3726 | 0 | 0 | N
20 | PWD | ELECT | 2020 | 10.22.1 | Providing and fixing following Time switch (timer) in existing panel including connection, testing and commissioning as per specification.Digital type | 4 | Each | 1901 | 7604 | 0 | 0 | N
21 | PWD | ELECT | 2020 | 10.22.2 | Analoge type | 4 | Each | 2525 | 10100 | 0 | 0 | N
22 | PWD | ELECT | 2020 | 10.23 | Providing and fixing panel mounting digital type VAF (Volt-amp-frequency combined) Multi Function meter of size 100x100 (NS) in existing cubical panel including connection, testing and commissioning etc. as per specification. | 4 | Each | 1201 | 4804 | 0 | 0 | N
23 | PWD | ELECT | 2020 | 12.1 | Earthing with G.I. earth pipe 4.5 metre long, 40 mm dia including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe etc. with charcoal and salt as per specification and IS Code 3043: 1987(R 2016) | 168 | Set | 3243 | 544824 | 0 | 0 | N
24 | PWD | ELECT | 2020 | 12.3 | Earthing with copper earth plate 600 mm X 600 mm X 3 mm thick including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe, with charcoal and salt as per specification and IS Code 3043: 1987(R 2016) | 8 | Set | 6209 | 49672 | 0 | 0 | N
25 | PWD | ELECT | 2020 | 12.5 | Supplying and laying 25 mm X 5 mm copper strip at 0.50 metre below ground as strip earth electrode, including soldering, excavation and refilling the trench etc. as per specification. | 40 | Metre | 513 | 20520 | 0 | 0 | N
26 | PWD | ELECT | 2020 | 12.12 | Supplying and laying 6 SWG G.I. wire at 0.50 metre below ground level for conductor earth electrode, including soldering, excavation and refilling the trench etc. as per specification. | 840 | Metre | 36 | 30240 | 0 | 0 | N
27 | PWD | ELECT | 2020 | 12.16 | Providing and fixing 25 mm X 5 mm G.I. strip on surface or in recess for connections etc. as per specification. | 100 | Metre | 115 | 11500 | 0 | 0 | N
28 | PWD | ELECT | 2020 | 12.19.1 | Providing maintenance free earthing with following size GI pipe including making bore pit of minimum 150mm dia, providing and laying approved make Earthing Electrode of Pipe-in-Pipe technology as per IS 3043(R 2016) -1987 made of corrosion free G.I. Pipes having outer pipe of 80mm dia and inner pipe of 50mm dia and filling with specified qty highly conductive compound around pipe and above that with soft soil in bore pit complete and providing masonry enclosure with cover plate having locking arrangement and watering pipe etc. as per specification:With 3 metre long GI Pipes and 50 kg back filling compound. | 4 | Each | 10955 | 43820 | 0 | 0 | N
29 | PWD | ELECT | 2020 | 14.1.1 | Supplying and laying ISI marked double wall HDPE pipe (IS 14930 Part II) having corrugation on the outer wall and plan surface on inner wall in ground below road, path etc at a depth not less than 40 cm and upto 90 cm including excavation, dismantling of road if required and refilling the trench with excavated material, ramming and making the surface good etc. as per specification. 63 mm outer dia and 50 mm Inner dia | 2100 | Metre | 184 | 386400 | 0 | 0 | N
30 | PWD | ELECT | 2020 | 14.1.4 | 120 mm outer dia and 103.5 mm Inner dia | 250 | Metre | 253 | 63250 | 0 | 0 | N
31 | PWD | ELECT | 2020 | 14.3.1 | Supplying and laying following size medium class G.I. pipe in ground below road, path etc at a depth not less than 40 cm and upto 90 cm including excavation, dismantling of road if required and refilling the trench with excavated material, ramming and making the surface good etc. as per specification.50 mm internal dia | 400 | Metre | 333 | 133200 | 0 | 0 | N
32 | PWD | ELECT | 2020 | 15.1.11 | Supplying and laying following sizes one number FRLS PVC insulated/XLPE, PVC sheathed, steel armoured, aluminium conductor power cable of 1.1 KV grade direct in ground at a depth not less than 40 cm and upto 90 cm including excavtion, sand cushioning, protective covering and refilling the trench etc as per specification, IS: 1554 (1988, Part 1) / IS: 7098 (1988, Part 1). 3.5 x 25 sq. mm. | 4200 | Metre | 315 | 1323000 | 0 | 0 | N
33 | PWD | ELECT | 2020 | 15.1.12 | 3.5 x 35 sq. mm. | 2100 | Metre | 316 | 663600 | 0 | 0 | N
34 | PWD | ELECT | 2020 | 15.1.15 | 3.5 x 95 sq. mm. | 250 | Metre | 488 | 122000 | 0 | 0 | N
35 | PWD | ELECT | 2020 | 15.28.4 | Supplying, fixing and cramping suitable size and all type aluminium ferule/ lugs to following size 1.1 KV grade power cable core / lead, pressed with high pressure cramping tool including connection to switch gear/ MCCB etc as per specification. .25 sq. mm | 1344 | Each | 22 | 29568 | 0 | 0 | N
36 | PWD | ELECT | 2020 | 15.28.5 | 35 sq. mm | 32 | Each | 20 | 640 | 0 | 0 | N
37 | PWD | ELECT | 2020 | 15.28.8 | 95 sq. mm | 16 | Each | 26 | 416 | 0 | 0 | N
38 | PWD | ELECT | 2020 | 19.8.3 | Supply of hot dipped galvanized (in single dip to minimum 75 micron) octogonal pole made of 3mm thick steel grade E-350 sheet having window and flush cover with locking arrangement at suitable height from base for cable termination block, pole suitably reinforced with welded steel section at window cut section to make the strength of pole unaffected, with following minimum specifications with 4 way terminal connector including 4mm thick anchor plate, 4 nos 24mm dia foundation bolts of EN8 grade, and as per IS 2062 & BS EN: 10025. (designed for wind speed upto 180km/hr, IS: 875 Part 3) 11 metre high, dia 210mm at bottom and 90mm at top, base plate size 300x300x20mm, foundation bolts 750mm long | 168 | Each | 20261 | 3403848 | 0 | 0 | N
39 | PWD | ELECT | 2020 | 19.9.8 | Supply and fixing following street light pole bracket on existing pole made out of 50 mm dia MS "B" class pipe welded to 300 mm long MS pole canopy of suitable dia at a angle of 102.50 including having MS triangular stiffner of size 150 X 50 X 5 mm thick, making arrangement for tightening the bracket with pole by providing suitable size heavy duty nuts and bolts in canopy, painting with one coat of approved steel primer etc. as per specification.Double Over Hang 2.00 metre Long | 176 | Each | 2029 | 357104 | 0 | 0 | N
40 | PWD | ELECT | 2020 | 19.11.9 | Erection of GI octogonal/ tubular/conical pole on existing cement concrete foundation having grouted bolts and nuts, aligning in true vertical position as per specification. 11 metre high | 168 | Each | 1125 | 189000 | 0 | 0 | N
41 | PWD | ELECT | 2020 | 19.12 | Designing and providing suitable RCC foundation in Cement Concrete 1:2:4 (1 cement: 2 coarse sand: 4 graded stone aggregate 20 mm nominal size) for 3 mere to 12 metre high GI octagonal pole including steel reinforcement form work, embeding 2 nos 50mm dia PVC pipe for cable entry in each foundation, excavation disposal of surplus soil and curing etc. as per specification. | 59.535 | Cum | 5219 | 310713.165 | 0 | 0 | N
42 | PWD | ELECT | 2020 | 30.1 | Earth work in all type soil except soft rock / hard rock with all lead and 1.5 metre lift, dressing, stacking excavated strata including refilling of excavated soil in trench / pit to ground level complete as per specification. | 1140 | Cum | 168 | 191520 | 0 | 0 | N
| TOTAL AMOUNT | [7 empty] | 14131838.845
| SAY IN LACS | [7 empty] | 141.3184
Sub-Engineer P.W.D. E/M Sub-Division Raigarh(C.G.)
S.D.O. P.W.D. E/M Sub-Division Raigarh(C.G.)
Executive Engineer P.W.D. E/M Division Raigarh(C.G.)

## D to UP Road (new sor)
Estimate For Providing Road Lighting Works From Dhimrapur Chowk To Kotara Thana Chowk At Raigarh Block, District Raigarh (C.G.)
S.N. | S.O.R. | Particulars Of Item | Qty. | Unit | Rate | Amount
1 | 1.13 | Wiring for circuit/ sub main wiring along with earth wire with the following sizes of FRLS PVC insulated copper conductor, wire in concealed FRLS PVC conduit (heavy duty, thickness of pipe should be 2 mm) as per specification and IS: 694 (2010), IS: 9537 (2000 Part 5)
| 1.13.1 | 3 X 1.5 sq. mm in 20mm conduit | 5160 | Metre | 92 | 474720
2 | 6.28 | Supplying, installation, testing and commissioning of following 230/250 volts LED street light fitting with all accessories like driver, heat sink made of die cast aluminium with IP 66 protection and 15 KV surge protection on pole bracket, including connection, earthing, Separate housing for driver etc complete as per specification and P.F. should be greater than 0.9. LED chip efficacy ratio ≥ 120 lumens /watt.
| 6.28.14 | 210 watt | 344 | Each | 9347 | 3215368
3 | 7.1 | Supplying and fixing wall/ floor mounted metal board of welded construction, fabricated with minimum 50mmX 50mm X 6mm angle iron frame work, with horizontal and vertical intermediate members of suitable angle/flat iron for mounting of switch gears including painting etc. as per specification. | 5.76 | Sqm | 3025 | 17424
4 | 7.10 | Providing and fixing metal clad, TP&N switch fuse unit (re-wirable), 415/500 volts, with porcelain re-wireble fuses including drilling holes on the board, connections, earthing the body etc. as per specification. (Thimbeling shall be paid separately).
| 7.10.4 | 200 amps | 6 | Each | 5420 | 32520
5 | 7.18 | Providing and making interconnection in cubical panel between BBC and switchgears with following size copper strip of length upto 50cm as per specification (To be measured separately for each phase/ neutral).
| 7.18.1 | 20x3mm (100 amps) | 16 | Each | 173 | 2768
| 7.18.2 | 25x5mm (200 amps) | 8 | Each | 296 | 2368
6 | 7.19 | Fabrication, supply, installation, testing and commissioning of cubicle type compartmentalized wall/ floor mounted power cum control panel board of specified size and following depth made out of not less than 2 mm thick CRCA MS powder coated sheet with suitable size compartments for bus bars, switchgears and necessary cutouts for voltmeters, ammeters etc as per specifications including powder coating painting but without busbars, switchgears and other accessories etc complete as per specification.
| 7.19.1 | Upto 300 mm deep | 2.16 | Sqm | 6818 | 14726.88
| 7.19.2 | Above 300 mm and upto 450 mm deep | 3.6 | Sqm | 7525 | 27090
7 | 7.21 | Supply, installation, testing and commissioning of 4 pole (3 phase + neutral) copper (electric grade) bus bars in existing cubicle type compartmentalized wall/ floor mounted panel board along with suitable size and shape insulators, necessary bolts and nuts etc complete as per specification.
| 7.21.1 | 100 amp (20x3mm) | 9.6 | Metre | 1319 | 12662.4
| 7.21.2 | 200 amp (25x5mm) | 7.2 | Metre | 2382 | 17150.4
8 | 9.1 | Providing and fixing following rating and breaking capacity MCCB in existing cubicle panel board including drilling holes in cubicle panel, making connections, etc. as per specification, IS/ IEC: 60947-2 and Ics = 100 % Icu.
| 9.1.4 | 3 pole MCCB, 100A, Adjustable Thermal - Magnetic Release, 25KA | 8 | Each | 3734 | 29872
| 9.1.27 | 4 pole MCCB, 200A, Adjustable Thermal - Magnetic Release, 35KA | 2 | Each | 13051 | 26102
9 | 9.11 | Supplying and fixing SP MCB, 240 volts, 'C' curve, suitable for inductive load in the existing MCB DB complete with connections, testing and commissioning etc. as per specification.
| 9.11.2 | 6 amps to 32 amps | 344 | Each | 148 | 50912
10 | 9.14 | Supplying and fixing TP MCB, 440 volts, 'C' curve, suitable for lighting and other loads in the existing MCB DB complete with connections, testing and commissioning etc. as per specification.
| 9.14.5 | 63 amps | 4 | Each | 996 | 3984
11 | 9.27 | Supplying and fixing Low voltage (class -II) surge protection device (SPD) TP&N 440 volts, in the existing MCB DB complete with connections, testing and commissioning etc. as per specification. | 4 | Each | 8251 | 33004
12 | 10.14 | Providing and fixing 4 pole, 415/500 volts following rating (AC-1 Duty) power contactor in existing starter/ cubical panel including, connections, testing and commissioning etc. as per specification.
| 10.14.4 | 100 amps | 4 | Each | 7337 | 29348
13 | 10.17 | Providing and fixing penal mounting 230 volt LED type indicating lamp in existing cubical panel including, connections, testing and commissioning etc. as per specification. | 18 | Each | 94 | 1692
14 | 10.21 | Providing and fixing penal mounting selector switch in existing cubical panel including, connections, testing and commissioning etc. as per specification.
| 10.21.1 | For voltmeter | 18 | Each | 189 | 3402
| 10.21.2 | For ammeter | 18 | Each | 207 | 3726
15 | 10.22 | Providing and fixing following Time switch (timer) in existing panel including connection, testing and commissioning as per specification.
| 10.22.1 | Digital type | 4 | Each | 1901 | 7604
| 10.22.2 | Analoge type | 4 | Each | 2525 | 10100
16 | 10.23 | Providing and fixing panel mounting digital type VAF (Volt-amp-frequency combined) Multi Function meter of size 100x100 (NS) in existing cubical panel including connection, testing and commissioning etc. as per specification. | 4 | Each | 1201 | 4804
17 | 12.1 | Earthing with G.I. earth pipe 4.5 metre long, 40 mm dia including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe etc. with charcoal and salt as per specification and IS Code 3043: 1987(R 2016) | 168 | Set | 3243 | 544824
18 | 12.3 | Earthing with copper earth plate 600 mm X 600 mm X 3 mm thick including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe, with charcoal and salt as per specification and IS Code 3043: 1987(R 2016) | 8 | Set | 6209 | 49672
19 | 12.5 | Supplying and laying 25 mm X 5 mm copper strip at 0.50 metre below ground as strip earth electrode, including soldering, excavation and refilling the trench etc. as per specification. | 40 | Metre | 513 | 20520
20 | 12.12 | Supplying and laying 6 SWG G.I. wire at 0.50 metre below ground level for conductor earth electrode, including soldering, excavation and refilling the trench etc. as per specification. | 840 | Metre | 36 | 30240
21 | 12.16 | Providing and fixing 25 mm X 5 mm G.I. strip on surface or in recess for connections etc. as per specification. | 100 | Metre | 115 | 11500
22 | 12.19 | Providing maintenance free earthing with following size GI pipe including making bore pit of minimum 150mm dia, providing and laying approved make Earthing Electrode of Pipe-in-Pipe technology as per IS 3043(R 2016) -1987 made of corrosion free G.I. Pipes having outer pipe of 80mm dia and inner pipe of 50mm dia and filling with specified qty highly conductive compound around pipe and above that with soft soil in bore pit complete and providing masonry enclosure with cover plate having locking arrangement and watering pipe etc. as per specification:
| 12.19.1 | With 3 metre long GI Pipes and 50 kg back filling compound. | 4 | Each | 10955 | 43820
23 | 14.1 | Supplying and laying ISI marked double wall HDPE pipe (IS 14930 Part II) having corrugation on the outer wall and plan surface on inner wall in ground below road, path etc at a depth not less than 40 cm and upto 90 cm including excavation, dismantling of road if required and refilling the trench with excavated material, ramming and making the surface good etc. as per specification.
| 14.1.1 | 63 mm outer dia and 50 mm Inner dia | 3500 | Metre | 184 | 644000
| 14.1.4 | 120 mm outer dia and 103.5 mm Inner dia | 750 | Metre | 253 | 189750
24 | 14.3 | Supplying and laying following size medium class G.I. pipe in ground below road, path etc at a depth not less than 40 cm and upto 90 cm including excavation, dismantling of road if required and refilling the trench with excavated material, ramming and making the surface good etc. as per specification.
| 14.3.1 | 50 mm internal dia | 700 | Metre | 333 | 233100
25 | 15.1 | Supplying and laying following sizes one number FRLS PVC insulated/XLPE, PVC sheathed, steel armoured, aluminium conductor power cable of 1.1 KV grade direct in ground at a depth not less than 40 cm and upto 90 cm including excavtion, sand cushioning, protective covering and refilling the trench etc as per specification, IS: 1554 (1988, Part 1) / IS: 7098 (1988, Part 1).
| 15.1.11 | 3.5 x 25 sq. mm. | 5000 | Metre | 315 | 1575000
| 15.1.12 | 3.5 x 35 sq. mm. | 3000 | Metre | 316 | 948000
| 15.1.15 | 3.5 x 95 sq. mm. | 550 | Metre | 488 | 268400
26 | 15.28 | Supplying, fixing and cramping suitable size and all type aluminium ferule/ lugs to following size 1.1 KV grade power cable core / lead, pressed with high pressure cramping tool including connection to switch gear/ MCCB etc as per specification. .
| 15.28.4 | 25 sq. mm | 1344 | Each | 22 | 29568
| 15.28.5 | 35 sq. mm | 32 | Each | 20 | 640
| 15.28.8 | 95 sq. mm | 16 | Each | 26 | 416
27 | 19.8 | Supply of hot dipped galvanized (in single dip to minimum 75 micron) octogonal pole made of 3mm thick steel grade E-350 sheet having window and flush cover with locking arrangement at suitable height from base for cable termination block, pole suitably reinforced with welded steel section at window cut section to make the strength of pole unaffected, with following minimum specifications with 4 way terminal connector including 4mm thick anchor plate, 4 nos 24mm dia foundation bolts of EN8 grade, and as per IS 2062 & BS EN: 10025. (designed for wind speed upto 180km/hr, IS: 875 Part 3)
| 19.8.3 | 11 metre high, dia 210mm at bottom and 90mm at top, base plate size 300x300x20mm, foundation bolts 750mm long | 168 | Each | 20261 | 3403848
28 | 19.9 | Supply and fixing following street light pole bracket on existing pole made out of 50 mm dia MS "B" class pipe welded to 300 mm long MS pole canopy of suitable dia at a angle of 102.50 including having MS triangular stiffner of size 150 X 50 X 5 mm thick, making arrangement for tightening the bracket with pole by providing suitable size heavy duty nuts and bolts in canopy, painting with one coat of approved steel primer etc. as per specification.
| 19.9.8 | Double Over Hang 2.00 metre Long | 176 | Each | 2029 | 357104
29 | 19.11 | Erection of GI octogonal/ tubular/conical pole on existing cement concrete foundation having grouted bolts and nuts, aligning in true vertical position as per specification.
| 19.11.9 | 11 metre high | 168 | Each | 1125 | 189000
30 | 19.12 | Designing and providing suitable RCC foundation in Cement Concrete 1:2:4 (1 cement: 2 coarse sand: 4 graded stone aggregate 20 mm nominal size) for 3 mere to 12 metre high GI octagonal pole including steel reinforcement form work, embeding 2 nos 50mm dia PVC pipe for cable entry in each foundation, excavation disposal of surplus soil and curing etc. as per specification. | 204.5 | Cum | 5219 | 1067285.5
31 | 30.1 | Earth work in all type soil except soft rock / hard rock with all lead and 1.5 metre lift, dressing, stacking excavated strata including refilling of excavated soil in trench / pit to ground level complete as per specification. | 3000 | Cum | 168 | 504000
| Total Amount |  |  |  |  | 14132035.18
|  | G. Total Amount |  |  |  | 14132035.18
| Say In Lacs |  |  |  |  | 141.3204
Sub-Engineer P.W.D. E/M Sub-Division Raigarh(C.G.)
S.D.O. P.W.D. E/M Sub-Division Raigarh(C.G.)
Executive Engineer P.W.D. E/M Division Raigarh(C.G.)

## NIT (new)
To enable entering data into the sheet, please click on 'Enable Editing'.
Please insert items from 12th row.
Every row will be considered as a distinct item.
The row, in which the two fields- 'Item Code' and 'Description' are blank, will not be considered.
If 'CREDIT ITEM' is not entered, default value '0' will be taken.
If 'Calc Field' is not entered, default value 'N' will be taken.
MAX ITEM LIMIT IN EACH EXCEL FILE IS 1000
NIT SCHEDULE FOR Providing Road Lighting Works From Dhimrapur Chowk To Kotara Thana Chowk At Raigarh Block, District Raigarh (C.G.)
The rates taken in the estimate are as per CGPWD,(E&M) SOR in-forced from 01-06-2020. | [7 empty] | PAC Amount 141.32 Lacs
Sr. No. | Department | SOR | Year | S.O.R. | Particulars Of Item | Qty. | Unit | Rate | Amount | Ref Serial No | CREDIT ITEM (0/1) | Calc Field(Y/N)
1 | PWD | ELECT | 2020 | 1.13.1 | Wiring for circuit/ sub main wiring along with earth wire with the following sizes of FRLS PVC insulated copper conductor, wire in concealed FRLS PVC conduit (heavy duty, thickness of pipe should be 2 mm) as per specification and IS: 694 (2010), IS: 9537 (2000 Part 5) 3 X 1.5 sq. mm in 20mm conduit | 5160 | Metre | 92 | 474720 | 0 | 0 | N
2 | PWD | ELECT | 2020 | 6.28.14 | Supplying, installation, testing and commissioning of following 230/250 volts LED street light fitting with all accessories like driver, heat sink made of die cast aluminium with IP 66 protection and 15 KV surge protection on pole bracket, including connection, earthing, Separate housing for driver etc complete as per specification and P.F. should be greater than 0.9. LED chip efficacy ratio ≥ 120 lumens /watt. 150 watt | 344 | Each | 9347 | 3215368 | 0 | 0 | N
3 | PWD | ELECT | 2020 | 7.1 | Supplying and fixing wall/ floor mounted metal board of welded construction, fabricated with minimum 50mmX 50mm X 6mm angle iron frame work, with horizontal and vertical intermediate members of suitable angle/flat iron for mounting of switch gears including painting etc. as per specification. | 5.76 | Sqm | 3025 | 17424 | 0 | 0 | N
4 | PWD | ELECT | 2020 | 7.10.4 | Providing and fixing metal clad, TP&N switch fuse unit (re-wirable), 415/500 volts, with porcelain re-wireble fuses including drilling holes on the board, connections, earthing the body etc. as per specification. (Thimbeling shall be paid separately). 200 amps | 6 | Each | 5420 | 32520 | 0 | 0 | N
5 | PWD | ELECT | 2020 | 7.18.1 | Providing and making interconnection in cubical panel between BBC and switchgears with following size copper strip of length upto 50cm as per specification (To be measured separately for each phase/ neutral).20x3mm (100 amps) | 16 | Each | 173 | 2768 | 0 | 0 | N
6 | PWD | ELECT | 2020 | 7.18.2 | 25x5mm (200 amps) | 8 | Each | 296 | 2368 | 0 | 0 | N
7 | PWD | ELECT | 2020 | 7.19.1 | Fabrication, supply, installation, testing and commissioning of cubicle type compartmentalized wall/ floor mounted power cum control panel board of specified size and following depth made out of not less than 2 mm thick CRCA MS powder coated sheet with suitable size compartments for bus bars, switchgears and necessary cutouts for voltmeters, ammeters etc as per specifications including powder coating painting but without busbars, switchgears and other accessories etc complete as per specification.Upto 300 mm deep | 2.16 | Sqm | 6818 | 14726.88 | 0 | 0 | N
8 | PWD | ELECT | 2020 | 7.19.2 | Above 300 mm and upto 450 mm deep | 3.6 | Sqm | 7525 | 27090 | 0 | 0 | N
9 | PWD | ELECT | 2020 | 7.21.1 | Supply, installation, testing and commissioning of 4 pole (3 phase + neutral) copper (electric grade) bus bars in existing cubicle type compartmentalized wall/ floor mounted panel board along with suitable size and shape insulators, necessary bolts and nuts etc complete as per specification.100 amp (20x3mm) | 9.6 | Metre | 1319 | 12662.4 | 0 | 0 | N
10 | PWD | ELECT | 2020 | 7.21.2 | 200 amp (25x5mm) | 7.2 | Metre | 2382 | 17150.4 | 0 | 0 | N
11 | PWD | ELECT | 2020 | 9.1.4 | Providing and fixing following rating and breaking capacity MCCB in existing cubicle panel board including drilling holes in cubicle panel, making connections, etc. as per specification, IS/ IEC: 60947-2 and Ics = 100 % Icu. 3 pole MCCB, 100A, Adjustable Thermal - Magnetic Release, 25KA | 8 | Each | 3734 | 29872 | 0 | 0 | N
12 | PWD | ELECT | 2020 | 9.1.27 | 4 pole MCCB, 200A, Adjustable Thermal - Magnetic Release, 35KA | 2 | Each | 13051 | 26102 | 0 | 0 | N
13 | PWD | ELECT | 2020 | 9.11.2 | Supplying and fixing SP MCB, 240 volts, 'C' curve, suitable for inductive load in the existing MCB DB complete with connections, testing and commissioning etc. as per specification.6 amps to 32 amps | 344 | Each | 148 | 50912 | 0 | 0 | N
14 | PWD | ELECT | 2020 | 9.14.5 | Supplying and fixing TP MCB, 440 volts, 'C' curve, suitable for lighting and other loads in the existing MCB DB complete with connections, testing and commissioning etc. as per specification. 63 amps | 4 | Each | 996 | 3984 | 0 | 0 | N
15 | PWD | ELECT | 2020 | 9.27 | Supplying and fixing Low voltage (class -II) surge protection device (SPD) TP&N 440 volts, in the existing MCB DB complete with connections, testing and commissioning etc. as per specification. | 4 | Each | 8251 | 33004 | 0 | 0 | N
16 | PWD | ELECT | 2020 | 10.14.4 | Providing and fixing 4 pole, 415/500 volts following rating (AC-1 Duty) power contactor in existing starter/ cubical panel including, connections, testing and commissioning etc. as per specification. 100 amps | 4 | Each | 7337 | 29348 | 0 | 0 | N
17 | PWD | ELECT | 2020 | 10.17 | Providing and fixing penal mounting 230 volt LED type indicating lamp in existing cubical panel including, connections, testing and commissioning etc. as per specification. | 18 | Each | 94 | 1692 | 0 | 0 | N
18 | PWD | ELECT | 2020 | 10.21.1 | Providing and fixing penal mounting selector switch in existing cubical panel including, connections, testing and commissioning etc. as per specification. For voltmeter | 18 | Each | 189 | 3402 | 0 | 0 | N
19 | PWD | ELECT | 2020 | 10.21.2 | For ammeter | 18 | Each | 207 | 3726 | 0 | 0 | N
20 | PWD | ELECT | 2020 | 10.22.1 | Providing and fixing following Time switch (timer) in existing panel including connection, testing and commissioning as per specification.Digital type | 4 | Each | 1901 | 7604 | 0 | 0 | N
21 | PWD | ELECT | 2020 | 10.22.2 | Analoge type | 4 | Each | 2525 | 10100 | 0 | 0 | N
22 | PWD | ELECT | 2020 | 10.23 | Providing and fixing panel mounting digital type VAF (Volt-amp-frequency combined) Multi Function meter of size 100x100 (NS) in existing cubical panel including connection, testing and commissioning etc. as per specification. | 4 | Each | 1201 | 4804 | 0 | 0 | N
23 | PWD | ELECT | 2020 | 12.1 | Earthing with G.I. earth pipe 4.5 metre long, 40 mm dia including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe etc. with charcoal and salt as per specification and IS Code 3043: 1987(R 2016) | 168 | Set | 3243 | 544824 | 0 | 0 | N
24 | PWD | ELECT | 2020 | 12.3 | Earthing with copper earth plate 600 mm X 600 mm X 3 mm thick including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe, with charcoal and salt as per specification and IS Code 3043: 1987(R 2016) | 8 | Set | 6209 | 49672 | 0 | 0 | N
25 | PWD | ELECT | 2020 | 12.5 | Supplying and laying 25 mm X 5 mm copper strip at 0.50 metre below ground as strip earth electrode, including soldering, excavation and refilling the trench etc. as per specification. | 40 | Metre | 513 | 20520 | 0 | 0 | N
26 | PWD | ELECT | 2020 | 12.12 | Supplying and laying 6 SWG G.I. wire at 0.50 metre below ground level for conductor earth electrode, including soldering, excavation and refilling the trench etc. as per specification. | 840 | Metre | 36 | 30240 | 0 | 0 | N
27 | PWD | ELECT | 2020 | 12.16 | Providing and fixing 25 mm X 5 mm G.I. strip on surface or in recess for connections etc. as per specification. | 100 | Metre | 115 | 11500 | 0 | 0 | N
28 | PWD | ELECT | 2020 | 12.19.1 | Providing maintenance free earthing with following size GI pipe including making bore pit of minimum 150mm dia, providing and laying approved make Earthing Electrode of Pipe-in-Pipe technology as per IS 3043(R 2016) -1987 made of corrosion free G.I. Pipes having outer pipe of 80mm dia and inner pipe of 50mm dia and filling with specified qty highly conductive compound around pipe and above that with soft soil in bore pit complete and providing masonry enclosure with cover plate having locking arrangement and watering pipe etc. as per specification:With 3 metre long GI Pipes and 50 kg back filling compound. | 4 | Each | 10955 | 43820 | 0 | 0 | N
29 | PWD | ELECT | 2020 | 14.1.1 | Supplying and laying ISI marked double wall HDPE pipe (IS 14930 Part II) having corrugation on the outer wall and plan surface on inner wall in ground below road, path etc at a depth not less than 40 cm and upto 90 cm including excavation, dismantling of road if required and refilling the trench with excavated material, ramming and making the surface good etc. as per specification. 63 mm outer dia and 50 mm Inner dia | 3500 | Metre | 184 | 644000 | 0 | 0 | N
30 | PWD | ELECT | 2020 | 14.1.4 | 120 mm outer dia and 103.5 mm Inner dia | 750 | Metre | 253 | 189750 | 0 | 0 | N
31 | PWD | ELECT | 2020 | 14.3.1 | Supplying and laying following size medium class G.I. pipe in ground below road, path etc at a depth not less than 40 cm and upto 90 cm including excavation, dismantling of road if required and refilling the trench with excavated material, ramming and making the surface good etc. as per specification.50 mm internal dia | 700 | Metre | 333 | 233100 | 0 | 0 | N
32 | PWD | ELECT | 2020 | 15.1.11 | Supplying and laying following sizes one number FRLS PVC insulated/XLPE, PVC sheathed, steel armoured, aluminium conductor power cable of 1.1 KV grade direct in ground at a depth not less than 40 cm and upto 90 cm including excavtion, sand cushioning, protective covering and refilling the trench etc as per specification, IS: 1554 (1988, Part 1) / IS: 7098 (1988, Part 1). 3.5 x 25 sq. mm. | 5000 | Metre | 315 | 1575000 | 0 | 0 | N
33 | PWD | ELECT | 2020 | 15.1.12 | 3.5 x 35 sq. mm. | 3000 | Metre | 316 | 948000 | 0 | 0 | N
34 | PWD | ELECT | 2020 | 15.1.15 | 3.5 x 95 sq. mm. | 550 | Metre | 488 | 268400 | 0 | 0 | N
35 | PWD | ELECT | 2020 | 15.28.4 | Supplying, fixing and cramping suitable size and all type aluminium ferule/ lugs to following size 1.1 KV grade power cable core / lead, pressed with high pressure cramping tool including connection to switch gear/ MCCB etc as per specification. .25 sq. mm | 1344 | Each | 22 | 29568 | 0 | 0 | N
36 | PWD | ELECT | 2020 | 15.28.5 | 35 sq. mm | 32 | Each | 20 | 640 | 0 | 0 | N
37 | PWD | ELECT | 2020 | 15.28.8 | 95 sq. mm | 16 | Each | 26 | 416 | 0 | 0 | N
38 | PWD | ELECT | 2020 | 19.8.3 | Supply of hot dipped galvanized (in single dip to minimum 75 micron) octogonal pole made of 3mm thick steel grade E-350 sheet having window and flush cover with locking arrangement at suitable height from base for cable termination block, pole suitably reinforced with welded steel section at window cut section to make the strength of pole unaffected, with following minimum specifications with 4 way terminal connector including 4mm thick anchor plate, 4 nos 24mm dia foundation bolts of EN8 grade, and as per IS 2062 & BS EN: 10025. (designed for wind speed upto 180km/hr, IS: 875 Part 3) 11 metre high, dia 210mm at bottom and 90mm at top, base plate size 300x300x20mm, foundation bolts 750mm long | 168 | Each | 20261 | 3403848 | 0 | 0 | N
39 | PWD | ELECT | 2020 | 19.9.8 | Supply and fixing following street light pole bracket on existing pole made out of 50 mm dia MS "B" class pipe welded to 300 mm long MS pole canopy of suitable dia at a angle of 102.50 including having MS triangular stiffner of size 150 X 50 X 5 mm thick, making arrangement for tightening the bracket with pole by providing suitable size heavy duty nuts and bolts in canopy, painting with one coat of approved steel primer etc. as per specification.Double Over Hang 2.00 metre Long | 176 | Each | 2029 | 357104 | 0 | 0 | N
40 | PWD | ELECT | 2020 | 19.11.9 | Erection of GI octogonal/ tubular/conical pole on existing cement concrete foundation having grouted bolts and nuts, aligning in true vertical position as per specification. 11 metre high | 168 | Each | 1125 | 189000 | 0 | 0 | N
41 | PWD | ELECT | 2020 | 19.12 | Designing and providing suitable RCC foundation in Cement Concrete 1:2:4 (1 cement: 2 coarse sand: 4 graded stone aggregate 20 mm nominal size) for 3 mere to 12 metre high GI octagonal pole including steel reinforcement form work, embeding 2 nos 50mm dia PVC pipe for cable entry in each foundation, excavation disposal of surplus soil and curing etc. as per specification. | 204.5 | Cum | 5219 | 1067285.5 | 0 | 0 | N
42 | PWD | ELECT | 2020 | 30.1 | Earth work in all type soil except soft rock / hard rock with all lead and 1.5 metre lift, dressing, stacking excavated strata including refilling of excavated soil in trench / pit to ground level complete as per specification. | 3000 | Cum | 168 | 504000 | 0 | 0 | N
| TOTAL AMOUNT | [7 empty] | 14132035.18
[5 empty] | G. Total Amount |  |  |  | 14132035.18
| SAY IN LACS | [7 empty] | 141.3204
Sub-Engineer P.W.D. E/M Sub-Division Raigarh(C.G.)
S.D.O. P.W.D. E/M Sub-Division Raigarh(C.G.)
Executive Engineer P.W.D. E/M Division Raigarh(C.G.)