# KARNATAKA POWER TRANSMISSION CORPORATION LIMITED

TECHNICAL SPECIFICATION

FOR

HIGH PERFORMANCE CONDUCTOR (HPC) WITH AMPACITY 700A

(Physical properties equivalent to Coyote ACSR)

# VOLUME – II

SECTION – IVB

# TECHNICAL SPECIFICATION FOR HIGH PERFORMANCE CONDUCTOR HAVING AMPACITY OF 700A

PART (A)

1.	GENERAL INFORMATION:

  - Preamble:

  - KPTCL has decided to uprate by replacing the existing ACSR COYOTE by equivalent HPC (High Performance Conductor) except Gap Type conductor on the existing towers. The intermediate supports (Narrow Base Tower / High Tensile Tubular Mono-Pole) shall be used only in case of long spans to get the adequate clearances. Replacement of existing ACSR COYOTE conductor by High Performance Conductor is to be carried out for the following 220kV/110kV/66kV lines.

Name of the project:

Strengthening of existing 66KV Transmission line from the existing 220/66KV Anchepalya substation to Yadiyuru substation with HTLS/HPC conductor on existing 66KV Anchepalya – Yadiyuru SC line on DC towers with one of the circuit to be LILO of Thippur Substation for distance of 28.564Kms in Kunigal Tq, Tumkuru Dist.

The above lines are passing through thickly populated Residential & Commercial plots along the narrow streets and hence utmost care must be taken by the contractor during Releasing & Stringing of the conductor without causing any damage to the property.  The bidders are advised to compulsorily carry out the walk-over survey/ route-inspection to familiarize with the work before quoting.  The preliminary and detailed survey has been conducted by KPTCL and all the necessary data such as Topo -sheet extract, route profile & tower schedule will be furnished to the successful contractor.

  - Design details of the existing 66KV D/C tower:

The existing 66KV DC towers are of M/s. RPG/M/s Kalpataru design and commissioned almost 20 - 30 years back.

The following are the design parameters of the tower:

- Type of tower				          : Lattice type, Pylon tower

- Normal Span      		                    : 275 M

- Wind Span				           : 300 M

- Weight Span 			                    : 412 M

- Conductor used			           : ACSR COYOTE

- Ground wire used			           : 7/3.15 mm, 110 KG class

- Maximum design tension of                   : 1546 Kg

conductor at 32° C FW (43 kg/M2)

- Tension of Power Conductor                   : 1156 Kg

at 32° C No Wind  condition

- Maximum Sag at 75 deg. C

No Wind condition			            : 5.5 M

- Height of bottom

Conductor at tower			             : 10.8M

- Code according to which

the tower is designed  		             : as per old code IS:802

- Factor of Safety in the design,

Under Normal condition (NC)	             : 2.0

Under Brocken Wire Condition (BWC)	    : 1.5

- Scope of the Work:

- Supply & Stringing of High Performance Conductor & Releasing of ACSR COYOTE conductor.

- Supply & Installation of necessary conductor accessories suitable for High Performance Conductor.

- Replacement of Insulator (wherever necessary) and Insulator Hardware.

- Supply & Erection of steel Mono-pole / Lattice type Narrow Base towers wherever required including foundation work.

- Releasing of the existing ACSR COYOTE conductor and stringing of High Performance Conductor simultaneously so that the conductor do not touch / damaged the obstacles below the line.

- Supply and stringing of Earth wire along with accessories wherever required and releasing of damaged Earth wire.

  - Statutory Electrical clearances:

All the electrical clearances such as Ground clearances (along the road and across the road), clearances from the building (both horizontal and vertical) shall be maintained as per CEA regulations (Measures relating to safety and Electric supply Regulations - 2023).

TECHNICAL SPECIFICATION

SECTION II

PART (B)

1.0	Description of High Performance Conductor (HPC) and its Technical Requirements

1.1	The High Performance Conductor (except GAP Conductor) shall be capable of providing the specified ampacity of 700A at a continuous operating conductor temperature higher than that of the maximum permissible operating temperature of the COYOTE Conductor without exceeding the level of maximum permissible sag of the ACSR COYOTE Conductor at 75°C ie., 5.5Mtrs Sag.

The physical and operating performance requirements of the transmission line with High Performance Conductor are mentioned below. The bidder shall offer High Performance Conductor complying with the specified requirements. The Bidder shall indicate particulars of the proposed conductor in the relevant GTP schedule of BPS along with calculations to establish compliance with the specified requirements i.e., Current carrying capacity (Clause 1.2), Physical dimensional (Clause 1.3), sag-Tension (Clause 1.4). In case any changes are required in the design of High Performance Conductors to comply the stipulated requirement of the technical specification, the same shall be carried out without any extra cost to KPTCL. The AC resistance/Ohmic losses at temperature corresponding to the specified ampacity shall not exceed the value guaranteed by the bidder in schedule-01 of the bid proposal Sheets.

1.2	Current Carrying Capacity /Ampacity Requirements

1.2.1	The High Performance Conductor shall be suitable to carry minimum 50 Hz alternating current of 700 Amperes under the ambient conditions & maximum conductor sag specified below while satisfying other specified technical requirements/ parameters:-

Ambiant température            : 40° C

Solar Absorption coefficient   : 0.8

Solar Radiation                      : 1045 watt/Sq.m

Emisitivity Constant              : 0.45

Wind velocity                         : 0.56m/sec

(Considering angle between wind & axis of conductor as 90deg)

Effective angle of incidence of sun’s rays= 90°

Elevation above sea level= 0 mtr (approx.)

Maximum permissible Conductor sag for 275M span at steady state conductor temperature and nil wind corresponding to 50 Hz alternating current of 275 Amperes under ambient conditions specified above = 5.5Mtrs.

The calculations for Ampacity shall be based on latest edition of IEEE Standard 738 (IEEE 738-2023) in SI units. The bidder in his bid shall furnish calculation for the ampacity based on the above standard for the proposed High Performance Conductor. Also the bidder shall furnish the calculations for AC resistance at ambient conditions & at maximum continuous operating temperature corresponding to 700A, DC resistance and I²R loses at ambient conditions & at maximum continuous operating temperature for the proposed High Performance Conductor

For calculation of the radial temperature gradient within the conductor, effective thermal conductivity (kth) shall be considered as 1 watt/m-°C. Further, conductor sag at designed maximum temperature shall be calculated considering temperature of core corresponding to the designed maximum temperature of conductor, irrespective of the magnitude of radial temperature gradient.

AC resistance of the offered High Performance Conductor and the Ratio of AC resistance & DC resistance for High Performance Conductor shall be calculated on the basis of Chapter-2, EPRIAC Transmission Line Reference Book – 200 kV and above or the formulae indicated as follows:-

R ac= Rdc X (1+ 0.00519 X (mr)n X k1+k2) where, mr= 0.3544938 /(Rdc)½

If mr < 2.8, then n= 4 - 0.0616 + 0.0896 X mr–0.0513 X (mr)2

If mr > 2.8 < 5.0, then n=4 + 0.5363 - 0.2949 X  mr + 0.0097  X (mr)2

k1 = {cos (90(d/D)P)}2.35 where,

p = 0.7 + 0.11Xmr–0.04Xmr2 +0.0094Xmr3

k2  = 0 for composite core type High Performance Conductor

= 0.15 for single aluminum layer type High Performance Conductor

= 0.03 for three aluminum layer type High Performance Conductor

= 0.003 for three aluminum layer type High Performance Conductor

where,

D= conductor outer diameter in meters

d = conductor inner diameter in meters

Rdc = DC resistance of conductor at given temperature, ohms/km

Rac = AC resistance of conductor at given temperature, ohms/km

The bidder in his bid shall furnish the calculations for Ampacity based on the above for the proposed High Performance Conductor.

1.2.2	The design of conductor shall be suitable for operation at a steady state conductor temperature experienced for an AC current flow of 700 Amperes under the above ambient conditions based on ampacity calculations mentioned above. The bidder shall also indicate the maximum permissible conductor temperature for continuous operation without any deterioration of its electrical, mechanical & metallurgical properties.

The maximum permissible conductor temperature for continuous operation shall not be considered, more than 180°C. The bidder shall also furnish the maximum permissible conductor temperature for short term operations including permissible duration of such short term operation.

The UTS of conductor declared in the GTP shall be guaranteed UTS of conductor at room temperature. Further, UTS of conductor achieved at maximum continuous operating temperature (700A) shall not be less than 80% of UTS at ambient temperature declared in the GTP.

1. 3	Technical Particulars of High Performance Conductor

The High Performance Conductor shall meet the following minimum requirements:

| Overall diameter of complete conductor | Less than or Equal to 15.89mm |
| --- | --- |
| Approx. mass of complete conductor (Kg/Km) | Less than or Equal to 521Kg/Km |
| Direction of lay of outer layer | Right Hand |

(*) Important Note:

The diameter and unit weight of COYOTE ACSR is 15.89mm and 521Kg/Km respectively.  In the design of existing tower the weight span is considered as 1.5 times the normal span and since the ground terrain is almost flat with slight undulations, the additional cushioning available for weight span (ie., 412-275 = 137M) can be utilized for developing conductor with higher unit weight.

Similarly, the available additional cushioning of 10% of wind span plus the difference in transverse component due to the conductor tension between the designed angle of deviation & the actual angle of deviation can be utilized for developing the higher diameter of the conductor.

In view of the above two points the conductor with higher diameter/cross-section could also be developed keeping the design conductor tension of the tower within the limits.

The bidder shall indicate the technical particulars and details of the construction of the conductor in the relevant schedule of GTP. The bidder shall also guarantee the DC resistance of conductor at 20° C and AC resistance at the calculated temperature corresponding to minimum alternating current flow of 700 Amperes at specified operating conditions.

The bidder shall submit the supporting calculations for the AC resistance indicating details & justifications of values of temperature coefficient of resistance & DC to AC resistance conversion factor(s) with due reference to construction / geometry of the conductor.

1.4 Sag-Tension Requirements

1.4.1	The High Performance Conductor shall meet the following sag tension requirements for ruling span of 275M

| Particulars | Limiting value |
| --- | --- |
| Tension at every day condition (32°C, no wind) | Not exceeding 25% of UTS of proposed conductor |
| Maximum Sag at maximum continuous operating temperature (corresponding to 700A) | ≤ 5.5M |
| Tension at 32°C, full wind (43 kg/m2) | ≤ 1546 Kgs & not exceeding 50% of UTS of proposed conductor |
| Tension at 10°C, 2/3 Wind Pressure (28.67kg/m²) | ≤ 1567 Kgs & not exceeding 50% of UTS of proposed conductor |

The calculations for Sag & Tension for HPC shall be as described below:-

Sag-Tension calculations for High Performance Conductor can be carried by using PLSCAD.

Following values shall be considered for the purpose of sag-tension calculation:-

- Final values of modulus of elasticity of Aluminium/Aluminium Alloy/core, Coefficient of Linear Expansion of Aluminium/Aluminium Alloy/core, Stress-Strain coefficients & Creep  coefficients of Aluminium/Aluminium Alloy/core in the cable data (.wir file) used for calculation of sag in PLSCAD shall be based on either of the following :-

- Existing standard (.wir file) files on offered conductor as available in PLS website.

- A file derived from existing standard file for conductor of equivalent/ near equivalent stranding.

- A file derived from type test conducted on conductor of same stranding.

In each of the above cases, proper justification in the form of test reports/ calculations/ print out   of ‘.wir’ file   as available   on PLS website, etc. shall be required to be submitted during detailed Engineering with soft copy of (.wir file).

- PLSCAD  Sagging criteria/ conditions shall be based  on the sag tension limits specified above at Clause 1.4.1 and shall be carried out in a manner that the above mentioned sag-tension limits are met at worst conditions in initial condition and the tension limit at everyday condition  in "Final After Creep" as well as in "After Load" condition.

- The knee-point for High Performance Conductor guaranteed in GTP/TDS shall be considered from PLSCADD sag-tension calculation report. The value guaranteed by bidder shall be justified as per PLSCADD sagging criteria conditions during evaluation and detailed engineering.

- A proper justification may be asked to bidder for “Cable Condition in Automatic Sagging Criteria” considered for sag and tension calculation along with the final report outcomes during detailed engineering.

- Survey and profiling of existing line route needs to be performed using PLSCADD. The dot back file of PLSCADD working for complete project profiling showing the existing conductor and the proposed High Performance Conductor each section not violating the ground clearance shall be submitted during detailed sag engineering.

1.4.2	Sag-Tension calculations at various conditions mentioned above shall be submitted along with the bid. These calculations shall also    include calculations for determination of transition/knee point temperature in detail.

1.4.3	Various conductor parameters (viz. modulus of elasticity, coefficient   of linear expansion, stress- strain and creep, etc.) considered above in the sag tension calculation shall be verified during detailed engineering based on type tests conducted.

The bidder shall also furnish sag & tensions under no wind for various temperatures starting from 0°C to maximum continuous operating temperature in steps of 5°C.

1.4.4     	After award of the contract, the Supplier shall submit Sag-Tension calculations corresponding to various conditions given above for all the spans as per detailed survey and spans ranging from 50M to 400M in intervals of 50M before commencement of work.

1.4.5	Besides above, the Supplier shall also furnish along with the bid, details of creep characteristics in respect of the offered type of High Performance Conductor based on laboratory investigations/ experimentation (creep test as per IEE1138 or IEC 61395) conducted on similar type of conductor and shall indicate creep strain values corresponding to 1 month, 6 month, 1 year, 10 year & 20 year creep at everyday tension & at  maximum continuous operating temperature as well as at room temperature along with creep compensation temp calculations to be considered during stringing in detail.

1.5	Workmanship

1.5.1	All the conductor strands shall be smooth, uniform and free from all imperfections, such as spills and splits, cracks, die marks, scratches, abrasions, rust etc.

1.5.2	The finished conductor shall be smooth, compact, uniform and free from all imperfections including kinks (protusion of wires), wire cross over, over riding, looseness (wire being dislocated by finger/hand pressure and/or unusual bangle noise on tapping), material inclusions, white rust, powder formation or black spot (on account of reaction with trapped rain water etc.), dirt, grit etc.

1.6	Joints in Wires

1.6.1     Aluminium /Aluminium Alloy Wires

1.6.1.1	During stranding, no Aluminium/ Aluminium Alloy wire welds shall be made for the purpose of achieving the required conductor length.

1.6.1.2	No joints shall be permitted in the individual wires in the outer most layer of the finished conductor. However joints are permitted in the inner layer(s) of the conductor unavoidably broken during stranding provided such breaks are not associated with either inherently defective wire or with the use of short lengths of Aluminium /Aluminium Alloy wires. Such joints shall not be more than four (4 ) per conductor length and shall not be closer than 15 meters from joint in the same wire or in any other Aluminium /Aluminium Alloy wire of the completed conductor. A record of such joints for each individual length of the conductor shall be maintained by the Contractor for Owners review.

1.6.1.3	Joints shall be made by cold pressure butt welding and shall withstand a stress of not less than the breaking strength of individual strand guaranteed.

1.6.2       Core Wires

There shall be no joint of any kind in the finished wire entering into the manufacture of the strand. There shall also be no joints or splices in any length of the completed solid or stranded core.

1.7         Tolerances

Manufacturing tolerances on the dimensions to the extent of one percent (± 1%) shall be permitted for individual strands and the complete conductor.

1.8         Materials

The materials used for construction of the conductor shall be such that the conductor meets the specified technical and performance requirements.

1.8.1       Outer layer (Aluminium/Aluminium Alloy layers)

1.8.1.1	The material of outer layer of High Performance Conductor shall be of high temperature resistant aluminum alloy added with zirconium or any other suitable element(s) etc. to electrolytic aluminium having purity not less than 99.5% and a copper content not exceeding 0.04%. The strands shall be manufactured through appropriate manufacturing process to ensure consistent electrical mechanical and metallurgical properties under continuous high temperature operation. Bidder shall guarantee the chemical composition in the schedule GTP of BPS and also furnish description of the manufacturing process in the Bid.

1.8.1.2	In case of fully annealed type (0 tempered) aluminium/ alloy strands round/ trapezoidal/Z-shaped wire shall be accepted.

1.8.2      Core

The core wire strand(s) shall be of galvanized steel wires/aluminium clad steel wires/Zinc - 5% Aluminium – Misch metal alloy coated steel/aluminium clad steel/composite materials etc. and shall have properties conforming to the technical performance requirements of the finished conductor. In case, the designed maximum temperature of the offered High Performance Conductor exceeds 180 deg C, ordinary zinc coating/galvanizing of the Steel/Invar core wires shall not be accepted and only aluminium clad or Misch metal coated wires shall be permitted. Bidder shall furnish properties and composition of the core wire strand(s) in the schedule GTP of BPS. The properties & composition of core wires guaranteed by the bidder shall be based on the relevant India/International standards, wherever applicable.

The zinc used for galvanizing of core (if used) shall be electrolytic      High Grade Zinc of 99.95% purity. It shall conform to and satisfy all the requirements of IS:209. The minimum mass of zinc coating shall conform to the requirements of Class-I coating as per IEC-888. Zinc-5% Aluminium –Misch metal alloy coating, if used, shall conform to and satisfy all the requirements of ASTM B 803 / B 958.

The aluminium cladding of wires shall be with aluminum having purity not less than 99.5 % and shall be thoroughly bonded to the core wire strand(s). The minimum thickness of aluminium cladding shall be 0.07mm to achieve a minimum conductivity of 14% of IACS.

Where composite material for core is offered, the material shall be either of High strength grade or extra high strength grade as per ASTM B987. The materials shall be of such proven quality that its properties are not adversely influenced by the normal operating conditions of a 220kV/110kV/66kV transmission line in tropical environment conditions as experienced by the existing line. The bidder shall provide adequate details including specifications/test reports/ operating experience details/ performance certificates etc. in support of the suitability of the offered materials.

1.9	Conductor Length

1.9.1	After survey of the involved section of the line by tower contractor, the tower schedules, section lengths, special crossing etc. shall be furnished to the supplier. The supplier shall determine the most appropriate individual conductor lengths to be manufactured & supplied keeping in view tower schedules, section lengths, special crossings etc. and the drum schedules shall be submitted to Owner for review & approval.

1.9.2	The bidder shall also indicate the maximum single length of High Performance Conductor, he can manufacture in the guaranteed technical particulars of offer.

1.10       Evaluation of Ohmic Losses & Differential Price Loading

1.10.1	Based on the conductor parameters guaranteed by the bidders, average Ohmic losses for different type of conductors for all three phases of a one circuit of transmission line offered by the bidders shall be calculated as per the following formula:

Average Ohmic loss (kW) = Loss Load Factor x 3 x No. of sub-conductors per phase x Line Length x (Continuous operating current Specified)2 x AC Resistance corresponding to continuous operating current/1000

Average Ohmic loss (kW) per Km = 0.3x3x2x1x(700)2 x Rac/1000

= 882000x Rac/1000 KW/KM (For Double circuit line)

Average Ohmic loss (kW) per Km = 0.3x3x1x1x(700)2 x Rac/1000

= 441000x Rac/1000 KW/KM (For Single circuit line)

Where, Rac is the AC resistance per Km guaranteed by the bidder at temperature corresponding to the continuous operating current of 700A under normal/ambient condition.

Differential price evaluation for the conductors offered by the bidders shall be carried out considering the average Ohmic losses calculated as above and considering Rs. 1,60,000/- (One Lakhs Sixty Thousand only) per kW.

The best parameter of loss (lowest ohmic loss for conductor) corresponding to lowest AC resistance quoted among bidders by any technically responsive and qualified bidder shall be taken as basis and that quoted by the particular bidder shall be used to arrive at differential price to be applied for each bid.

1.10.2     Penalty for excessive losses:

If, AC resistance found higher than AC resistance guaranteed in the bid on (type) testing, Undisputed liquidated damages shall be recovered from the supplier at the following rates for each kilowatt of excess loss Rupees. 3,20,000/- (Rupees of Three lakhs Twenty Thousand only). The AC resistance test procedure is as detailed in the Annexture-1

Fraction of KW quoted, capitalized cost of losses shall be calculated on pro-rata basis. No bonus shall be payable for loss, which are less than those, stated in the bid.

2.0         Tests and Standards

2.1          Type Tests

2.1.1	Type Tests on Stranded Conductor/ Stranded wire

The following tests shall be conducted once on sample/samples of conductor from each manufacturing facility:

| On complete Conductor |  |  |
| --- | --- | --- |
| a) | DC resistance test on stranded conductor | : As per Annexure-A |
| b) | UTS test on stranded conductor at - Room Temperature - Elevated Temperature | : As per Annexure-A |
| c) | Stress- Strain test on stranded conductor and core at room temperature | : IEC 1089 |
| d) | Stress-strain test on stranded conductor and core at elevated temperature | As per Annexure-A |
| e) | High temperature endurance & creep test on stranded conductor | : As per Annexure-A |
| f) | Sheaves Test | : As per Annexure-A |
| g) | Axial Impact Test | : As per Annexure-A |
| h) | Radial Crush Test | : As per Annexure-A |
| i) | Torsional Ductility Test | : As per Annexure-A |
| j) | Aeolian Vibration Test | : As per Annexure-A |
| k) | Temperature Cycle Test | : As per Annexure-A |
| l) | Salt Spray Test (applicable for stranded composite core conductors having galvanic protection layer not conforming to ASTM B987 | : As per Annexure-A |
| m) | Radio Interference voltage test (dry) (for 400KV line) | : As per Annexure-A |
| n) | Corona extinction voltage test (dry) (for 400KV line) | : As per Annexure-A |

| On Conductor Strand/core |  |  |
| --- | --- | --- |
| a) | Heat resistance test on Aluminium Alloy strands or core | : As per Annexure-A |
| b) | Bending test on aluminium clad core (if applicable) | : As per Annexure-A |
| c) | Compression test on aluminium clad core (if applicable) | : As per Annexure-A |
| d) | Coefficient of linear expansion on core/ core strand | : As per Annexure-A |
| e) | Brittle fracture test on composite core (if applicable) | : As per Annexure-A |
| f) | Bending test on composite core (if applicable) | : As per Annexure-A |

The bidder should submit complete Type test reports as per above schedule conducted in NABL laboratory (ISO/IEC 17025) and witnessed and approved by Indian utility, should not be older than seven (7) years, as on the date of bid opening. In addition to the above all the type tests shall be repeated for every 1500 KMs of proposed High Performance Conductor of the same type and make ordered after the award of the Contract which will be witnessed by the purchaser’s representative. The extra cost if any shall be clearly indicated in the price schedules attached to the Section BPS.

In the event of any discrepancy in the test report (i.e., any test report not	applicable due to any design / material/manufacturing process change including substitution of components or due to non-compliance with the requirement stipulated in the Technical Specification) the tests shall be conducted by the Contractor at no extra cost to the Employer/ Purchaser.

2.2    Acceptance Tests

| a) | Visual and dimensional check on drum | : As per Annexure-A |
| --- | --- | --- |
| b) | Visual check for joints scratches etc. and length measurement of conductor by rewinding | : As per Annexure-A |
| c) | Dimensional check on core strands/ composite core and Aluminium Alloy strands | : As per Annexure-A |
| d) | Check for lay-ratios of various layers | : As per Annexure-A |
| e) | Galvanising test on core strands | : As per Annexure-A |
| f) | aluminum thickness on aluminium clad wires | : As per Annexure-A |
| g) | Torsion and Elongation tests on core strands/composite core | : As per Annexure-A |
| h) | Breaking load test on core strands and Aluminium / Aluminium Alloy strands | : As per Annexure-A |
| i) | Wrap test on core strands and Aluminium Alloy strands | : As per IEC:888 & IES:889 |
| j) | Minimum conductivity test on thermal resistant Aluminium Alloy strands | : As per IEC : 889 & IEC: 468 |
| k) | Procedure qualification test on welded joint of Aluminium Alloy strands | : As per Annexure-A |
| l) | Heat resistance test on Aluminium Alloy strands | : As per Annexure-A |
| m) | Ageing test on filler (if applicable) | : As per Annexure-A |
| n) | Minimum conductivity test on aluminium clad core strands | : As per Annexure-A |
| o) | Ageing test on filler (if applicable) : | : As per Annexure-A |
| p) | Glass transition temperature test on composite core (if applicable) | : As per Annexure-A |
| q) | Flexural Strength test on composite core (if applicable) | : As per Annexure-A |
| r) | Bending test on composite core (if applicable) | : As per Annexure-A |
| s) | Galvanic Protection Barrier Layer Thickness test on composite core (applicable for composite core conductors having galvanic barrier layer conforming to ASTM B987) | : As per Annexure-A |
| NOTE: All the above tests except (K) shall be carried out on Aluminium / Aluminium Alloy and core strands after stranding only. |  |  |

2.3    Routine Test

| a) | Check to ensure that the joints are as per Specification |
| --- | --- |
| b) | Check that there are no cuts, fins etc., on the strands. |
| c) | Check that drums are as per Specification |
| d) | All acceptance tests as mentioned above to be carried out on 10 % of drums |

2.4   Tests during Manufacture

| a) | Chemical analysis of zinc used for galvanizing | :As per Annexure-A |
| --- | --- | --- |
| b) | Chemical analysis of Aluminium alloy used for making Aluminium Alloy strands | :As per Annexure-A |
| c) | Chemical analysis of core strands/ composite core | :As per Annexure-A |

2.5   Testing Expenses

2.5.1	The break-up of the testing charges for the type tests specified shall be indicated separately.

2.5.2	Bidder shall indicate the laboratories in which they propose to conduct the type tests. They shall ensure that adequate facilities are available in the laboratories and the tests can be completed in these laboratories within the time schedule guaranteed by them.

2.5.3	In case of failure in any type test the Supplier is either required to manufacture fresh sample lot and repeat the entire test successfully once or repeat that particular type test three times successfully on the sample selected from the already manufactured lot at his own expenses. In case a fresh lot is manufactured for testing then the lot already manufactured shall be rejected.

2.5.4	The entire cost of testing for the acceptance and routine tests and Tests during manufacture specified herein shall be treated as included in the quoted unit price of conductor, except for the expenses of the inspector/Owner's representative.

2.5.5 	In case of failure in any type test, if repeat type tests are required to be conducted, then all the expenses for deputation of Inspector/Owner's representative shall be deducted from the contract price. Also if on receipt of the Supplier's notice of testing, the Owner's representative does not find material/ testing facilities to be ready for testing the expenses incurred by the Owner for re-deputation shall be deducted from contract price.

2.5.6	The Supplier shall intimate the Owner about carrying out of the type tests along with detailed testing programme at least 3 weeks in advance (in case of testing in India) and at least 6 weeks in advance (in case of testing abroad) of the schedule date of testing during which the Owner will arrange to depute his representative to be present at the time of carrying out the tests.

2.6	Additional Tests

2.6.1	KPTCL reserves the right of having at his own expenses any other test(s) of reasonable nature carried out at Supplier’s premises, at site or in any other place in addition to the aforesaid type, acceptance and routine tests to satisfy them self that the materials comply with the Specifications.

2.6.2 	The Owner also reserves the right to conduct all the tests mentioned in this specification at his own expense on the samples drawn from the site at Supplier’s premises or at any other test center. In case of evidence of non-compliance, it shall be binding on the part of Supplier to prove the compliance of the items to the technical specifications by repeat tests, or correction of deficiencies, or replacement of defective items all without any extra cost to the Owner.

2.7	Sample batch for Type Testing

2.7.1	The Supplier shall offer material for selection of samples for type testing only after getting Quality Assurance Plan approved from Owner’s Quality Assurance Department. The sample shall be manufactured strictly in accordance with the Quality Assurance Plan approved by Owner.

2.7.2	The Supplier shall offer at least three drums for selection of sample required for conducting all the type test.

2.7.3	The Supplier is required to carry out all the acceptance tests successfully in presence of Owner’s representative before sample selection.

2.8	Test Reports

2.8.1	Copies of type test reports shall be furnished in at least three copies along with one original. One copy will be returned duly certified by the Owner only after which the commercial production of the material shall start.

2.8.2	Record of routine test reports shall be maintained by the Supplier at his works for periodic inspection by the Owner’s representative.

2.8.3	Test Certificates of tests during manufacture shall be maintained by the Supplier. These shall be produced for verification as and when desired by the Owner.

2.9 	Inspection

2.9.1	The Owner’s representative shall at all times be entitled to have access to the works and all places of manufacture, where conductor shall be manufactured and representative shall have full facilities for unrestricted inspection of the Supplier’s works, raw materials and process of manufacture for conducting necessary tests as detailed herein.

2.9.2	The Supplier shall keep the Owner informed in advance of the time of starting and of the progress of manufacture of conductor in its various stages so that arrangements can be made for inspection.

2.9.3	No material shall be dispatched from its point of manufacture before it has been satisfactorily inspected and tested, unless the inspection is waived off by the Owner in writing. In the latter case also the conductor shall be dispatched only after satisfactory testing for all tests specified herein have been completed.

2.9.4	The acceptance of any quantity of material shall in no way relieve the Supplier of any of his responsibilities for meeting all requirements of the Specification, and shall not prevent subsequent rejection it such material is later found to be defective.

2.10	Test Facilities

2.10.1	The following additional test facilities shall be available at the Supplier’s works:

a)	Calibration of various testing and measuring equipment including tensile testing machine, resistance measurement facilities, burette, thermometer, barometer etc.

b)	Standard resistance for calibration of resistance bridges.

c)	Finished conductor shall be checked for length verification and surface finish on separate rewinding machine at reduced speed (variable from 8 to 16 meters per minute). The rewinding facilities shall have appropriate clutch system and free of vibrations, jerks etc. with traverse laying facilities.

2.11	Packing

2.11.1	The conductor shall be supplied in returnable, strong, wooden/painted steel/hybrid (painted steel cum wood) drums provided with lagging of adequate strength, constructed to protect the conductor against all damage and displacement during transit, storage and subsequent handling and stringing operations in the field. The Supplier shall select suitable drums for supply of conductor and shall be responsible for any loss or damage to conductor and/or drum during transportation handling and storage due to improper selection of drum or packing. The drums shall generally conform to IS: 1778, except as otherwise specified hereinafter.

2.11.2 	The drums shall be suitable for wheel mounting and for letting off the conductor under a minimum controlled tension of the order of 5 KN.

2.11.3	The Bidder should submit their proposed drum drawings along with the bid.

2.11.4 	One conductor length only shall be wound on each drum.

2.11.5	The conductor ends shall be properly sealed and secured on the side of one of the flanges to avoid loosening of the conductor layers during transit and handling.

2.11.6	Marking

Each drum shall have the following information stenciled on it in indelible ink along with other essential data:

(a)	Contract/Award letter number.

(b)	Name and address of consignee.

(c)	Manufacturer’s name and address.

(d)	Drum number

(e)	Size of conductor

(f)	Length of conductor in meters

(g)	Arrow marking for unwinding

(h)	Position of the conductor ends

(i)	Distance between outer-most Layer of conductor and the inner surface of lagging.

(k)	Barrel diameter at three locations & an arrow marking at the location of the measurement.

(l)	Number of turns in the outer most layers.

(m)	Gross weight of drum after putting lagging.

(n)	Tear weight of the drum without lagging.

(o)	Net weight of the conductor in the drum.

(p)	CIP/MICC No.

The above should be indicated in the packing list also.

2.12	Verification of Conductor Length

The Owner reserves the right to verify the length of conductor after unreeling at least ten (10) percent of the drums in a lot offered for inspection.

2.13	Standards

2.13.1	The conductor shall conform to the following Indian/International Standards, which shall mean latest revisions, with amendments/changes adopted and published, unless specifically stated otherwise in the Specification.

2.13.2	In the event of the supply of conductor conforming to standards other than specified, the Bidder shall confirm in his bid that these standards are equivalent to those specified. In case of award, salient features of comparison between the standards proposed by the Supplier and those specified in this document will be provided by the Supplier to establish their equivalence.

| Sl. No. | Indian Standard | Title | International Standard |
| --- | --- | --- | --- |
| 1. | IS: 209-1992 | Specification for zinc | BS:3436-1986 |
| 2. | IS: 398-1982 | Specification for Aluminum Conductors for Overhead Transmission Purposes | IEC:1089-1991 BS:215-1970 |
| 3. | IS:398-1990 Part-II | Aluminum Conductor Galvanized Steel Reinforced | BS;215-1970 IEC:1089-1991 |
| 4. | IS:398-1992 Part-V | Aluminum Conductor Galvanized Steel- Reinforced For Extra High Voltage (400 KV) and above | IEC:1089-1991 BS:215-1970 |
| 5. | IS : 1778-1980 | Reels and Drums for Bare Conductors | BS:1559-1949 |
| 6. | IS : 1521-1991 | Method of Tensile Testing of Steel Wire | ISO 6892-1984 |
| 7. | IS : 2629-1990 | Recommended Practice for Hot Dip Galvanizing of Iron and Steel |  |
| 8. | IS : 2633-1992 | Method of Testing Uniformity of Coating on Zinc Coated Articles |  |
| 9. | IS : 4826-1992 | Galvanized Coating on Round Steel Wires | IEC : 888-1987 BS:443-1969 |
| 10. | IS : 6745-1990 | Methods of Determination of Weight of Zinc Coating of Zinc Coated Iron and Steel Articles | BS:433-1969 ISO 1460 - 1973 |
| 11. | IS : 8263-1990 | Method of Radio Interference Tests on High Voltage Insulators | IEC:437-1973 NEMA:107-1964 CISPR |
| 12. | IS : 9997-1988 | Aluminum Alloy Redraw Rods | IEC 104 - 1987 |
| 13. |  | Zinc Coated steel wires for stranded Conductors | IEC : 888-1987 |
| 14. |  | Hard drawn Aluminum wire for overhead line conductors | IEC : 889-1987 |
| 15. | IS:398 (Part-IV) | Aluminum Alloy stranded conductor | IEC : 208-1966 BS-3242-1970 |
| 16. |  | Aluminum clad steel wires | IEC:1232 |
| 17. |  | Method of measurement of resistivity of metallic materials | IEC:468 |
| 18. |  | Ampacity (Standard for calculating the Current Temperature Relationship of Bare overhead conductors. | IEEE738-2023 |
| 19. |  | Thermal Resistant aluminum alloy wire for overhead line Conductor. | IEC 62004 |
| 20 |  | Standard Specification for Zinc-Coated (Galvanized) Steel Core Wire for Use in Overhead Electrical Conductors | ASTM B498 |
| 21 |  | Standard Specification for High-Strength Zinc Coated (Galvanized) Steel Core Wire for Aluminum and Aluminum-Alloy Conductors, Steel Reinforced | ASTM B606 |
| 22 |  | Standard Specification for Aluminum-Clad Steel Core Wire for Use in Overhead Electrical Aluminum Conductors | ASTM B502 |
| 23 |  | Standard Specification for Thermostat Metal Sheet and Strip | ASTM B388 |
| 24 |  | Standard Specification for Thermostat Component Alloys | ASTM B753 |
| 25 |  | Standard Specification for Zinc-5% Aluminum Misch. metal Alloy-Coated Carbon Steel Wire | ASTM A856 |
| 26 |  | 7 Standard Specification for Steel Sheet Piling, Cold Formed, Light Gage | ASTM A857 |
| 27 |  | Standard Specification for Aluminum 1350–H19 Wire for Electrical Purposes | ASTM B230 |
| 28 |  | Standard Specification for Aluminum-Alloy 6201- T81 and 6201-T83 Wire for Electrical Purposes | ASTM B398 |
| 29 |  | Standard Specification for Aluminum 1350 Round Wire, Annealed and Intermediate Tempers, for Electrical Purposes | ASTM B609 |
| 30 |  | Aluminum alloy wire for stranded conductors for overhead lines – Al 59 wire | SS 424 0813 |
| 31 |  | Aluminum alloy stranded conductors for overhead lines – Al 59 wire | SS 424 0814 |
| 32 |  | 0 Conductors for overhead lines. Aluminum conductors steel supported (ACSS) | BS EN 50540 |
| 33 |  | Standard Specification for Heat Resistant Aluminum-Zirconium Alloy Wire for Electrical Purposes | ASTM B 941 |
| 34 |  | standard Specification for Extra-High-Strength and Ultra-High-Strength Zinc-Coated (Galvanized) Steel Core Wire for Overhead Electrical Conductors | ASTM B 957 |
| 35 |  | Standard Specification for Zinc–5 % Aluminum Misch metal Alloy-Coated Steel Core Wire for Aluminum Conductors, Steel Reinforced (ACSR) | ASTM B 802 |
| 36 |  | Standard Specification for Extra-High-Strength and Ultra-High-Strength Class A Zinc–5% Aluminum-Mischmetal Alloy-Coated Steel Core Wire for Use in Overhead Electrical Conductors | ASTM B 958 |
| 37 |  | Standard Specification for Fiber Reinforced Aluminum Matrix Composite (AMC) Core Wire for Aluminum Conductors, Composite Reinforced (ACCR) | ASTM B 976 |
| 38 |  | Standard Specification for Carbon Fiber Thermoset Polymer Matrix Composite Core (CFC) for use in Overhead Electrical Conductors | ASTM B987- 17 |

The standards mentioned above are available from:

| Reference Abbreviation | Name and Address |
| --- | --- |
| BS | British Standards, British Standards Institution 101, Pentonvile Road, N - 19-ND UK |
| IEC/CISPR | International Electro Technical Commission, Bureau Central de la Commission, electro Technique international, 1 Rue de verembe, Geneva SWITZERLAND |
| BIS/IS | Beureau Of Indian Standards. Manak Bhavan, 9, Bahadur Shah Zafar Marg, New Delhi - 110001. INDIA |
| ISO | International Organisation for Standardization. Danish Board of Standardization Danish Standardizing Sraat, Aurehoegvej-12 DK-2900, Heeleprup, DENMARK. |
| NEMA | National Electric Manufacture Association, 155, East 44th Street. New York, NY 10017 U.S.A. |
| CEA | Central Electricity Authority, Sewa Bhawan, Rama Krishna Puram, Sector-1, New Delhi-110066. |

Annexure-A

1.	Tests on Conductor

1.1	UTS Test on Stranded Conductor at:

a) UTS Test on Stranded Conductor room temperature*

Circles perpendicular to the axis of the conductor shall be marked at two places on a sample of conductor of minimum 5M length between fixing arrangement suitably fixed by appropriate fittings on a tensile testing machine. The load shall be increased at a steady rate up to 50% of minimum specified UTS and held for one minute. The circles drawn shall not be distorted due to relative movement of strands. Thereafter the load shall be increased at steady rate to minimum UTS and held for one minute. The Conductor sample shall not fail during this period. The applied load shall then be increased until the failing load is reached and the value recorded.

* The test is to be conducted at ambient temperature, between Minimum and maximum ambient temperature of 0 deg C and 50 deg C respectively.

b) UTS Test on Stranded Conductor elevated temperature

UTS Test on Stranded Conductor shall be conducted as per Clause No. 1.1(a) specified above keeping conductor temperature at the designed maximum temperature.

  - Corona Extinction Voltage Test [Applicable only for 400kV System]:

Not applicable for 66KV & 220kV lines.

  - Radio Interference Voltage Test [Applicable only for 400kV System]:

Not applicable for 66KV & 220kV lines.

1.4	D.C. Resistance Test on Stranded Conductor

On a conductor sample of minimum 5M length two contact-clamps shall be fixed with a predetermined bolt torque. The resistance shall be measured by a Kelvin double bridge or using micro ohm meter of suitable accuracy by placing the clamps initially zero metre and subsequently one metre apart. The test shall be repeated at least five times and the average value recorded. The value obtained shall be corrected to the value at 20deg C as per IS: 398-(Part-IV)/(Part-V). The resistance corrected at 20deg C shall conform to the requirements of this Specification.

1.5	Stress-strain test at elevated temperature

Stress-strain test as per IEC-61089 shall be conducted keeping conductor temperature at designed maximum temperature.

UTS for this test shall be 80% of the UTS guaranteed in the GTP.

1.6        High Temperature endurance & creep test

Two conductor samples of length equal to at least 100xd+2xa (where, d is the conductor diameter and ‘a’  is the distance between the end fitting and the gauge length or 20Mtrs whichever is the more) shall be strung at tension equal to 25% of conductor UTS. The distance ‘a’ shall be at least 25% of the gauge length or 2m whichever is the smaller. The conductor samples shall be subjected to tests as indicated below:

(i)    On one of the conductor samples, the conductor temperature shall be maintained at 20degC for1000hours. The elongation/creep strain of the conductor during this period shall be measured and recorded at end of 1hour, 10hour, 100hour and subsequently every100hour up to 1000hours time period.

(ii)  On other conductor sample, the conductor temperature shall be increased to designed maximum temperature in steps of 20deg. C and thermal elongation of the conductor sample shall be measured & recorded at each step. The temperature shall be held at each step for sufficient duration for stabilization of temperature. Further, the temperature of   the   conductor shall be    maintained   at    designed   maximum temperature ( +10° C)  for 1000hours.  The elongation/creep strain of the conductor during this period shall be measured and recorded at end of 1hour, 10hour, 100hour and subsequently every100 hour up to 1000hours time period. After completion of the above, the core of the conductor sample shall be subjected to UTS test as mentioned above at clause1.1 of Annexure-A. The conductor core shall withstand a load equivalent to 95 % of UTS. In case of polymer composite core conductor, the flexural strength & glass transition temperature of the core shall also be evaluated and the same shall not be degraded by more than 10% over the value guaranteed in the GTP. The value of the Tg after the test, shall however, in no case be less than the design maximum temperature of the conductor. The supplier shall plot the thermal elongation with temperature.

The supplier shall furnish details of creep characteristic in respect of the conducted based on laboratory test and other laboratory investigations/experimental conducted on similar type of conductor and shall indicate creep strain values corresponding to 1-month, 6-month, 1-year, 10-year & 20-year creep at everyday tension & designed maximum temperature as well as room temperature.

1.7 	Sheaves Test

The conductor sample of minimum length of 35 meter shall be tensioned at 25% of the UTS and shall be passed through pulleys having diameter of 32 times that of the conductor with angle of 20° between the pulleys. The conductor shall be passed over the pulleys 36times a speed of 2m/sec. After this test UTS test on the conductor shall be carried out as mentioned above at clause 1.1. In case of polymer composite core conductors, the core shall be inspected for any sign of damage or cracking through dye penetration test as per ASTM D5117.

1.8	Axial Impact Test

The conductor sample shall be suspended vertically and load applied by dropping a 650 Kg from an elevation of 4 meters above the sample. The impact velocity shall be not less than 8 m/sec. with an initial pre-tension of 200kgs. The curve for load vs. time shall be recorded and recorded load of failure for core shall not be less than UTS of core.

1.9	Radial Crush Test

A section of conductor is to be crushed between two six inch steel plates. Load shall be held at 350Kgs for 1 minute and then released. Core/All the core strands shall be subsequently disassembled and tensile tested. Core/All the core strands shall exhibit full strength retention vis-à-vis guaranteed breaking strength of core wires (after stranding)

1.10     Torsional Ductility Test

The conductor sample of 10-15m shall be loaded to 25% of UTS and then rotated in increasing steps of +/-180deg. The entire conductor shall with stand at least 16 such rotations and there shall not be any damage to Aluminium Alloy or core wires. In case of composite core conductors, after 4 rotations or after separation of aluminium strands, the aluminium wires shall be cut and removed from the conductor and the exposed core shall be twisted up to 16 rotations. The composite core shall not break after completion of 16 rotations.

1.11	    Aeolian Vibration Test

The conductor and supporting hardware shall be loaded to 25% of RTS. A dynamometer, load cell, calibrated beam or other device shall be used to measure the conductor tension. Some means should be provided to maintain constant tension to allow for temperature fluctuations during the testing. The overall span between system terminations shall be a minimum of 30m. The span shall be supported at a height such that the static sag angle of the cable to horizontal is (1.5 + 0.5)deg in the active span. Means shall be provided for measuring and monitoring the mid-loop (antinodes) vibration amplitude at a free loop, not a support loop.

An electronically controlled shaker shall be used to excite the conductor in the vertical plane. The shaker armature shall be securely fastened to the conductor so it is perpendicular to the conductor in the vertical plane. The shaker should be located in the span to allow for a minimum of six vibration loops between the suspension assembly and the shaker

The test shall be carried out at one or more resonance frequencies (more than 10 Hz). The amplitude at the anti-node point shall be one third of conductor diameter. The assembly shall be vibrated for not less than 10 million cycles without any failure. After the test, the conductor should not exhibit any damage (broken strands). The conductor shall be tested to demonstrate that it retains at least 95% UTS.

1.12     Temperature Cycle Test

The purpose of this test is verification of degradation characteristics of metallic and non-metallic material when subjected to thermal cycling temperature cycling can create large internal stresses due to thermal expansion mismatch between constituents.

Test Methods:

- Mechanical tension, tension as that of every day condition of the proposed conductor “initial condition” from PLSCADD, marks on the conductor at the edge of the conductor.

- 100 cycles from room temperature up to designed maximum temperature. Hold at maximum temperature +2.5°C for 5 minutes.

- After the above mentioned 100 cycles, the mechanical tension shall be increased up to 70% of UTS at room temperature and kept at this tension for 24Hrs. Thereafter, release to tension as that of everyday condition of the proposed conductor “initial condition” from PLSCADD.

- This cycling test shall be repeated 5times.

- During the test, temperature of connectors, conductor and resistance are recorded according to ANSI 119.

- A breaking load test is applied at the end of the test.

Conductor strength has to be higher than 95% UTS.

- In case of polymer composites, the flexural strength should not be less than 90% of the value guaranteed in GTP and the Glass Transition temperature shall not be less than 90% of the value guaranteed in GTP after thermal cycling. Flexural strength shall be obtained on the basis of test procedure.

Concerning polymer core conductor, it is recommended to make a Tg and bending tests on initial and aged conductor. The maximum test temperature must be defined by manufacturer. At the end of the test the Tg and bending test will be performed. Final and initial values will be compared. The (Tg) drop should be less than10% of the guaranteed in the GTP and any change in flexural should be less than10%.

1.13	Heat Resistance test on Aluminium Alloy wire

Breaking load test as per clause 1.21 above shall be carried out before and after heating the sample in uniform heat furnace at following temperature for one hour. The breaking strength of the wire after heating shall not be less than the 90% of the breaking strength before heating:-

| Maximum continuous operating temperature of the conductor | Test Temperature |
| --- | --- |
| Up to 150 deg. C | 230 deg C (+5/-3 deg C) |
| More than 150 deg. C & up to 210 deg. C | 280 deg C (+5/-3 deg C) |
| More than 210 deg. C & up to 230 deg. C | 400 deg C (+5/-3 deg C) |

1.14	Bending test on Aluminium clad core strand

A sample of aluminium clad invar strand measuring 30 cm in length shall be subject to bending with help of a vise. The vised length of wire should be 5 cm and radius of bend 4.8 mm. The bending should be first 90 degrees left and 90 degree right. After this operation the strand should cut at the bending point. There should be no separation of core and aluminium at the bending point after this operation.

1.15	Compression test on Aluminium clad strand

A sample of aluminium clad core strand 10mm in length is to be compressed by a plate with a load of 3600kgs. The aluminium and core strand should not break.

1.16     Coefficient of linear expansion for core/core strands

The temperature and elongation on a sample shall be continuously measured and recorded at interval of approximately 15 degree C from 15 degree C to maximum continuous operating temperature corresponding to rated current (700A) by changing the temperature by suitable means. Coefficient of linear expansion shall be determined from the measured results.

1.17      Strand Brittle fracture test (for polymer composite core only):

The sample shall be tensioned to approx. 25% of UTS with simultaneous application of 1N-HNO3 acid directly in contact with naked polymer composite core for 96hrs. The contact length of acid shall not be less than 40mm and thickness around the core not less than 10mm. The rod shall withstand 80% of SML for 96 hours.

1.18	Visual and Dimensional Check on Drums

The drums shall be visually and dimensionally checked to ensure that they conform to the approved drawings.

1.19	Visual Check for Joints, Scratches etc.

Conductor drums shall be rewound in the presence of the Owner. The Owner shall visually check for scratches, joints etc. and that the conductor generally conform to the requirements of this Specification. Ten percent (10%) drums from each lot shall be rewound in the presence of the Owner's representative.

1.20	Dimensional Check on Core Strands and Aluminium Alloy Strands

The individual strands shall be dimensionally checked to ensure that they conform to the requirement of this Specification.

1.21	Check for Lay-ratios of Various Layers

The lay-ratios of various layers shall be checked to ensure that they conform to the guaranteed values furnished by the Contractor.

1.22	Galvanizing Test

The test procedure shall be as specified in IEC: 888. The material shall conform to the requirements of this Specification. The adherence of zinc shall be checked by wrapping around a mandrel four times the diameter of steel wire.

1.23	Aluminum thickness on aluminum clad wires

The thickness of aluminium of the specimen shall be determined by using suitable electrical indicating instruments operating on the permeameter principle, or direct measurement. Measurements shall be read to three decimal places, and number rounded to two decimal places is considered as measured thickness. For reference purposes, direct measurement shall be used to determine aluminium thickness on specimens taken from the end of the coils.

1.24	 Torsion and Elongation Tests on Core Strands/composite core

The test procedures for Torsion and Elongation tests on core wires shall be as per clause No. 6.3.3 and 6.3.2 b) of IEC 61232 respectively. In torsion test, the number of complete twists before fracture shall not be less than 18 on a length equal to 100 times the standard diameter of the strand. In case test sample length is less or more than 100 times the stranded diameter of the strand, the minimum number of twists will be proportioned to the length and if number comes in the fraction then it will be rounded off to next higher whole number. In elongation test, the elongation of the strand shall not be less than 1.5% for a gauge length of 250 mm. In case of composite core High Performance Conductor, the following procedure shall be applicable:-

i)   Elongation Test:-

The elongation of the composite core sample at fracture shall be determined using extensometer. The load along the core shall be gradually increased. The elongation achieved on reaching the tensile strength of the core shall not be less than the value guaranteed in the GTP.

- Torsion Test:

The purpose of the test is to determine the resilience of the composite core to twisting and to show that after the composite core has experienced the prescribed twisting, it will not crack or have a loss in tensile strength due to the twisting. A sample length that is 170 times the diameter of the composite core being tested is mounted in the gripping fixtures. One grip shall then be fixed so that it does not twist and the other end shall be twisted a full 360 degrees and then fixed in this position for 2 minutes. Once the twist time is completed, the core is untwisted and inspected for any crazing or other damage. If no damage is observed, the composite core is then tensile tested to failure and the final load recorded. For the test to be accepted, the composite core must withstand at least 100% of its rated tensile strength. Two samples need to be completed in order to satisfy the testing requirement.

1.25	Breaking load test on Aluminium Alloy & Core strands and D.C Resistance test on Aluminium Alloy wire

The above tests shall be carried out as per IEC: 888/889 and the results shall meet the requirements of the specification.

1.26	Wrap test on Core strands (Applicable for steel/Al clad Steel core only)

The wrap test on steel strands shall meet the requirements of IEC: 888. In case of aluminium clad core wire, the same shall be wrapped around a Mendel of diameter of five times that of the strand to form a helix of eight turns. The strand shall be unwrapped. No breakage of strand shall have occurred.

1.27	Resistivity test on thermal resistant aluminium alloy strands

Resistivity test as per IEC-468/IEC 889 shall be conducted to confirm minimum conductivity as per specification requirement.

1.28	Procedure Qualification test on welded Aluminium Alloy strands

Two Aluminium Alloy wire shall be welded as per the approved quality plan and shall be subjected to tensile load. The breaking strength of the welded joint of the wire shall not be less than the guaranteed breaking strength of individual strands.

1.29	Ageing Test on Filler (if applicable)

The test shall be done in accordance with Grease drop point test method. The specimen should be drop as a droplet when kept at a temperature 40 deg. C above designed maximum operating temperature of the conductor for 30 minutes. The temperature shall then be increase till one droplet drops and the temperature recorded.

1.30	Resistivity test on aluminium clad wire

Resistivity test as per IEC-468 shall be conducted to confirm minimum conductivity as per specification requirement.

1.31   Glass Transition Temperature Test (for Polymer composite core only)

Test shall be conducted as per ASTM B987. The minimum glass transition temperature shall be either (i) the design maximum continuous operating temperature of the offered High Performance Conductor + 35 Deg C or (ii) minimum glass transition temperature as per ASTM B987 i.e.180 deg. C + 25 Deg C ; Whichever is lower.

In case, the design maximum continuous operating temperature of the offered High Performance Conductor is more than the minimum glass transition temperature as per ASTM B987 i.e. more than 180 deg. C, the test shall be conducted as per ASTM B987 & the minimum glass transition temperature shall be the design maximum continuous operating temperature of the offered High Performance Conductor + 25 Deg C.

1.32     Flexural Strength Test for composite core:

Test method shall be as per ASTM D7264, ASTM D4475 or ISO 14125. The flexural strength shall not be less than the value guaranteed in the GTP

1.33     Chemical Analysis of Aluminium Alloy and Core

Samples taken from the Aluminium and core coils/strands shall be chemically/spectrographically analyzed. The same shall be in conformity to the particulars guaranteed by the bidder so as to meet the requirements stated in this Specification.

1.34	Chemical Analysis of Zinc

Samples taken from the zinc ingots shall be chemically/ spectrographically analyzed. The same shall be in conformity to the requirements stated in the Specification.

1.35     AC Resistance Test:

The sample length taken shall be 5m. The end terminations shall be dead end. A mechanical force of the tension as that of every day condition of the proposed conductor– “Initial condition” from PLSCADD tension at everyday condition shall be applied to the conductor. This mechanical force shall be maintained during all the test even at high temperature. Use appropriate measuring instruments in order to determine DC & AC resistance.

Generally, voltage (U), current (I) and phase angle (ϕ) between voltage & current are measured.

Rac = (UCosϕ)/I

As difference between DC & AC resistance is very less, accurate instrumentation shall be chosen. Reference length for voltage measurement shall be at least 2mtrs and 1.5m from span extremities. It shall be checked properly that no thermal effect due to dead end impacts reference length temperature. Follow the procedure mentioned:

DC resistance shall be measured before the beginning of test. Apply 10 short current pulses from 0A to maximum current (700A) at room temperature. Pulse duration shall be determined in order to have no conductor temperature change and enough time to perform measurement. Between each current pulse, 30min should be kept. This shall allow temperature to be homogeneous along and inside the conductor.

DC resistance shall be measured before the beginning of test and if possible at each current step. 10 current steps shall be determined in order to assess AC resistance between 0A and maximum current (700A). Current shall be applied to the conductor and maintained during at least 60min before AC resistance measurement. It shall be checked that temperature is stabilized before performing measurements. Specific care shall be taken in order to avoid uneven temperature on reference length. DC resistance and AC resistance shall be corrected according to temperature & up-to-date devices giving the same results can be used for the AC resistant measurements.

1.36     Salt Spray Test:

The test shall be performed as per ASTM B117 on 3 samples of conductor, each 1 m in length. The three samples shall be simultaneously subjected to salt spray exposure in an environmental chamber for 1000 hours. After this test, the individual strands and composite core shall be subjected to visual examination and tensile strength test. There shall be no pitting, corrosion or deterioration on any component of the conductor after 1000 hrs of salt-spray exposure. The individual strands of aluminium/ aluminium alloy and the composite core shall retain 95% of the strength guaranteed in GTP.

1.37        Bending Test on Polymer Composite Core (Type Test)

Bending test on polymer composite core (CFC) before stranding shall be performed as per ASTM B987/B987M-17 on polymer composite core samples taken from composite core at conductor manufacturing unit before stranding of conductor. Alternatively, supplier may carry out bending test on polymer composite core (CFC) before stranding on the samples taken at the core manufacturing unit, from the same reel being supplied to conductor manufacturer subject to proper traceability of the same at the conductor manufacturers works.

Bending test on polymer composite core (CFC) shall also be performed as per ASTM B987/B987M-17 on polymer composite core samples taken from stranded conductor. For test after stranding the diameter of cylindrical mandrel shall be as following:

- For high strength grade CFC – 60 times the diameter of CFC

- For Extra high strength grade CFC – 70 times the diameter of CFC

1.38        Bending Test on Polymer Composite Core (Acceptance Test)

Bending test on polymer composite core (CFC) shall also be performed as per ASTM B987/B987M-17 on polymer composite core samples taken from stranded conductor. For test after stranding the diameter of cylindrical mandrel shall be as following:

- For high strength grade CFC – 60 times the diameter of CFC

- For Extra high strength grade CFC – 70 times the diameter of CFC

GUARANTEED TECHNICAL PARTICULARS OF HIGH PERFORMANCE CONDUCTOR

| Sl. |  | Description |  |  |  | Unit |  | Value guaranteed by the Bidder |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1. |  | Name & address of Manufacturer |  |  |  |  |  |  |  |  |
| 2. |  | Construction of conductor/ Designation of conductor as per IEC:1089 |  |  |  |  |  |  |  |  |
| 3.1 |  | PARTICULARS OF RAW MATERIALS |  |  |  |  |  |  |  |  |
| 3.1 |  | Outer Layers - Applicable Standard (if any) - Type of Aluminum/ alloy - Minimum purity of aluminum - Maximum Copper content - Zirconium content - Maximum - Minimum e) Other elements---------- - ---------- - ---------- |  |  |  | % % % % % % |  |  |  |  |
| 3.2 |  | Inner Core - Applicable Standard (if any) - Material of core - Chemical composition of core - ---------- - ---------- |  |  |  | % % |  |  |  |  |
| 3.3 |  | Zinc used for galvanization of inner core (if applicable) a) Minimum purity of zinc |  |  |  | % |  |  |  |  |
| 3.4 |  | Chemical Composition of Misch Metal coating on core wires (if applicable) i) Zinc ii) Aluminium iii) Other elements |  |  |  | % % % |  |  |  |  |
| 3.5 |  | Aluminium used for Aluminium Cladding (if applicable) a) Minimum purity of aluminum b) Maximum Copper content c) Other elements |  |  |  | % % % |  |  |  |  |
| 4. |  | STRANDS OF OUTER CONDUCTING PART (AFTER STRANDING) |  |  |  |  |  |  |  |  |
| 4.1 |  | Number of outer layers |  |  | Nos. |  |  |  |  |  |
| 4.2 |  | Number of strands a) 1st Layer from core b) 2nd Layer from core c) 3rd Layer from core |  |  | Nos. Nos. Nos. |  |  |  |  |  |
| 4.3 |  | Diameter of strands - Nominal - Maximum - Minimum |  |  | mm mm mm |  |  |  |  |  |
| 4.3 |  | Minimum Breaking load of strand - Before stranding - After stranding |  |  | kN kN |  |  |  |  |  |
| 4.4 |  | Resistance of 1m length of strand at 20 deg. C |  |  | Ohm |  |  |  |  |  |
| 4.5 |  | Final Modulus of elasticity |  |  | Kg/sq. mm |  |  |  |  |  |
| 4.6 |  | Final Coefficient of linear expansion |  |  | Per 0 C |  |  |  |  |  |
| 5 |  | INNER CORE STRANDS/ INNER CORE (AFTER STRANDING) |  |  |  |  |  |  |  |  |
| 5.1 |  | Number of layers in inner core (excluding central wire) |  |  |  |  |  |  |  |  |
| 5.2 |  | Number of strands a) 1st Layer from center (excluding central wire) b) 2nd Layer from center c) 3rd Layer from center |  |  | Nos. Nos. Nos. |  |  |  |  |  |
| 5.3 |  | Diameter - Nominal - Maximum - Minimum |  |  | mm mm mm |  |  |  |  |  |
| 5.3 |  | Minimum Breaking load of strand/Core - Before stranding - After stranding |  |  | kN kN |  |  |  |  |  |
| 5.4 |  | Resistance of 1m length of strand at 20 deg. C |  |  | Ohm |  |  |  |  |  |
| 5.5 |  | Final Modulus of elasticity |  |  | Kg/sq. mm |  |  |  |  |  |
| 5.6 |  | Final coefficient of linear expansion |  |  | Per 0 C |  |  |  |  |  |
| 5.7 |  | Aluminum cladding of INVAR core (if applicable) |  |  |  |  |  |  |  |  |
|  |  | a) Thickness of cladding |  |  |  |  |  |  |  |  |
|  |  | - Maximum |  | Mm |  |  |  |  |  |  |
|  |  | - Minimum |  | Mm |  |  |  |  |  |  |
|  |  | b) Minimum no. of twists in a guage length equal to 100 times diameter of wire which the strands can withstand in the torsion test i) Before stranding ii) After Stranding |  | Nos Nos |  |  |  |  |  |  |
|  |  | c) Minimum elongation of strand for a gauge length of 250 mm |  | % |  |  |  |  |  |  |
|  |  | - Resistance of 1m length of strand at 20 deg.c |  | Ohms |  |  |  |  |  |  |
| 5.8 |  | Galvanized/Misch Metal coating (if applicable) |  |  |  |  |  |  |  |  |
|  |  | - Minimum Mass of Zinc Coating per Sqm. |  |  | gm |  |  |  |  |  |
|  |  | - Minimum mass of Misch metal coating per sqm. Of uncoated wire surface (if applicable ) |  |  | gm |  |  |  |  |  |
|  |  | - Min. No. of twist a single strand shall withstand during torsion test for a length equal to 100 times dia. of wire after stranding |  |  | No.s |  |  |  |  |  |
|  |  | - Minimum elongation of strand for a gauge length of 250 mm |  |  | % |  |  |  |  |  |
| 5.9 |  | Carbon-fibre composite core (if applicable) |  |  |  |  |  |  |  |  |
|  |  | - Minimum elongation of core which the core will achieve elongation |  |  | % |  |  |  |  |  |
|  |  | - Flexural strength |  |  | Mpa |  |  |  |  |  |
|  |  | - Glass Transition |  |  | C |  |  |  |  |  |
| 6 |  | FILLER (if applicable) |  |  |  |  |  |  |  |  |
| 6.1 |  | Type & Designation of Filler |  |  |  |  |  |  |  |  |
| 6.2 |  | Chemical composition of Filler |  |  |  |  |  |  |  |  |
| 6.3 |  | Mass of Filler |  |  | Kg/km |  |  |  |  |  |
| 7 |  | COMPLETE HIGH PERFORMANCE CONDUCTOR |  |  |  |  |  |  |  |  |
| 7.1 |  | Cross section drawing of the offered conductor enclosed |  |  | Yes/No |  |  |  |  |  |
| 7.2 |  | Diameter of conductor - Nominal - Maximum c) Minimum |  |  | mm mm mm |  |  |  |  |  |
| 7.3 |  | UTS (minimum) of Conductor |  |  | kN |  |  |  |  |  |
| 7.4 |  | Lay ratio of conductor - 1st layer from Centre (excluding central wire) - 2nd Layer - 3rd Layer |  |  |  |  |  | Max. |  | Min. |
| 7.5 |  | DC resistance of conductor at 20oC |  |  | Ohm/ km |  |  |  |  |  |
| 7.6 |  | Final Modulus of elasticity |  |  |  |  |  |  |  |  |
|  |  | - Up to transition temperature |  | Kg/sq. mm |  |  |  |  |  |  |
|  |  | - Above transition temperature |  | Kg/sq. mm |  |  |  |  |  |  |
| 7.7 |  | Coefficient of linear expansion |  |  |  |  |  |  |  |  |
|  |  | - Up to transition temperature |  | Per deg C |  |  |  |  |  |  |
|  |  | - Above transition temperature |  | Per deg C |  |  |  |  |  |  |
| 7.8 |  | Calculation for transition temperature enclosed |  | Yes/No |  |  |  |  |  |  |
| 7.9 |  | Transition temperature (corresponding to 275M ruling span and tension at ruling condition as per 7.19) |  | Deg C |  |  |  |  |  |  |
| 7.10 |  | Maximum permissible conductor temperature for continuous operation |  | Deg C |  |  |  |  |  |  |
| 7.11 |  | Maximum permissible conductor temperature for short term operation |  | Deg C |  |  |  |  |  |  |
| 7.12 |  | Permissible duration of above short term operation |  | Minutes |  |  |  |  |  |  |
| 7.13 |  | Steady state conductor temperature at conductor current of 700A and under Ambient conditions detailed in Clause 1.2.1 of Section-II of the Technical Specification (Vol-II) |  | Deg C |  |  |  |  |  |  |
| 7.14 |  | AC resistance at maximum continuous operating temperature corresponding to specified maximum operating current (700 A under ambient condition enclosed as per Clause 1.2.1 of Section-II of the Technical Specification) |  | Ohm/km |  |  |  |  |  |  |
| 7.15 |  | AC resistance at continuous operating temperature corresponding to specified operating current of 720A) under ambient condition enclosed as per Clause 1.2.1 of Section-II of the Technical Specification) |  | Ohm/km |  |  |  |  |  |  |
| 7.16 |  | Details of Creep characteristic for High Performance Conductor enclosed (as per Clause 1.4.3 of Section-II of the Technical Specification (Vol-II)) |  | Yes/No |  |  |  |  |  |  |
| 7.17 |  | Sag Tension Calculation |  |  |  |  |  |  |  |  |
| 7.17.1 |  | Sag Tension Calculation enclosed (clause 1.4.1 of Sec-II of TS) |  | Yes/No |  |  |  |  |  |  |
| 7.17.2 |  | Tension at 32 deg. C & no wind |  | Kg |  |  |  |  |  |  |
| 7.17.3 |  | Sag & tension at maximum continuous operating temperature (corresponding to current of 700A and Ambient conditions detailed in Clause 1.4.1 of Section-II of the Technical Specification (Vol-II)) |  | Meters & Kgs |  |  |  |  |  |  |
| i) |  | Tension for following conditions: |  |  |  |  |  |  |  |  |
| a) |  | 32 deg. C & full wind condition |  | Kg |  |  |  |  |  |  |
| b) |  | 32 deg. C & Nil wind condition |  | Kg |  |  |  |  |  |  |
| c) |  | Minimum temperature & Nil wind condition |  | Kg |  |  |  |  |  |  |
| d) |  | Minimum tempt. & 36% of full wind condition |  |  |  |  |  |  |  |  |
| e) |  | 32 deg. C & 75% of full wind condition |  |  |  |  |  |  |  |  |
| ii) |  | Tension at 10deg. C & 2/3 wind pressure of 28.67 kg/m² |  | Kg |  |  |  |  |  |  |
| 7.17.4 |  | Tension at transition temperature |  | Kg |  |  |  |  |  |  |
| 7.18 |  | Direction of lay for outside layer |  |  |  |  |  |  |  |  |
| 7.19 |  | Linear mass of the Conductor - Standard - Minimum - Maximum |  | Kg/km Kg/km Kg/km |  |  |  |  |  |  |
| 7.20 |  | Standard length of conductor |  | M |  |  |  |  |  |  |
| 7.21 |  | Maximum length of conductor that can be offered as single length |  | M |  |  |  |  |  |  |
| 7.22 |  | Tolerance on standard length of conductor |  | % |  |  |  |  |  |  |
| 7.23 |  | Drum is as per specification |  | Yes/No |  |  |  |  |  |  |
| 7.24 |  | No. of cold pressure butt welding equipment available at works |  | Nos. |  |  |  |  |  |  |

| Date: | (Signature)…………………………… |
| --- | --- |
| Place: | (Printed Name) …………………….. |
|  | (Designation)……………………….. |
|  | (Common Seal) ……………………… |