TECHNICAL SPECIFICATION FOR STEEL MONOPOLE STRUCTURE FOR TRANSMISSION LINE

(Design, Testing, Fabrication & Supply of 220KV D/C Monopoles)

Karnataka power Transmission Corporation Limited

Part I(A)

General

Brief Description of the project:

The project envisages:

Construction of 220KV DC line on 220KV DC Towers & 220KV DC Monopoles from the existing 220KV Indi Substation to proposed 220/110KV Chadachan substation for a distance of 29.628Kms. As per the detailed survey report, 03Nos. of 220KV D/C Monopoles are provisioned construction of proposed 220KV D/C line.

The 220KV Double-circuit line is to be constructed on 220KV double-circuit lattice towers and 220kV double circuit Monopoles using AAAC Moose conductor. KPTCL has conducted the preliminary survey to access the quantity of Monopoles and lattice towers. Since the existing 220KV IPP Savalsang line and its associated towers are located within the same survey number through which the proposed line is passing. Therefore, to avoid potential future ROW issues, provision has been made for 03Nos. of 220KV D/C design-based Monopoles.

As per the detailed survey report, 03Nos. of 220KV double-circuit Monopoles (design based) and 122Nos. of 220KV D/C Lattice type towers are being used.

The maximum diameter of the monopole pole shall be restricted to 1.5 - 2.0M at Normal level.

Important: The bidders shall compulsorily visit the spot and inspect each location to access the suitability of pole and if there is any suggestion the same may be brought in the pre-bid meeting.

TECHNICAL SPECIFICATIONS FOR 220KV DOUBLE CIRCUIT HIGH TENSILE STEEL TUBULAR POLES

- INTRODUCTION

This specification covers the technical and associated requirements for tubular steel pole type of transmission lines used in electric power transmission rated 220KV double-CIRCUIT line. The poles shall be supplied complete with structural steel works, bolts, nuts, washers and miscellaneous fittings.

The purchaser is looking for safe design of mono-pole keeping the loading and line parameters as detailed in the specification. The high tensile tubular mono-poles shall be with polygon cross-section and tapered from base to top. The Double-circuit pole shall be designed to carry 06 no’s of AAAC Moose conductor and one of 48 fibre OPG Wire. The configuration of the pole shall be such that it satisfies all the Electrical clearances such as live metal clearances, mid-span clearance, ground clearance etc., as per IS: 5613.

The bidder may offer the most economical design considering the total cost of super structure and foundation.

It is not KPTCL’s intent to outline all the technical requirements or to set forth those requirements adequately covered by applicable codes and standards. Contractor shall furnish high quality work and materials meeting the requirements of this specification and industry standards.

The Contractor shall bear full responsibility that the steel poles have been designed and fabricated in accordance with all codes, standards and applicable governmental regulations and perform under the condition and to the standards specified herein.

No departure shall be made from this specification and standards unless waived or modified in writing by KPTCL. Contractor shall obtain from its sub-Contractors a statement as to compliance with this specification without exception and/or if there are any exceptions, these shall be described in detail and included in Contractor's proposal. Contractor shall add a statement that no other exceptions are taken to this specification.

The bidder shall note that the design of the pole becomes the property of the purchaser in case orders are placed & the purchaser reserves the right to adopt the design in any of their future projects. The Contractor shall furnish detailed design documents of each type of pole along with foundation design and a complete set of reproducible fabrication drawings to KPTCL.

Contractor shall have the technical and manufacturing support of a reputed national / international manufacturer of Monopoles. The manufacturer shall make a written agreement with the contractor for providing design and manufacturing support for the project. Copy of the agreement shall be submitted along with the tender. The contractor cannot change the pole manufacturer after the submission of the tender.

  - POLE MANUFACTURER’S EXPERIENCE.

The pole manufacturer shall meet the manufacturing experience as stipulated in the qualifying requirements of the commercial condition of the contract.

The manufacturer shall also be capable of manufacturing Monopoles of diameter of 2400mm with a wall thickness of 25mm.

The pole manufacturer should also have conducted full scale testing of their pole for 220 KV or above voltage levels. Copies of previous test reports for such poles shall be submitted along with the offer. The type test should have been conducted within 5 years as on the date of bidding.

- CODES AND STANDARDS.

The specified material and services shall be furnished in accordance with, but not limited to, the following codes and standards or to applicable Indian/international standards,

In case Indian standards are not available for any of the items, relevant ASTM codes as mentioned shall be adhered to manufacturing and installation.

BIS – Bureau of Indian Standards.

IS: 802 (Part-1/Sec-1) & IS: 802 (part-1/Sec-2) – 2015 & 2016 Use of structural steel in overhead transmission line towers. Materials, Loads and Permissible stresses.

IEC 60652 - Loading tests on overhead line structures.

IS: 5613 (Part-2/Sec-1) 1985 – Code of practise for design installation and maintenance of overhead lines.

ASTM – American Society for Testing and Materials.

A 36 / 36 M.	Standard Specification for Structural Steel, Book 01.04

A 123.	Specification for Zinc (Hot-Dip Galvanized) Coatings on iron and Steel Products, Book 01.06, 15.08.

A 143-89.	Recommended Practice for Safeguarding Against Embrittlement of Hot Dip Galvanized Structural Steel Product and Procedure for Detecting Embrittlement

A 153.	Specification for Zinc Coating (Hot Dip) on Iron and Steel Hardware, Book 01.06.15.08.

A 307.	Standard Specification for Carbon Steel Bolts and Studs, 60,000 psi Tensile, B00k 01.01, 15.08.

A 325.	Specification for Structural Bolts, Steel, Heat Treated, 120/105 ksi Minimum Tensile Strength, Book 15.08.

A 354.	Specification for Quenched and Tempered Alloy Steel Bolts, Studs and Other Externally Threaded Fasteners.

A 370.	Test Methods and Definitions for Mechanical Testing of Steel Products.

A 384.	Recommended Practice for Safeguarding against Warpage and Distortion during Hot-dip Galvanizing of Steel Assemblies.

A 394.	Standard Specification for Galvanized Steel Transmission Tower Bolts and Nuts.

A 449.	Specification for Quench and Tempered Steel Bolts and Studs.

A 490.	Specification for Heat Treated, Steel Structural Bolts, 150 ksi (1035 Mpa) Tensile Strength.

A 563.	Specification for Carbon and Alloy Steel Nuts.

A 572/572M.	Specification for High-Strength Low Alloy Columbium Vanadium Steels of Structural Quality.

A 588/588M.	Specification for High Strength Low-Alloy Structural Steel with 50 ksi (345 Mpa) Minimum Yield Point to 4 in. (100 mm) Thick.

A 633/633M.	Specification for Normalized High Strength Low Alloy Structural Steel.

A 673/673M.	Specification for Sampling Procedure for Impact Testing of Structural Steel.

A 687.	 Specification for High Strength Non-Headed Steel Bolts and Studs.

A 780.	Practice for Repair of Damaged and Uncoated Areas of Hot-Dip Galvanized Coatings.

A 871/871M.	Specification for High Strength Low Alloy Structural Steel Plate with Atmospheric Corrosion Resistance.

F 436-82.	Standard Specification for Hardened Steel Washers.

AWS – American Welding Society.

D1.1-92.	Structural Welding Code – Steel.

Specification for Carbon Steel Covered Arc-Welding Electrodes.

A5.17-89.	Specification for Carbon Steel Electrodes and Fluxes for Submerged Arc-Welding

ASCE – American Society of Civil Engineers.

ASCE/SEI 48, "Design of Steel Transmission Pole Structures," /CBIP manual July 2014 (Publication No-323)

ISO – International Standards Organisation.

ISO 9001.	Quality System Model for Quality Assurance in Design/Development, Manufacture and Testing.

ISO 9002.	Quality System Model for Quality Assurance in Production, I installation and Servicing.

CEA (Technical Standards for Construction of Electrical Plants and Electric lines) Regulations and CEA (Measures relating to Safety & Electric Supply) Regulations shall be followed.

These codes and standards set forth the minimum requirements which may be exceeded by Contractor if, in Contractor's judgment and with KPTCL acceptance, superior or more economical designs and materials are available for successful and continuous operation of Contractor's equipment as required by this specification.

- MONOPOLES: TYPES AND FITTINGS

3.1		GENERAL DESCRIPTION:

i)   220KV Design based Double circuit Monopoles.

ii) Monopole types/deviation limits/typical use:

The monopole types are classified as given in the following Table:

| Type | Deviation limit | Typical use |
| --- | --- | --- |
| 2P3+0 & 2P3+3M | 300 to 600 deviations With Dead End (0° - 15°) | - Angle tower with tension insulator string. - Tension tower for uplift forces resulting from a uplift span. - For angle of deviation of 30 to 60 deg. - For Dead End condition 0 – 15 deg. |

(iii) The three phase conductors of the Double circuit towers / Monopoles shall be in vertical formation (I, I, I)

3.2	BODY EXTENSIONS:

Each type of monopole shall be designed with 0M & 3M body extension.

- TECHNICAL REQUIREMENTS FOR POLES.

4.1.	DESIGN.

4.2	General.

The pole structure shall be designed as per ASCE standard 48-19 (or subsequent revision) as applicable except otherwise specified in this specification considering loading requirement except wind loading on body of the steel pole) as stipulated in latest versions of IS: 802. Load on the pole body due to wind shall be calculated as

per IEC 60826 and relevant formula for calculation is given below for reference. For calculation of wind load, the basic wind speed shall be as per wind map given in National Building Code 2016. Manufacturers shall provide attachment points/devices at various locations on the pole body for application of wind loads during prototype testing of pole.

For pole structures to be used in the areas up to 60 km from sea coast, K4 factor (i.e. importance factor for cyclonic region) of 1.3, as per IS: 875-3, shall also be considered for calculation of design wind speed i.e. Vd = VRK1K2K3K4 to be used in IS 802.

AII designs are to be made in accordance with the information provided herein and on the accompanying outline drawings. AII outline dimensions are fixed but where no dimensions are given, the framing, may be modified to suit the Contractor's design, subject to compliance with all the requirements of the specification.

The steel poles design calculations shall be the responsibility of the pole manufacturer. It shall be designed for the configuration, loadings and limitations provided elsewhere in the tender documents.

The Contractor, at KPTCL request, shall explain and provide all the necessary information pertaining to the design of any or all elements of the structure.

Structures shall be designed so that member unit stress does not exceed the yield point stress of the material. The ratio of major axis of tubular diameter to wall thickness shall be such that local buckling does not govern member design.

The maximum deflection of 5% (under ultimate load condition) of the height of pole shall be considered in the design where there is no restriction at site. However maximum deflection during testing shall not exceed 8% after testing for 10 critical load cases. Deflection during everyday loading conditions should not exceed 2%. However, in any situation, the required electrical clearance at site has to be maintained as per Central Electricity Authority (Measures Relating to Safety and Electric Supply) Regulations.

Cross section of the pole shall be polygon and shall be tapered from top to the base.

Cross arm member shall be of polygonal cross section with taper and shall conform to KPTCL's general arrangement drawings. The strength of the attachment of cross arms to the columns shall be sufficient to develop the full capability of the cross arm.

Members requiring more than one length of tubular section shall be constructed by telescoping the sections together with sufficient overlap to develop the full strength of the member. Minimum overlap shall be 1.5 times the maximum inside diameter of outer section at the telescopic joint.

Rigging accessories, insulator attachment plates, ladder, lugs for bolted steps and lighting brackets, and hand line attachment shall be welded to the structure.

D/T and W/T Ratio for Design of pole Structure:

While designing the pole structure, the D/T ratio and W/T ratio (D: Diameter of section, W: Width of side, & T: Thickness of sheet), as applicable in line with ACSE 48-19 (or its latest version), shall be maintained properly to avoid buckling and ovality of the individual sections of the pole structure under load during transportation and handling.

Maximum diameter of the Pole: The maximum diameter of the Monopole shall be limited to 1.5 – 2.0M at Normal level.

4.3 Structural Analysis:

Elastic methods of analysis shall be used. Stability shall be provided for the structure as a whole and for each structural element. The load effects resulting from the deflected shape of the structure and individual elements shall be considered during design.

The analysis shall include all structural members (including inter pole ties, bracings and guys, if required) in their actual, manufactured geometry and sizes.

When values for the following are specified in the tender documents, the analysis shall include differences in support elevation, support movement and erection tolerances.

- ELECTRICAL CLEARANCES:

5.1	Ground clearances:

The minimum ground clearance from the bottom conductor shall not be less than 8M under the maximum sag conditions i.e., at maximum temperature and in still air. The bottom cross arm shall be maintained at 15.5M level in order to match the bottom cross arm height of 220KV D/C lattice towers (Gadag – Bagalkote design).

5.2 LIVE METAL CLEARANCES:

The minimum live metal clearance to be provided between the live parts and steel work of superstructure shall be as given in the table-4.

TABLE – 4   (Various live metal clearances in mm)

| Insulator string | Swing Angle | 220KV |
| --- | --- | --- |
| Single Suspension String | 0 Degree Swing | 2130 |
|  | 15 Degree Swing | 1980 |
|  | 30 Degree Swing | 1830 |
|  | 45 Degree Swing | 1675 |
| Double Suspension String | 0 Degree Swing | 2130 |
| Single/Double Tension String | 0 Degree Swing | 2130 |
| Jumpers in Tension String | 0 Degree Swing | 2130 |
|  | 10 Degree Swing | 2130 |
|  | 20 Degree Swing | 1675 |
|  | 30 Degree Swing | 915 |

Note: In case pilot insulator strings are proposed to be used, the angle of swing to be considered shall be a minimum of 15 deg.

In computing live metal clearances, the dimensions of single tension, double tension and single suspension (as pilot insulator) and Double Suspension string shall be taken as given in Annexure A,B,C,D enclosed. The design of the poles shall be such that it should satisfy all the above conditions when clearances are measured from any live point on the insulator strings.

5.3	ANGLE OF SHIELDING:

The angle of shielding is defined as the angle formed by the line joining the centerlines of the earth wire and power conductors, in still air, at pole support to the vertical line through the centerline of earth wire and the same, shall be less than 30 deg. The drop of the earth wire clamp should be considered while calculating the minimum angle of protection.

5.4	MID SPAN CLEARANCE:

The minimum vertical mid span clearance between any of the earth wires and the nearest power conductor shall not be less than 8.5 M.

This is the vertical clearance between the earth wire and the nearest power conductor under all temperatures and in still air condition in the normal ruling span.  Further, the tensions of the earth wires and power conductors shall be so coordinated that the sag of earth wires shall be at least 10% less than that of the power conductors under all temperatures and loading conditions.

5.5   DESIGN LOADS:

The pole shall be designed to withstand the external loading for various loading conditions as shown in the loading trees enclosed with the specification. These loads are factored (ultimate) loads. The following parameters have been considered in the calculation of the loads.

The bidder shall strictly follow the loading trees furnished for the purpose of design of Poles and their foundations. The bidders, however, can re-check the loading calculations and if any discrepancies are observed, the same shall be brought to the notice of the purchaser and obtain the necessary clarification.

The bidder shall furnish the loading calculations and loading tree of design loads in accordance with this specification in his offer.

The ultimate forces in all stress carrying member shall be multiplied by ‘Overload factor’ of 1.02’.

- EXTERNAL LOADS ON POLE

6.1 WIND PRESSURE:

The wind pressure on pole, power conductor and earth wire shall be in accordance with IS-802 (Part1/Section-1)-2015/CBIP Manual-2014, with modifications specified elsewhere in the specification.

6.2 WIND LOAD ON POLE:

The wind load on the exposed area of the pole shall be calculated by the designer and the same shall be furnished. The following data shall be considered for calculation of wind load.

- Wind Zone shall be considered as 1.

- Terrain Category shall be considered as 2.

- Reliability level shall be considered as 2.

6.3 WIND ON CONDUCTORS, GROUND WIRE & INSULATORS:

The wind load on conductor, ground wire and insulator string have been calculated as per IS-802 (Part-1/Sec-1)-2015/CBIP Manual-2014.

The calculated Wind pressures are tabulated below.

Wind pressure in kg/sq.M

| Voltage Class | Power Conductor | Ground Wire | Insulator string |
| --- | --- | --- | --- |
| 220kV | 106.5 | 133 | 133.5 |

- MAXIMUM TENSIONS:

Maximum tension shall be based on either:

- at 10 deg.C with 36% full wind pressure, or

- at 32 deg.C with full wind pressure whichever is more stringent.

- SAG – TENSION CALCULATION:

The sag-tension calculation for conductor & ground wire made in accordance with relevant provision of IS-5613 (Part-2/Sec-1)-1985 is enclosed with this specification as Annexure-E. The bidders, however, can re-check the sag-Tension values and if any discrepancies are observed, the same shall be brought to the notice of the purchaser and obtain the necessary clarification.

- LIMITING TENSIONS OF CONDUCTOR AND EARTHWIRE:

The ultimate tensions of conductor & ground wire shall not exceed 70% of the corresponding ultimate tensile strength.

In addition, the maximum conductor and earth wire tension at 32 deg. C without external load due to wind shall be 25% of the ultimate tensile strength of the conductor and earth wire.

- NORMAL SPAN:

The normal span of the line shall be 150M.

10.1	WIND AND WEIGHT SPANS:

The wind and weight spans to be adopted in the design of the structures shall be as follows:

10.2	WIND SPAN:

The wind span is the sum of the two half spans adjacent to the support under consideration.  For Normal horizontal terrain this shall be equal to Normal span.

10.3	WEIGHT SPAN:

The weight span is the horizontal distance between the lowest points of the conductors on the two spans adjacent to the tower.

The weight spans to be considered in the tower design shall be as follows.

| Weight Span Details |  | 2P3+0M/+3M |
| --- | --- | --- |
| Normal condition | Max. | 225 |
|  | Min. | -225 |
| Broken Wire condition | Max. | 135 |
|  | Min. | -135 |

- CONDUCTOR AND EARTH WIRE CONFIGURATION:

The three phase conductors of the Multi-circuit tower shall be in vertical formation with conductor phase to phase distance for 220kV circuit not less than 4.9 M. The inter circuit conductor to conductor distance shall be 5.0M. Each phase conductor of 220kV circuit consists of single AAAC Moose conductor. 48F OPGW wire will be used as a continuous earth wire at a suitable elevation above the conductors so as to provide effective shielding angle of less than 300 with electrically safe clearance between power conductors and earth wire.

Typical configuration of 220KV Double-Circuit Monopoles carrying six power conductors and one OPGW wire is enclosed as Annexure-F.

- LOADS ON TOWERS:

The external loading viz., Transverse, Longitudinal & Vertical acting at each conductor and ground wire attachment point under I) Reliability  2) Security & 3) Safety conditions has been  calculated by the purchaser, in accordance with IS-802 (Part-1 Sec.1) - 2015 and the same in the form of “Loading Trees” have been furnished as Annexure-G.

- DESIGN CALCULATION AND DRAWINGS:

The following design calculations and drawings are required to be furnished to the purchaser:

- Along with the bid:-

i) Loading trees and line diagrams indicating electrical clearances, steel sheet thickness used all dimensions etc., for Double-circuit Monopole of type 2P3+3M.

ii) Detail design calculation of poles and foundation for ‘2P3+3M’ type pole.

iii) Typical foundation sketches for all types of soil for 2P3+3M.

- On award of Contract:

i)  The successful bidder shall submit the detail design documents of all the 4-types of poles and foundation design for all types of soil conditions, duly vetted and certified by M/s. CPRI, Bengaluru or M/s. SERC, Chennai for the final approval of the purchaser.

ii) 	After obtaining the approval of the design of the pole, the bidder shall develop the structural drawings of each type of pole and submit the same for scrutiny and approval of the purchaser.

The structural drawing shall indicate all the fabrication details such as wall thickness, inside and outside diameter at the top and bottom of each section of the pole, length of overlap, details of the fixing of the main and auxiliary cross arm with the pole, details of the base plate, stiffners and no. of bolts, no. of sides in the polygon section, joint details, etc.,

The details of each joint shall be indicated as expanded view to the higher scale.

iii)	After obtaining the approval for the structural drawings the bidder shall fabricate the proto type assembly of the pole and offer the same for inspection by the purchaser.

iv)	After successful prototype assembly inspection the bidder shall incorporate the changes suggested, if any, during the inspection, in the structural drawings.

v)  Proto type testing:

The successful bidder shall arrange for type testing of pole type 2P3 with +3M Body Extension at any reputed Tower Test bed like CPRI/ any other NABL accredited test bed and intimate the date of testing. The pole testing shall be conducted in the presence of Engineers from Technical Section, O/o. CEE (P&C), KPTCL.

v)   The bidder shall submit the tower “Rigging Chart” issued by the tower testing authorities for verification and approval of the purchaser at least one week before the date of prototype testing.

vi)	After successful testing of the pole in presence of the engineers from KPTCL, the bidder shall furnish the “Type test Report “issued by the tower testing authorities.

vii)	The final structural drawings along with Bill of Materials of the normal pole, all body extension, and base plate shall be submitted for final approval of the purchaser.

viii)	After approval of design, drawings and bill of materials, the successful bidder shall furnish the following in fifteen (15) copies to the purchaser for necessary distribution along with the originals on polyester tracing paper of 50 microns thickness within fifteen (15) days after approval of drawings.

- Detailed design calculations along with drawings of poles and foundations.

- Detailed structural drawings indicating wall thickness, inside and outside diameter at the top and bottom of each section of the pole, length of overlap, details of the fixing of the main and auxiliary cross arm with the pole, details of the base plate, stiffeners and no. of bolts, no. of sides in the polygon section, joint details, etc.,

- Shop drawings showing all details relevant to fabrication.

- All drawings for the pole accessories.

The bidder shall also submit two sets of soft copies on CD of all the above documents to the purchaser

13.1 The contractor is required to submit four copies of the drawings for owner’s approval. While submitting the designs, structural drawings, bill of materials and any other drawings pertaining to the subject transmission line, the contractor shall clearly indicate on each drawing KPTCL specification No., Name of the transmission line and project, letter reference No. and date on which the submission are made. The same practice is also to be followed while submitting distribution copies.

13.2 The design and drawings as covered in clause 13.0 above shall be approved/commented by the owner as the case may be within 30 (thirty) days of receipt of designs/drawings in KPTCL design office.  If the designs/drawings are commented by the owner, the contractor shall submit revised designs/drawings duly incorporating all comments within 15 (fifteen) days of date of issue of comments.

13.3 The contractor is required to furnish the progress of submissions and approvals of designs and drawings on twenty fifth day of every month till the completion of all the design activities.

13.4 The details shall include description of design/drawing, schedule date of submission, schedule date of approval, actual date of approval, schedule date of submission of distribution copies, actual date of submission of distribution copies, schedule date of pole test, actual date of pole test and “Remarks” column.  Provision of six additional columns shall also be made in the above progress report to indicate date of comments issued by the owner and details of revised design/drawings.

- TESTS:

14.1 PROTOTYPE POLE TESTING

The Pole structure designed and supplied by Contractor shall be proto type tested by Contractor at NABL accredited pole testing station in India only. The proto type pole structure after inspection by Purchaser shall be transported to the test bed by the Contractor. The Contractor shall also carryout erection of pole structure in vertical position in the pole testing station and after successful completion of proto-type testing, shall dismantle and take back.

Testing of Pole structure shall generally conform to IS: 802 (Part-III)/IEC-60652. The responsibility for design and successful proto type testing shall solely lie with the Contractor. At the time of proto-assembly and/or proto testing, if any modification is required to be carried out, the same shall be carried out by the Contractor. These modifications, if any, shall also be incorporated on the fabrication shop drawings and structural drawings.

A galvanized pole structure of each type complete with extension or critical poles (poles with maximum angle of deviation or with maximum extension or both) as decided by the Purchaser based on quantities of supply and site requirement shall be subjected to design and non-destructive tests by applying test loads in a manner approved by the Purchaser. The pole shall withstand these tests without showing any sign of failure or permanent distortion/deformation in any part and does not exceed the specified deflection limits.

  - TESTS FOR GALVANISATION:

Galvanization of the members of the tower shall withstand tests as ASTM A123.

- INSPECTION:

15.1	The supplier shall keep the purchaser informed well in advance of the commencement of manufacture, progress of manufacture thereof and fabrication of various tower parts at various stages, so that arrangements could be made for inspection by the purchaser.

15.2	The acceptance of any batch of items shall in no way relieve the supplier of any of his responsibilities for meeting all the requirements and intent of this specification and shall not prevent subsequent rejection if any item of that batch is later found defective.

15.3  The purchaser or his authorized representatives shall have free access at all   reasonable times to all parts of the supplier’s works connected with the fabrication of the material covered under the contract for satisfying themselves hat the fabrication is being done in accordance with the provisions of this specification.

15.4   Unless specified otherwise, inspection shall be made at the place of manufacture prior to dispatch and shall be conducted so as not to interfere unnecessarily with the operation of the work.

15.5   Should any member of the structure be found not to comply with the approved design, it shall be liable for rejection. No member once rejected shall be resubmitted for inspection, except in cases where the purchaser or his authorized representative considers that the defects can be rectified.

15.6	Defects which occur during fabrication shall be made good with the consent of and according to the procedure to be laid down by the purchaser.

15.7	All gauges and templates necessary to satisfy the purchaser for conducting tests shall be made available at the test site by the supplier.

15.8	The correct grade and quality of steel shall be used by the supplier. To ascertain the quality of steel, the purchaser may at his discretion get the material tested at an approved Laboratory.

15.9	The time frame for executing the work is also indicated in this schedule.  The supplier has to match the supply and delivery of base plate & anchor bolts, pole etc., to complete the work within the time schedule desired by the purchaser.

15.10	SCHEDULE OF PRICES:

The prices for design of tower, design of foundation, developing the structural and shop drawings, fabrication and galvanization of proto type pole, proto type testing of tower, etc., shall be furnished in the relevant   schedule.

- DESIGN PARTICULARS:

Pole design data and ceiling weights proposed to be used by the bidder shall be furnished in Schedule – Schedule of Guaranteed Technical Particulars given in Section DRS.

  - Design Loads.

The steel pole shall be designed to withstand the loading conditions shown on the loading tree provided by KPTCL. These loads are factored/ ultimate loads as given in the loading trees.

The specified wind load on the steel pole shown on the drawings shall be applied on full projected area of the pole. The wind load shall be applied throughout the exposed length of steel pole. The Contractor shall indicate on the design drawings the magnitude and the location of the wind forces assumed in the design.

  - Allowable Stresses.

The allowable stresses for tubular members, guys and connection bolts shall comply with the requirements of ASCE/SEI-48-11, Design of Steel Transmission Pole Structures.

- MATERIALS.

  - Pole Structure.

Steel grades having designated yield strength less than or equal to that of IS: 2062 grade E450 or equivalent are to be used in Pole structures, which includes pole shaft, cross arms & arm brackets, base plate etc. The quality of steel shall be BR/B0/C type as per IS 2062. Not more than three grades of steel shall be permitted for use. Steel plates below 6 mm size exclusively used for packing plates/packing washers produced as per IS: 1079 (Grade-HR0) are also acceptable.

Pole shall be continuously tapered from top to bottom with uniform slope. However, when required straight sections (without tapered) may be designed/used as extensions.

Steel grade of weldable quality only shall be selected. The grades of steel shall be selected to meet the design requirements & climatic conditions keeping in view the overall optimum weight of the pole structure and availability of material.

The sheets/plates of monopole shall be from primary steel producers such as TATA/SAIL/JSW/ RINL/ POSCO/ ArcelorMittal Nippon Steel India/ Jindal Steel/ only. If the sheets/plates cannot be directly procured from these sources, the same can be procured from dealer/distributors subject to condition that the original makers of the steel are aforementioned suppliers and same should be traceable. The manufacturer shall provide necessary documents for the same.

Quality Control Order issued by Ministry of Steel, as applicable, shall be followed.

  - Anchor Bolts.

Anchor bolts shall generally conform to IS: 5624. The size, grade & numbers of anchor bolts and its thread & nuts selection should be compatible with the required strength as per design. The anchor bolts for the pole shall be provided with top and bottom templates to form cage. This is to get a proper alignment of bolts during casting of foundation. Anchor bolts shall be completely galvanized.

  - Structural Plates

Plate and "product of a coil" that is used to produce load carrying components shall be considered structural plate. Material used for grounding plates, identification plates, pole caps, disposable cage plates and similar components does not need to be classified as structural plates.

Structural plate less than or equal to 31.75 mm (1.25 in.) in thickness shall conform to ASTM A36, ASTM A572, ASTM A 633 or ASTM A871.

Yield strength of Plates used for manufacturing the shafts shall be confirming to Gr 65 of ASTM A572. The silicon content of plates used for the pole shaft shall be limited to less than 0.06 % to have a better quality of Galvanising.

  - Fasteners: Bolts, Nuts and Washers:

All bolts and nuts shall conform to IS: 12427. All bolts and nuts shall be galvanized as per IS: 1367 (Part-XIII)/IS: 2629 and shall have hexagonal head and nuts, the heads being forged out of the solid steel rods & shall be truly concentric, and square with the shank, which must be perfectly straight.

The foundation bolts shall be of minimum 16 mm diameter and of property class 6.8/8.8 and the connection bolts shall be of minimum 12 mm and of property class 8.8 specified in IS: 1367(Part-III). Nuts of property class matching with the property class of mating bolt as specified in IS: 1367 (Part-VI) shall be used.

Bolts up to M16 and having length up to 10 times the diameter of the bolt should be manufactured by cold forging and thread rolling process to obtain in good & reliable mechanical properties and effective dimensional control. The shear strength of bolts shall be as per applicable standard. Bolts should be provided with washer in accordance with IS: 1363 (Part-I) to ensure proper bearing.

All bolts shall be threaded to take the full depth of the nuts and threaded enough to permit firm gripping of the members. It shall be ensured that the threaded portion of each bolt protrudes not less than 3 mm when fully tightened. All nuts shall fit and tight to the point where the shank of the bolt connects to the head.

To obviate bending stress in bolts or to reduce it to minimum, no bolt shall connect aggregate thickness of more than three (3) times its diameter.

Bolts at the joints shall be staggered so that nuts may be tightened with spanners without fouling.

Nuts should be double chamfered as per the requirement of IS:1363 Part- III. It should be ensured by the manufacturer that nuts should not be overlapped beyond 0.4 mm oversize on effective diameter of bolts. The nuts shall be forged and tapped after galvanizing and then lubricated.

The bolts and nuts shall be free from forging & threading defects such as cuts, splits, burrs, bulging, taper, eccentricity, loose fit etc.

Flat and tapered washers shall be provided wherever necessary.

Spring washers shall be provided for insertion under all nuts. These washers shall be of steel and shall be electro-galvanized, positive lock type and 3.5 mm in thickness for 16 mm dia. bolt and 4.5 mm for 24 mm bolt. In place of spring washer, double nut or lock nut may be provided with flat washer.

The surface of the washers shall be free of scales and burrs. The washers shall be coiled without any kinks (except for the shape with turned-up ends). The ends of the washer shall be so served as to prevent tangling.

The spring washers after coiling shall be suitably heat treated so as to result in the finished washer having hardness 43 to 50 HRC when tested in accordance with IS: 1586.

To ensure effective in-process Quality Control it is essential that the manufacturer have all the testing facilities for tests like weight of zinc coating, shear strength, other testing facilities etc. in-house. The manufacturer should also have proper Quality Assurance System which should be in line with the requirement of this specification and IS: 14000 series Quality System standard.

  - Weld Material.

The material used for making welds shall be compatible with the parent material, as defined by ANSI/AWS D1.1-92 and shall meet the impact requirements specified in 3.2.4 for the lowest toughness requirements of the plates being joined.

- DETAILING.

  - Typical Details.

Telescoping splices joining sections (slip joints) shall be designed to assure a minimum lap of 1.5 times the largest inside diameter of the outer section.

Anchor bolts shall be provided with top and bottom templates to form a cage at job site.

  - Circumferential welds.

Shaft-to-shaft, pole shaft-to-base plate, and pole shaft-to-flange shall be full penetration welds.

Arm shaft-to-arm bracket shall be partial penetration groove weld with fillet overlay, sized to develop the full strength of the shaft.

Other accessories (Iugs and plates for grounding, jacking, climbing and identification) shall be fillet and/or groove welds sized to develop the loading requirements of the attachment.

  - Longitudinal Welds.

Longitudinal welds in outer section of slip joints and within 76.2 mm (3") of a full penetration weld shall be full penetration.

Longitudinal welds shall be a minimum of 60% penetration in other locations.

  - Plate Bends.

The minimum inside radius of plate bends shall be such that cracking does not occur. Care must be taken to prevent the steel from cracking especially at the free ends of the bend either during the bending operation or subsequently due to residual stresses.

- FABRICATION.

  - General.

Fabrication shall be performed in strict compliance with KPTCL's approved shop detail drawings. Material substitution or deviations from the final approved drawings shall not be made without written approval from KPTCL.

The manufacturer shall accurately identify all material to assure proper usage.

  - Pole Shaft.

The pole shaft shall present the most pleasing appearance possible consistent with the strength requirements in the specification and drawings. Pole shall be continuously tapered from top to bottom with a uniform slope. No multi-ply steel plates will be allowed for the pole structure fabrication. Shaft shall be made with number of sections specified in the Standard Drawings.

The cross section of the pole shall be as specified in the Standard Drawings with all sides equal.

  - Pole Slip Joint.

Pole section shall be made with telescopic slip joints for easy assembly either in air or on the ground at the construction site. Overlapping shall not be less than 1.5 times the largest inside diameter of the female section.

The taper of each section at a slip joint should match the taper of the adjacent section to provide proper splice tolerances. No circumferential weld within a shaft section shall be permitted. Other type of connection will not be permitted.

  - Insulator String, Ground String and Guying Assembly.

Insulator string, ground string and guying assembly attach to the pole shaft shall be provided and shall refer to the General Design for different type of structures.

  - Cross Arms.

Cross-arm shall be furnished with hoisting lugs to facilitate line construction and maintenance.

- Other pole attachments.

  - ANTI-CLIMBING DEVICES:

Spikes type anti-climbing device shall be provided at 3 meters level from the ground.

  - CAUTION PLATES, NUMBER PLATES, CIRCUIT PLATES AND BIRD GUARDS:

Each pole will be fitted with Number Plates, Caution Plates (Danger Boards), Circuit plates and phase plates. These will be provided at appropriate level from the ground level (about 2.5 m to 3.5 m from ground level) so that the man standing at the foot at ground level will be able to clearly identify the same.

Suitable provision shall be made in the pole for fixing the above plates.

  - EARTH BONDS:

Suitable arrangements for fixing flexible copper bonds shall be made in the pole at the ground wire peak. Flexible copper bonds of 300mm and 450mm lengths are adopted in suspension and anchor poles respectively.

  - EARTHING:

Suitable provision shall be made in pole for fixing the pipe type /counter poise earthing, which will be done in accordance with clauses 11.0 and sub-clauses there of as per IS:5613-Part-2/Sec-2, corresponding to figure 6 and where the desired tower footing resistance cannot be achieved, then it shall be by counter poise earthing corresponding to fig-9 in the said IS.

  - Climbing Devise (Ladder & Step bolts)

Each pole shall be provided with the climbing devices such as ladder where maintenance personnel can climb on the pole face. The ladder shall be approximately 2.5m above ground level and up to the pole cross-arm and from there on to the ground wire peak.

Ladder shall have suitable proven connection to the pole considering the safety of the maintenance personal.

The step bolts, if provided, shall conform to IS: 10238 and shall be of not less than 16 mm diameter & 175 mm long and spaced not more than 450 mm apart. The head diameter shall be 35mm. The step bolt shall be fixed on two sides of polygon of the pole structure in alternate step arrangement. Each step bolt shall be provided with two hexagon nuts on one end to fasten the bolt securely to the pole and button head at the other end to prevent the feet from slipping away. The step bolts shall be capable of withstanding a vertical load not less than 1.5 kN.

  - MATERIAL PREPARATION.

The Pole Structure along with cross arms, earthwire peaks, base plate and joints shall be fabricated by the Contractor as per the design developed by the Contractor and approved by the Purchaser/Consultant.

The fabrication of Pole structure shall be in conformity with the following:

Except where hereinafter modified, details of fabrication shall conform to good industry practices and relevant standards.

Connections by means of slip joints or flange joints are both acceptable on mutual agreement as per the site requirements and conditions. Joints shall be so designed and fabricated that eccentricity is avoided as far as possible.

Pole section, if made with telescopic slip joints, shall be suitable for easy assembly either in air or on the ground at the construction site. Overlapping shall not be less than 1.5 times the largest inside diameter of the female section. The taper of each section at a slip joint should match the taper of the adjacent section.

On slip joints, diameter of the inner and outer part of the pole structure shall be controlled to ensure smooth assembly of the monopole structure.

In case of flange joints, the flanges welded to pole sections will be joined with Bolts & Nuts.

The cross arms shall be connected to the monopole by means of suitable flanges welded on the body and cross arms.

The Pole structures shall be accurately fabricated to connect together easily at site without any undue strain on the structure.

The diameter of the hole for bolts shall be equal to the diameter of bolt plus 1.5 mm.

The structure shall be designed so that all parts shall be accessible for inspection and cleaning. Drain holes shall be provided at all points where pockets of depression are likely to hold water. The top end of the pole, earth-wire peaks and cross arms shall be suitably sealed with cover plate bolted to the structure.

Maximum size of individual fabricated/welded piece shall be so selected to facilitate easy handling transportation and erection of pole structure. Any other specific restriction on length due to site condition should be specified by the Purchaser beforehand. The limits of weights & dimensions of individual components shall be finalized at the time of design development and approval.

All similar parts shall be made strictly inter-changeable. All steel sections before any work is done on them, shall be carefully leveled, straightened and made true to detailed drawings by methods which will not injure the materials so that when assembled, the adjacent matching surfaces are in close contact throughout.

In case of restriction due to size of hot dip galvanizing bath, pole segments shall be fabricated & galvanized as per following table and shall be seamlessly welded.

| Sl. No. | Outer Diameter of pole segment (in mm) | Max. permissible no. of fabricated parts per pole segment |
| --- | --- | --- |
| 1 | Up to 600 | 1 |
| 2 | 600≤ D<1200 | 2 |
| 3 | 1200≤D<1800 | 3 |
| 4 | 1800≤D | 4 |

No sharp/rough edges shall be permitted in the entire structure.

Suitable provisions shall be kept in design and detailing of pole structure for easy erection at site using conventional as well as mechanized methods. Detailed erection procedure/manuals shall be prepared and submitted by the Contractor.

Design and detailing for providing ladders/step bolts/hooks etc. shall be done so that such provision would facilitate accessibility to all parts of pole structures and installation & maintenance of insulators, hardware assemblies, conductors etc. can be done easily. Design detailing for provision of other accessories viz. Anticlimbing device, Danger plate, Number plate, Phase plate etc. shall also be done.

At base plate and other intermediate flange connections the plate shall be perfectly levelled to ensure uniform and gap free connection.

Lifting and handling of monopole during galvanization, fabrication etc. shall be done in such a way that each panel of monopole is perfectly straight. Also, spider bracings may be used inside the pole to arrest distortion or bending during handling.

Material Cutting, Forming & Bending:

The required material cutting, forming and bending operations shall be carried out generally in accordance with ASCE standard 48-19 (or subsequent revision) "Design of Steel transmission Pole Structures".

Before any cutting work is started, all steel shall be carefully straightened & trued by pressure and not by hammering. They shall again be trued after cutting & welding etc.

Drilling and Punching

Holes for bolts shall be drilled or punched with a jig or made with plasma/gas but drilled holes shall be preferred.

Holes must be perfectly circular and no tolerance in this aspect is permissible.

The maximum allowable difference in diameter of the holes on the two sides of plates or angle is 0.8 mm, i.e., the allowable taper in a punched hole should not exceed 0.8 mm on diameter (Not applicable for template holes and lifting holes).

Holes must be square with the plates and have their walls parallel.

All burrs left by drills or punch shall be removed completely. When the pole members are in position the holes shall be truly opposite to each other. Drilling or reaming to enlarge holes shall not be permitted.

When hot bending is required, heating shall be done evenly over the entire bend area and shall be of sufficient temperature to minimize separation and necking down of the cross section. The temperature used in hot bending shall be such that the physical properties of the steel are not diminished.

  - WELDING.

Welding being the key process of pole manufacturing, the manufacturer should have ISO 3834-2 certification for quality of welding.

All welding shall be in accordance with the latest revision of American Welding Society Structural Welding Code (ANSI/AWS D1.1). Welding terms and symbols should comply with the AWS definitions and symbols.

Care should be exercised with respect to welding procedures, qualification of welders/operators, electrodes, preheat, notch toughness and minimum yield of the electrodes to ensure conformance with the requirements of the ANSI/AWS D 1.1 code. Preheating shall be done according to the ANSI/AWS code or the steel producer’s recommendations, or both. The welding shall be done by the shield metal-arc, gas shielded flux core, gas shield metal arc or submerged-arc processes. The storage of welding consumables (welding wire, electrodes, fluxes and gases) shall be in accordance with AWS D1.1 and as per manufacturer’s recommendations. These details shall be included in MQP (Manufacturing Quality Plan) to be prepared and submitted by the Contractor.

Circumferential and longitudinal welds within the slip joint area of pole sections should be ultrasonically inspected in accordance with AWS D1.1. Longitudinal welds in pole sections where visual inspection is not adequate, magnetic particle tests or dye penetration test should be conducted in accordance with AWS D1.1.

Pole shaft-to-base plate and pole shaft-to-flange shall be full penetration welds. Arm shaft-to-arm bracket shall be partial penetration groove weld with fillet overlay, sized to develop the full strength of the shaft. Longitudinal seam welding of pole shaft (not in slip joint area) shall be partial penetration (min. 60%) from outer side.

Warping of base plate due to exposure to extreme heat during welding shall be avoided.

- SURFACE PREPARATION AND COATING.

  - Galvanising:

The pole manufacturer has to submit in writing the suitability of its galvanizing facility/bath where the pole sections are to be galvanized.

Fully galvanized poles structures and anchor plate excluding template shall be used for the transmission lines. Galvanizing of the pole structure shall conform to IS: 2629 and IS: 4759. All galvanized members shall withstand tests as per IS: 2633. For fasteners, the galvanizing shall conform to IS: 1367 (Part-13). Spring washers shall be electro-galvanized as per service grade 4 of IS: 1573.

The galvanizing shall be done after all fabrication work is completed, except that the nuts may be tapped or re-run after galvanizing. Threads of bolts and nuts shall have a neat fit and shall be such that they can be turned with finger throughout the length of threads of bolts and they shall be capable of developing full strength of the bolts.

All fabrication work on pole sections (including welding of base section with base plate) shall be completed in all respect before hot dip galvanization. No cutting, grinding, welding, fabrication etc. shall be allowed on any pole sections after hot dip galvanization is over except sections that will use metallizing.

The zinc coating shall be adherent, reasonably uniform, smooth, continuous and free from imperfections such as black/bare spots, ash rust strains, bulky white deposits/wet storage strains and blisters.

The fabricated pole structure parts shall have a minimum overall mass of Zinc coating and average zinc coating thickness as given below:

|  | Minimum mass of zinc coating (g/m2) | Average coating thickness of zinc coating (micron |
| --- | --- | --- |
| For plates and sections below 5 mm | 460 | 65 |
| For plates and sections of 5 mm and above | 610 | 87 |

For installation in coastal areas (upto 20 km from sea coast), the fabricated pole parts shall have a minimum overall mass of Zinc coating and average zinc coating thickness as given below:

|  | Minimum mass of zinc coating (g/m2) | Average coating thickness of zinc coating (micron |
| --- | --- | --- |
| For plates and sections below 5 mm | 610 | 87 |
| For plates and sections of 5 mm and above | 900 | 127 |

All fabrication work on pole sections (including base section with base plate) shall be complete in all respects before hot dip galvanizing. No cutting or welding shall be allowed on any of the sections after hot dipped galvanizing.

Hot dipping shall be done with single dipping method. Cold galvanizing methods will not be accepted.

Bolts, nuts and washers shall be galvanized in accordance with ASTM A 153. Bolts and nuts shall be assembled after galvanizing and shall fit with finger pressure only and nuts shall be interchangeable on any bolts without shake. Wrench tightness or spinning fit shall be caused for rejection.

Only the exposed threaded portion shall be galvanised in case of foundation Anchor bolts.

Repair of damaged hot dip galvanized surfaces during shipping or handling shall be in accordance with ASTM A780.

Heavy runs or lumps of excess zinc will not be acceptable in any area where they will interfere with bolt hole alignment (such as the "drip end" of punched angle braces, etc.), with matching flat surfaces which are to be bolted together, or are of such size and location that normal handling or erection may cause them to be dislodged. Sharp, pointed, "stickers" of zinc which could cause injuries in handling shall be removed.

Straightening of steel after galvanizing shall be accomplished without the use of heat. Steel so straightened shall be inspected to assure no deformation or cracking of galvanizing layer.

AII materials shall be cleaned or washed after galvanizing to remove traces of flux, flux inclusions, preflux slats, acid ash, dross or other extraneous materials. The presence of wet storage stain (White Rust) shall be caused for rejection.

  - PREPARATION FOR SHIPPING AND STORAGE.

Each shipment shall include a detailed packing list identifying all items by part number, including hardware. Special care shall be exercised in the handling, packaging and shipping of the materials to prevent denting, bending, or any other damage of the sections, cross arms and anchor bolt cages. Suitable cushioning, protective padding, dunnage or non-metallic spacers shall be used to prevent vangs and flanges welded to the tubular sections from damaging other tubular parts and to prevent damage and shifting during transit.

Small parts and fasteners shall be carefully boxed, crated, bagged or otherwise containerized and protected for shipment. Small pieces shall be bundled, with all the pieces in any bundle having the same mark. AII small pieces such as bolts, ground wire and insulator connections shall be packed in boxes of not over 150 pound gross weight each. Bolts of different size or length shall be wrapped in separate sacks before boxing. Description, quantity and marks or description of contents shall be shown on the outside.

Shipping shall be as specified in the Purchase Order and shall be in complete structure lots. AII identifications shown on bundles, boxes or other containers shall be included on Contractor's shipping and packaging lists.

All Materials shall be arranged to allow safe unloading at site.

Shop painted or galvanized steel will be stored in the field pending erection. Contractor shall provide storage and handling instructions to minimize damage to painted or galvanized surfaces.

  - MARKING.

AII parts of poles shall be appropriately marked or numbered. AII markings shall be indelible and clearly visible after galvanizing. Each pole shaft shall have a welded identification tag at 1.5m above ground level, which includes customer name, structure type, manufacturer name, year and month of fabrication. Each pole shaft section, cross arm and other separate pieces of structure shall have a welded identification tag marked with part number and serial number. All letters and numbers on identification tags shall have a minimum height of 15mm and be legible after galvanizing.

  - INSTALLATION.

When the installation and erection is by the Contractor such as for turnkey contracts, complete details of installation and erection, proper handling, transport to various sites, storage and performance guarantees, etc. shall be furnished for KPTCL review and approval.

- TESTS.

  - GENERAL.

AII materials shall comply with test criteria, and KPTCL acceptance of the steel poles and its components shall not relieve the Contractor of his responsibility for meeting all the requirements of this specification.

The steel poles and its components shall be given the manufacturer's routine shop tests and quality conformance tests .These tests shall be witnessed by KPTCL or its representative as per the approved quality assurance plan approved by KPTCL. Tests results shall be submitted to KPTCL. No steel poles shall be shipped until released for shipment by KPTCL.

  - MATERIAL.

Contractor shall furnish six (6) copies of certified mill test reports covering chemical and mechanical properties of the structural steel. Stock material may be used with KPTCL concurrence where Contractor's stock can be satisfactorily identified with the specified ASTM specification.

Contractor shall furnish all shop test reports for KPTCL for their review and records.

  - QUALITY CONFORMANCE INSPECTION.

This is intended to eliminate defective materials and components of the steel poles. Each component shall be inspected for conformance to the fabrication drawings. This inspection shall include, but not limited to:

- Ultrasonic inspection of base plate more than 50mm thick prior to welding for laminations.

- Visual inspection of dimensions to assure that tolerances are met.

- Visual inspection of cut edges to ANSI/AWS D.1.1 criteria.

- visual inspection of bent surfaces for surface separations (supplemented by magnetic particle in questionable areas);

- visual inspection of bolt holes to assure that they are cylindrical, perpendicular, free of burrs and without torn or ragged edges;

- visual inspection of all welds to ANSIIAWS 01.1 Section 8 criteria;

- ultrasonic inspection of all full penetration welds

- ultrasonic inspection of shaft to base plate weld after galvanizing for base plate thicker than 50mm (maybe waived if routine audits show no history of defects);

- visual inspection of all structural partial penetration or fillet welds, in questionable area use magnetic particle inspection according to ANSI/AWS D1.1 Section 8 criteria;

- visual inspection of finish;

- Magnetic thickness measurement of finish coatings.

  - FULL SCALE TESTS.

For the specified pole type, the Contractor shall carry out a full-scale test after all manufacturing is finished but before galvanizing. Written report of full scale test shall be submitted to KPTCL to assure that the proper design and fabricating procedures have been used.

The pole shall be erected on a rigid foundation and the vertical axis through the centre of gravity shall not be out of plumb by more than two tenths percent (0.2%) of the height at any level.

The pole structure shall sustain the load including overloads. These loads shall be applied in increments in steps of 50%, 75%, 90%, 95% with waiting period of 2 minute & 100% with waiting period of five (5) minutes.

The Contractor shall submit for KPTCL for approval his proposed method and facilities of applying and measuring the loads on the structure. The load measuring devices with appropriate numbering shall be suitably calibrated prior to and following the test in accordance with the manufacturer's recommendation at the presence of KPTCL Structural Design Engineer Representative(s).

Structure deflections under load shall be measured by suitable procedure at points designated. Deflection readings shall be recorded for the "before- load" and "Load-off" conditions.

The Contractor shall submit, fifteen (15) days prior to the performance of the tests, his testing programs to KPTCL for review and approval. These shall include test procedures, diagrams or test arrangements showing the points of location and magnitude of the loads to be applied, the designated points for deflection measurements, etc.

The testing of pole shall be carried out in the presence of KPTCL Structural Design Engineer who shall conduct a visual check and evaluate all parts of the structure for sign of failure following the completion of each test.

After completion of test, the test structure can be considered failure if the structure experienced any of the following:

- After the loads have been removed, the pole structure does not return to its original position within reasonable tolerance;

- Failure (i.e. bending, yielding, breaking, etc.) of the material or weld is detected; and

- Test structure does not pass all physical and dimensional checks as required in the test specified in this specification.

Such a failure shall be corrected and tested at the Contractor's expense.

In case of no failure, tested poles can be used for installation in the line.

- TEST REPORTS.

The Contractor shall furnish six (6) copies of a test report in English Language and that shall include;

- The designation and description of the pole tested;

- The name "KPTCL";

- The name of the person or organization (responsible engineer) that specified the loading, electrical clearances, technical requirements and general arrangement of the prototype;

- The name of the Engineer of Record;

- The name of the Manufacturer;

- A brief description and the location of the test facilities;

- The names and affiliations of the test witnesses;

- The dates of each test load case;

- Design and detail drawings of the pole, including any changes made during the testing program;

- A rigging diagram with details of the points of attachment to the pole;

- Calibration records of the load-measuring devices;

- A loading diagram for each load case tested;

- A tabulation of deflections for each load case tested;

- In case of failure; Photographs of failure: Loads at the time of failure; a brief description of the failure; The remedial action taken; The dimension of the failed members; and Test coupon reports of failed members;

- Photographs of the overall testing arrangement and rigging;

- Air temperature, wind speed and direction, any precipitation and any other pertinent meteorological data;

- MiII test reports of poles used in the test report;

- Test result of the test coupons taken following the completion of test.

- DATA AND DOCUMENTATION REQUIREMENTS.

  - GENERAL

Contractor furnished data and information shall be the performance data, predicted performance, interface requirements and construction features of all Contractor's furnished steel poles and materials. The accuracy of such information and its compatibility with overall performance requirements specified by KPTCL are the sole responsibility of the Contractor.

AII information submitted as part of the Proposal Data will become part of contract data for successful bidder. Any deviation from such data requires KPTCL approval for such a deviation to be acceptable to KPTCL.

  - DATA TO BE SUBMITTED ALONG WITH THE PROPOSAL.

- Description and outline drawings of proposed poles including configuration, shapes, sizes and material thickness, materials and dimensions of all major components, anticipated deflections and representative connection details;

- Description of design calculations to be performed and buckling criteria to be used;

- Reference lists;

- Certified sample mill test reports

- Proposed time bar schedule to meet delivery, installation/erection date(s) of the steel poles and its components;

- ISO 9001 Certification;

- Tentative Quality Control procedures and qualifications, and non-destructive testing to be performed;

- Estimated weight of each type of poles;

- Detailed list of all exceptions and/or deviations taken by the Bidder to the requirements of this specification or, if none are taken, a statement indicating that no exceptions or deviations are taken by the Bidder.

- Details of equipment available with the manufacturer for making these poles.

- Dimensions of the hot dip galvanizing facility of the manufacturer shall also be provided to ensure their capacity. This will be major qualifying criteria.

  - DATA TO BE SUBMITTED AFTER AWARD OF CONTRACT.

- List of Drawings and schedules of submittals;

- List of Codes used;

- The final design calculations showing design assumptions, analysis, joint fixity, foundation fixity, eccentricities induced to structure deflections and assumptions and computations used to determine radius of gyration and other critical sections;

- Maximum moments, shears, axial loads and member section modules required and furnished for at least every 20 foot (6.09 m) length, and at ground level, joints, splices and other critical sections;

- Detailed assembly and fabrication drawings;

- Bill of materials and parts list for each type of poles;

- Weights of each section and components of each type of poles including summary of total weights for each type of poles;

- Test reports.

- Calculations of stresses at the ground level, attachment connections, and moment connections;

- Maximum horizontal and vertical deflection at top of pole, at shield wire and conductor attachments, and at cross arm joints.

- Detailed QA Program based on ISO 9001 ;

- Detailed Contract Schedule Activity for the steel poles;

- As-built shop/erection drawings as finally approved.

Erection drawings shall show only one (1) pole each with its component parts, and shall have an identification mark. The number and length of bolts, with spring type of washer, nuts and locknut required for the assembly shall be shown at each connection.

A complete list of material listing quantities of all material required for the structure or part structure shown, including bolts, nuts, locknuts, washers shall be shown on Contractor's shop detail drawings. The bill of material shall include the quantity of pieces required, mark number, description, size, length, weight and total weight of material shown on the drawing, and the reference drawing on which the member is detailed.

Shop detail drawings shall show each individual member's dimensions and tolerances, welding requirements, connections, identification mark, quantities, material designation, surface treatment, and a bill of material.

The Contractor shall furnish in the manner, number of copies and within the time set forth in the Contract.

FOUNDATIONS:

- GENERAL:

  - The caisen type foundation shall be provided for each location. The successful bidder shall decide and design the foundation for each location based on the availability of space and other aspects. The bidder shall inspect each location to access the condition and quote. Detailed engineering is in the scope of bidder.

  - Foundation includes supply of all materials such as Cement, Coarse aggregate (stone metal) and fine aggregates (sand) etc., and also reinforcement steel.  Rates quoted for foundations in the appropriate Section shall include all items of work related to supply of all materials, labour, mobilization and installation of boring equipment and installation of foundations such as form work, excavation and back filling, providing reinforcement, etc., complete.

- CLASSIFICATION OF FOUNDATIONS AND TYPE OF FOUNDATION DESIGN:

  - The foundation design shall depend upon the type of soil and its properties prevailing at each location.

  - VOID

  - Proposals for raft type or embedded type shall be submitted by the successful bidder based on detailed soil investigations and approval for the same shall be obtained from the purchaser.

- SOIL INVESTIGATION:

The successful bidder shall undertake soil investigation at EACH location, and the type of foundation shall be decided and designed to suit the soil conditions.

- LOADS ON FOUNDATIONS AND STABILITY ANALYSIS:

The foundation loads and the stability analysis for various foundation loads shall be done in accordance with IS or any other relevant National or/and international standards in practice.

- PROPERTIES OF CONCRETE AND REINFORCEMENT:

Cement concrete used for the foundations shall be of Design Mix.

All the properties of concrete regarding its strength under compression, tension, shear, punching and bending etc., as well as workmanship shall confirm to IS 456-1978. Suitable tests for steel/concrete shall be carried out as per relevant BIS codes.

  - Aggregate to be used in concrete shall conform to IS 383 – 1970.

  - Water to be used for mixing concrete shall be fresh, clean and free from oil, acids, alkalies, organic materials or other deleterious substances.  Potable water is generally preferred.

  - For detailing of reinforcement IS: 2502 and SP: 34 shall be followed.  TMT bars conforming to IS-1786-2008(Fe 500 grade) shall be used as reinforcement.  However, in specific areas, mild steel (Grade-I) conforming to IS: 432 can also be used. The successful bidder shall supply, fabricate and place reinforcement to shapes and dimensions as indicated or as required to carry out the intent of drawings and specifications.

- DESIGN OF FOUNDATIONS:

  - The properties of soil as per the soil test report shall be considered for the design of foundations.

  - The Mono pole shall be anchored to the foundation through a suitable steel base plate & anchor bolts of required numbers shall be provided as per design.

  - Normally poles should not be subjected to uplift.  If there is uplift, sufficient anchorage should be provided in the foundation against uplift.

  - VOID

  - Design calculation should show that foundation is safe against overturning, down thrust and uplift.

  - The foundations shall be designed in accordance with relevant IS.

- FACTOR OF SAFETY:

For the design of foundation, the ultimate loads from the Towers design (for over turning, Bearing and uplift) shall be multiplied by a “Over load factor” of 1.15.  The strength design shall be in limit state as per IS-456.

- UNIT RATES:

Void

*******

GUARANTEED TECHNICAL PERTICULARS – MONOPOLES:

- Weight of steel tubular pole including X-arms and base plate & anchor bolts.

| POLE TYPE | 2P3 |
| --- | --- |
| Normal |  |
| +3.0M Extn |  |
| +6.0M Extn |  |

- Name of the Designers of Poles

2. Name of the Fabricators of poles

- Maximum working stresses employed in Design:

1.	Tension on net section area					Kg/Sq.mm

- Compression on gross sectional area 			Kg/Sq.mm

- Outer diameter of the pole at top and bottom in M

- Thickness of the wall in mm

- Maximum length of each unit of pole in M.

- Type of joint adopted for connecting each unit.

- Other Particulars:

    - Standards according to which properties of sections have been adopted in designs.

    - Standards to which the quality of steel for the sections have been adopted in designs.

    - Standards to which galvanizing will conform.

    - Maximum percentage increase in tower weight due to galvanization.

    - Quantity of zinc required per metric ton of tower weight.

    - Sizes of bolts and bolts holes.

    - Standards to which bolts and nuts will conform.

    - Name of manufacturer of bolts and nuts.

NAME OF BIDDER---------------------------------

SIGNATURE OF BIDDER-------------------------

DESIGNATION--------------------------------------

AUTHORISED COMMON RUBBER

STAMP SEAL OF BIDDER.

DATE ---------------------