KARNATAKA NEERAVARI NIGAM LIMITED

(A Government of Karnataka Undertaking)

OFFICE OF THE EXECUTIVE ENGINNER

KNNL, No 5 Bhadra canal Division, Davanagere.

Email: eebcddvg@yahoo.co.in

DRAFT TENDER SCHEDULE

FOR THE WORK OF

## KOGALURU TANK FILLING SCHEME

“Survey, Investigation, design, Supply, Installation, Testing and Commissioning of Lift Irrigation system (Head Works consisting of Intake canal, Jack well cum pump house, Power supply including substations and Transmission lines, Rising Main including Thrust Block, Valve Chambers,  Delivery chamber, approach roads etc) to Filling up of Kogaluru percolation tank coming under minor irrigation department from Kogaluru tank in Channagiri Taluk Davanagere  District on Turn-key basis” (KNNL/2026-27/LI/WORK_INDENT4628)

OFFICE OF THE

Executive Engineer KNNL, No.5 BCD Division, Davanagere

Annexure IV

### GOVERNMENT OF KARNATAKA

KARNATAKA NEERAVARI NIGAM LIMITED

(A Government of Karnataka Undertaking)

EXECUTIVE ENGINNER

KNNL, No 5 Bhadra canal Division, Davanagere.

Email: : eebcddvg@yahoo.co.in

TENDER FOR THE WORK OF

##### KOGALURU TANK FILLING SCHEME

“Survey, Investigation, design, Supply, Installation, Testing and Commissioning of Lift Irrigation system (Head Works consisting of Intake canal, Jack well cum pump house, Power supply including substations and Transmission lines, Rising Main including Thrust Block, Valve Chambers,  Delivery chamber, approach roads  etc) to Filling up of Kogaluru percolation tank coming under minor irrigation department from Kogaluru tank in Channagiri Taluk Davanagere  District on Turn-key basis” (KNNL/2026-27/LI/WORK_INDENT4628)

Sl.

No.

TENDER REFERENCE	:	No. KNNL/-----/---/----/------/-----/----

- PERIOD	OF	DOWNLOADING	OF TENDER DOCUMENT

- LAST DATE FOR DOWNLOADING OF TENDER DOCUMENT

- DATE AND PLACE OF PRE BID MEETING

- LAST DATE FOR SUBMISSION OF QUERRIES / CLARIFICATIONS IF ANY

- LAST DATE AND TIME FOR RECEIPT OF E-TENDERS

- TIME AND DATE OF OPENING OF ELECTRONIC TENDER DOCUMENT ONE (TECHNICAL BID)

- DATE OF VERIFICATION OF ORIGINAL DOCUMENTS

- TIME AND DATE OF OPENING OF ELECTRONIC TENDER DOCUMENT TWO (FINANCIAL BID)

:	Can be downloaded from E- Portal from: ---/--/---

-

:	---/--/---- upto --------

:	---/--/---- , -----------

:	---/--/---- , ------------

:	---/--/---- , ------------

---/--/---- , ------------

:	---/--/---- To ---/--/	, during office hours.

:	Will be intimated to the Qualified Tenderers

- PLACE OF OPENING OF ELECTRONIC TENDER DOCUMENT TWO (FINANCIAL BID)

:	Will be intimated to the Qualified Tenderers

- ADDRESS FOR COMMUNICATION	:	Office of  the Executive Engineer, KNNL,

No.5 BCD Division, Davanagere.

during officers hours

##### CONTENTS

| SECTION NO. | DESCRIPTION | PAGE No. |
| --- | --- | --- |
| 1. | INVITATION FOR TENDERS (IFT) | 4-18 |
| 2. | INSTRUCTIONS TO THE TENDERERS (ITT) | 19-35 |
| 3. | QUALIFICATION INFORMATION | 36-39 |
| 4. | FORM OF TENDER, LETTER OF ACCEPTANCE, NOTICE TO PROCEED WITH THE WORK AND AGREEMENT FORM | 40-44 |
| 5. | CONDITIONS OF CONTRACT (CC) | 45-99 |
| 6. | CONTRACT DATA | 100-142 |
| 7. | TECHNICAL SPECIFICATIONS | 143-520 |
| 8. | DRAWING | 521-521 |
| 9. | BILL OF QUANTITES (SCHEDULE –B) | 522-527 |
| 10. | FORMAT OF BANK GUARANTEE FOR SECURITY DEPOSIT | 528-528 |
| 11. | ANNEXURES | 529-601 |

SECTION 1 INVITATION FOR TENDERS (IFT)

### SECTION-1 INVITATION FOR TENDERS (IFT)

KARNATAKA NEERAVARI NIGAM LIMITED

(A Government of Karnataka Enterprises)

###### Office of the Executive Enginner, KNNL, No 5 Bhadra canal Division, Davanagere.

IFT No.: -	/	, Dated:

Through e –procurement

- The Executive Engineer, KNNL, KNNL, No 5 Bhadra canal Division, Davanagere..Invites Turnkey tenders on behalf of Managing Director, KNNL, Bengaluru, from eligible tenderers, for the construction of works detailed in the Table below. The tenderers may submit tenders for any or all of the works given in the Table. “Two Electronic Tender procedure as per Rule 28 of the KTPP Act shall be followed. The Tenderers are required to submit two separate sealed covers, one containing the Earnest money deposit and the details of their capability to undertake the tender (as detailed in ITT Clause 3 and 6), which will be opened first and the second cover containing the price tender which will be opened only if the Tenderer is found to be qualified to execute the tendered works. The Tenderers are advised to note the minimum qualification criteria specified in Clause 3 of the Instructions to Tenderers to qualify for award of the contract”.

- Tender documents may be downloaded from Government of Karnataka KPP Portal website https://kppp.karnataka.gov.in/under login for Contractors:

After login the Contractor has to, scroll down to the right-side bottom to see List of Tenders, click there to find the details of NIT and download copy of the tender. The tender can be downloaded in the portal as per

Prescribed date and time published in the portal. Only Interested Contractors who wish to participate should remit online transaction fee for tender after registering in the portal. The transaction fee is non-refundable.

- Tenders must be accompanied by earnest money deposit which will be paid online through e- Procurement portal as in Table below.

- Tenderers must submit Electronic Tender Documents One and Two electronically (on-line through internet) within the date and time published in e-procurement portal.

First Electronic Document (Technical Bid) shall contain the following qualification documents.

For individual Bidders

  - Copy of the valid KPWD Class II Registration Certificate

  - Copy of the valid Employees Provident Fund Registration Certificate along with latest paid challan copy.

  - Copy of the valid GST Certificate

  - Income tax returns of last 5 years.

  - The intending bidder/firm/company should furnish list of Man power, machinery available with them for taking up the work.

Second Electronic Document (Financial Bid) shall contain the following qualification documents.

- The tender (in the format indicated in section 4)

- Priced bill of quantities

First Electronic Tender (technical bid) will be opened at prescribed time and date in the e-procurement portal, in the presence of the Tenderers who wish to attend at the Office of the Executive Executive Engineer, KNNL, No 5 Bhadra canal Division, Davanagere.

Second Electronic Document (financial bid) will be opened only of those bidders who qualify in the technical bid. In case the lowest bidder fails to produce the original documents for entering into an agreement or the original documents submitted does not match with the uploaded documents or found false, then his bid is treated as non-responsive bid as per clause -26(4) of the KTPP rules and barred from participation in any of the tenders invited by the nigam apart from forfeiting the EMD paid through E-cash.

- A Pre-tender meeting will be held on --------date------at ----------Hrs. at the office of the Executive Engineer, KNNL, No 5 Bhadra canal Division, Davanagere, to clarify the issues if any, and to answer questions on any matter that may be raised at that stage as stated in Clause 8.2 of ‘Instructions to Tenderers’ of the tender document. The Contractor may seek clarification through e-procurement portal or through email to tender inviting authorities. The clarification will be published in the e- Procurement portal by uploading the clarifications.

- Other details can be seen in the tender documents.

| Sl. No. | Name of Work | Approximate amount put to tender (Rs. In lakhs) |  |  | EMD (Rs in Lakhs) | Tender Processing Fee (Non refundable) | Stipulated period for Completio n | Category of Contracto r Eligible |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Part-A Work portion | Part-B GST | Total |  |  |  |  |
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 |
| 1 | “Survey, Investigation, design, Supply, Installation, Testing and Commissioning of Lift Irrigation system (Head Works consisting of Intake canal, Jack well cum pump house, Power supply including substations and Transmission lines, Rising Main including Thrust Block, Valve Chambers, Delivery chamber, approach roads etc) to Filling up of Kogaluru percolation tank coming under minor irrigation department from Kogaluru tank in Channagiri Taluk Davanagere District on Turn-key basis” | 400.83 | 72.15 | 472.98 | 6.02 | As specified in the e- procurement portal | 11 Months (including Monsoon) | KPWD Class-2 & above registrati on |

Any details/information can be had from the web site https://kppp.karnataka.gov.in/

The detailed tender notification is as under

Note:

- The amount put to tender consist of the following.

- Turn Key Amount excluding GST: Rs. 400.83 Lakhs. The bidder should quote for this amount.

- GST Amount Rs. 72.15 Lakhs.

- Total Amount: Rs. 472.98 Lakhs.

Quoted amount is exclusive of all deposits and supervision charges of ESCOMS, Land Acquisition cost & SH & NH Crossing. The amount will be paid by the Nigam.

- Instructions to Bidders

The bids should submitted in two covers

  - FIRST ELECTRONIC DOCUMENT (TECHNICAL BID) SHALL CONTAIN THE FOLLOWING QUALIFYING DOCUMENTS:-

    - A copy of the Karnataka PWD Class –II &  Above Registration Certificate.

    - Copy of Valid Employees Provident Fund Registration Certificate.

    - Copy of Valid GST Registration Certificate

- The intending bidder/firm/company should furnish list of Man power, machinery available with them for taking up the work as per section 6.

- The details in support of qualification criteria as mentioned in para 4.0 below.

- Technical details containing document with preliminary designs, working  methodology in support of their bid as per the bidding document.

- Second Electronic Document shall contain financial Bid.

The First Electronic Document (Technical bid) will be opened first and thereafter Second Electronic Document (financial bid) will be opened only of those bidders who qualify in the technical bid. In case the lowest bidder fails to produce the original documents for entering into an agreement or the original documents submitted does not match with the uploaded documents or found false, then his bid is treated as non-responsive bid as per clause -26(4) of the KTPP rules & his name would be recommended for cancellation of registration in Karnataka PWD and barred from participation in any of the tenders invited by the KNNL apart from forfeiting the EMD paid through E-cash.

- Issue and submission of Tender Documents.

  - E-Procurement

    - The bidders can access and download blank tender document and submit their bidsthroughe- procurement from onward up to 4.00 PM in the E-procurement website https://kppp.karnataka.gov.in/ on payment (non-refundable) of such amount as prescribed in the e-procurement portal for the work towards transaction fee. The bidders can pay the transaction fee in the e-procurement portal using any of the following payment modes.

      - Credit cards

      - Direct debit

      - National electronic fund transfer (NEFT)

      - Over the counter (OTC) on or before up to 5.00 PM

    - The Pre–bid meeting will be held on 	at 11.00 AM in the office of the Executive Engineer, N0.5 Bhadra Canal Division, Davangere. The queries if any are to be sent not later than on by the intending bidders through e-mail to the Executive Engineer (the e-mail id for sending queries is eebcddvg@yahoo.co.in

    - Last Date & Time for tender queries / Clarifications is 	up to 05.30 PM

    - Last Date for Submission of completed e tendering documents is on 	up to 4.00 PM.

    - First Electronic Document (Technical BID) will be opened on 	 at 11.00 AM in the Presence of the Bidders who wish to participate.

    - Second Electronic Document (financial Bid) of the successful bidders who qualify in the technical bid will be opened after approval to the technical bid from the competent authority.

    - The necessary certificates/documents in support of pre-qualification criteria fulfilled as stipulated shall be scanned and attached to e-tender document. The scanned signature of the bidder /authorized representatives of the bidder shall be attached while uploading the bid document.

    - Further information about e-tendering can be had from https://kppp.karnataka.gov.in/

- Qualification Criteria:

  - To qualify for award of this contract, each tenderer in his / her name should have achieved. in the last five years (2021-22 to 2025-26) should have satisfactorily completed (at least 90% of contract value) as a prime contractor, at least One Lift Irrigation scheme/Tanks filling Scheme/Water Supply Scheme of value not less than Rs. 236.50 Lakhs. Work done certificate issued by an officer not below the rank of Executive Engineer of the concerned Division is to be uploaded for the technical bid. The cost of completed works of the previous year shall be given a weightage of 10% per year to bring it to the price level of financial year 2026-27 .

  - The annual turnover from all classes of civil engineering works should be costing not less than Rs.946.00 Lakhs, in any of the two financial years during the last five years (2021-22 to 2025-26). Audited profit and loss account certified by a practicing Chartered Accountant along with the copy of income tax returns filed for the years indicated above should be furnished. Duly mentioning UDIN on Turnover certificate (from CA). (The annual turnover of previous year shall be updated to the year of tender invitation at 10% per annum).

  - Liquid asset and/or availability of credit facilities of not less than Rs. 142.00 Lakhs for valid period upto Six Months (Unconditional credit lines/letters of credits/certificates from nationalized banks) for meeting the fund requirement etc. The contractor should upload necessary documents issued by the nationalized banks as per prescribed format enclosed as Annexure – XIV.

  - Each Tenderer should further demonstrate:

Availability by owning atleast 50% of the required / specified key and critical equipment for this work and (b) the remaining 50% can be deployed on lease / hire basis for all the works provided, the relevant documents (commitment agreements etc.) for availability for this work are furnished. The following key and critical equipment for the work. Modified as per G.O.No. FD 4 PCL 2008 dated 14/10/2008.

List of plant/machinery

| Sl No | Details of Machinery/Equipment | Total | Own | Hire/Lease |
| --- | --- | --- | --- | --- |
| 1. | Tippers | 6 | 3 | 3 |
| 2. | Excavators | 2 | 1 | 1 |
| 3. | JCB | 1 | 1 | - |
| 4. | DG set | 1 | - | 1 |
| 5. | Dewatering pumps | 3 | 1 | 2 |
| 6. | Mechanical Concrete mixer with hopper | 4 | 2 | 2 |
| 7. | Water tanker | 2 | 1 | 1 |

- The intending bidder should have supplied, erected, tested, completed and commissioned MS/HDPE/DI pipes of not less than 225 mm dia for a length of at least 3.85 km in any one year during the last five years i.e from the year 2021-22 to 2025-26. The necessary work done certificate issued by an officer not below the rank of Executive Engineer should be uploaded.

- The intending Bidder should have executed in any one year, the following minimum quantities of work during the last 5 years (i.e., from 2021-22 to 2025-26. The necessary work done certificate issued by an officer not below the rank of Executive Engineer should be uploaded.

| Sl. No. | Item | Quantity |
| --- | --- | --- |
| 1) | Earthwork Excavation | 4350.00 Cum |
| 2) | Reinforced Cement Concrete (M-15 Grade and above) | 310.00 Cum |
| 3) | Reinforcement steel bars for RCC works | 30.00 MT |
| 4) | Design Supplying, Erection and Commissioning of Pumps and motors of Min Capacity of 40 HP & above | 2 Nos |

  - BID CAPACITY

Tenderers who meet the above specified minimum qualifying criteria, will only be qualified, if their available tender capacity is more than the total tender value. The available tender capacity will be calculated as under:

Assessed available tender capacity = (A*N*1.5 - B)

Where;

A =Maximum value of civil engineering works executed in any one year during the last five years (2021-22 to 2025-26 ) (updated to 2026-27 price level) taking into account the completed as well as works in progress.

N =Number of years prescribed for completion of the works for which tenders are invited.

B = Value, at 2025-26 price level, of existing commitments and on-going works to be completed during the next (11/12) (period of completion of the works for which Tenders are invited) *

“If a bidder participates in more than one bid and technically qualifies and subsequently becomes

lowest in more number of bids than his/her bid capacity, then the tenderer can give his option to select the works based on his/her preference equivalent to his bid capacity. Further for the balance bids next lowest bidders will be eligible to accept at lowest bidders rates equivalent ot their bid capacity provided if the competent authority accepts it.”

In case first lowest bidder doesn’t come forward to conclude agreement and execute the work within the stipulated period the next lowest bidders will be offered to execute at the first lowest bidders rate if the competent authority desires it.

Note:  The statements showing the value of existing commitments and on-going works as well as the stipulated period of completion remaining for each of the works listed should be countersigned by the the Employer in charge, not below the rank of an Executive Engineer or equivalent.

  - General Conditions:

  - The bid shall be technically evaluated based on the specifications indicated in Section-3 titled

“Qualification information” in bid document.

  - The Bidder/JV partner/ Tie up partner shall not be under Corporate Debt Restructuring (CDR) / Strategic Debt Restructuring (SDR) or Bureau of Industrial and Financial Reconstruction (BIFR) in the last 5 Years prior to bid submission date. In this regard, the Bidder shall submit along with Bid, a certificate from their Statutory Auditor with a declaration that, the Bidder is not under CDR / SDR or BIFR.

  - Bids not satisfying minimum duty point parameters, efficiency parameters of pumps and motors and velocity parameters as specified in bid document shall be rejected.

  - During technical evaluation, if the employer finds that any certificates / information furnished is false, such bidders will be disqualified and barred from participation in the bid.

  - If any bidder fails to satisfy the conditions mentioned above, such bids will be rejected and their financial bids will not be opened.

  - The bidder should enclose the detailed methodology of execution of the scheme as per the scope of work.

  - The Bidder shall be responsible for successful performance of the contract

  - For construction of Transmission line/Substation Works, the contractor shall engage only those agencies who are licensed to do the power line construction works in Karnataka. They should have constructed at least one similar single power line equal to 80% of the length of power line for the work tendered in a single contract. The details of the transmission line construction contractor with registration certificate and certificates of experience signed by an officer of not below the rank of Executive Engineer of KPTCL shall be submitted for KNNL’s verification post award of the work.

  - The Bidder to participate in the tender under single bid basis only. Any violation will attract disqualification of the bid.

  - The pump manufacturer shall not enter into Tie-up with more than one bidder.

  - The contractor/authorized signatory should attach his/her scanned signature to the Schedule-B before uploading and also submitting their tenders.

  - If any of the dates mentioned above happen to be a general holiday, the next working day holds good.

  - The work of the construction of transmission line should be got done through a Government Licensed, Super Grade Electrical contractor CEIG approved, who have the experience of carrying out such works.

  - Further information can be had from the office mail ID eebcddvg@yahoo.co.in

  - Conditional tenders are liable to be rejected. The officer competent to accept the tender shall have the right to reject any or all the tenders without assigning any reason whatsoever.

  - Corrigendum will be published in the web site/ newspapers of all modifications /corrections if any.

  - The intending bidders should note that, if any of lands either in part/ parts or in whole required for the work is not acquired by the Nigam, it shall be the responsibility of the bidder to take the possession of such land and start the work by obtaining consent of the land owners before commencement of work at no extra cost to the Nigam and no claim / delays whatsoever relating to on account of non-availability of land would be entertained.

  - The intending bidders should note that, if any of the land either in part/parts or in whole required from the work is not yet acquired by the Nigama, it shall be the responsibility of the bidder to take possession of the such land and start the work by consent of the land owners before commencement of work at no extra cost to the nigama and no claim what so ever relating to non- availability of land would be entertained. Further, Nigam shall co-operate in getting the required for the work by inisiating LAQ proposal as per Land Aquisision Act.Any delay in obtaining consent of the land owners shall not be considered for any additional compensation. In case of any obstruction from the land owner during the construction period or during the maintenance period, the contractor has to make his own arrangements to get the dispute settled and to bear the extra cost, if any, on that account.

  - If the percentage quoted by the contractor for the work is below ninety percent of the updated recast estimated amount put to tender, then the contractor shall furnish an “additional performance security” in the form of Bank Guarantee for an amount equivalent to the difference

between the cost as per quoted percentage and 90% of the updated cost put to tender. In case of

contractor quoting above 125% of updated cost put to tender, then the over and above 125% of the updated cost put to tender will be withheld during the progress of work. The additional performance will be released proportionately to the bill amount till the contractor achieves progress of the entire cost of the work as per agreement. The withheld amount in the later case will be released only after entire work contracted is fully completed and so certified by the Executive Engineer.(If BG submitted while issuing fresh BG or extending any existing BG, claim period of a minimum one year from the date of expiry of validity period of BG is to be specified invariably) OR as per standard bid document, whichever is applicable

  - They should abide by the directions of Government towards recovery of 1% (or as modified by the Government from time to time) Cess from the contractor’s bill under the provisions of building and other constructions worker welfare cess Act 1996.

  - The intending bidders are advised to visit the site of work, make themselves familiar with local situation about the availability of construction materials, work men, land required for construction activities, etc and shall upload along with bid with details of references for visit of different parts of the scheme in the form of photographs of site.

  - The contractor is responsible for any damages due to natural calamity the government or Nigam will not give any compensation for until the completion of maintenance period.

  - The intending bidder/firm/company are advised to visit the work site before submission of the tenders.

  - The contractor should mention their recent correct portal address & mail address in declaration forms.

  - The tender processing charges paid by the bidder/firm/company are not refundable even if the tender is cancelled.

  - All materials like steel, cement, MS pipe etc., required for successful completion of the above work should be procured by the contractor only. No supply of any materials shall be made by KNNL.

  - The bidder/firm/company shall send the authorization letter for their representation duly attesting their signature.

  - .The bidder/firm/company shall adhere to accepted execution plan submitted by him under any circumstances without linking to the pending payment of the work & also land acquisition problems if any.

  - Typographical errors if any will not be the ground for any claims by the bidder/firm/company.

  - The amount put to tender is exclusive of GST. GST will be paid to the tendered amount separately as per prevailing rates. The contractor shall quote the rates excluding GST.

  - The contractor shall also abide by the other conditions as laid down in Bid document.

  - ¤zÉÃð±ÀPÀgÀPÀbÉÃj, UÀtÂ ªÀÄvÀÄÛ ¨sÀÆ«eÁÕ£À E¯ÁSÉ, £ÀA.49, R¤d ¨sÀªÀ£À, ¨ÉAUÀ¼ÀÆgÀÄ-01 gÀªÀgÀ ¸ÀÄvÉÆÛÃ¯É ¢£ÁAPÀ: 07.11.2023gÀ C£ÀéAiÀÄ ¸ÀPÁðj PÁªÀÄUÁjUÀ¼À°è §¼ÀPÉ ªÀiÁqÀÄªÀ G¥ÀR¤dUÀ½UÉ UÀtÂ ªÀÄvÀÄÛ ¨sÀÆ«eÁÕ£ÀE¯ÁSÉ¬ÄAzÀUÀtÂUÀÄwÛUÉUÉ ªÀÄAdÆgÀÄ ªÀiÁqÀ¯ÁzÀ G¥À R¤dUÀtÂUÀÄwÛUÉzÁgÀjAzÀR¤dgÀªÁ£É ¥ÀgÀªÁ¤UÉ (MDP) UÀ¼À ¥ÀæwUÀ¼À£ÀÄß PÁªÀÄUÁjAiÀÄ ©°è£ÉÆA¢UÉ ®UÀwÛ¹ ¸À°è¸ÀvÀPÀÌzÀÄÝ.

  - Further information about tendering can be had from https://kppp.karnataka.gov.in/#/portal/portal-home and office of the undersigned during office hours.

  - Further corrigendum/modifications/corrections/addendum if any can be had from https://kppp.karnataka.gov.in/#/portal/portal-home

Executive Engineer, KNNL, No.5 BCD Division, Davanagere.

Copy submitted for kind information:

- Copy submitted to the Personal Secretary to Hon’able Irrigation Minister, Water Resources Department, VidhanaSoudha, Bangalore for kind information.

- Copy submitted to the Managing Director, KNNL, 4th Floor, Coffee Board building, No.1, Dr. B.R. AmbedkarVeedhi, Bangalore – 01 for kind information.

- Copy submitted to Chief Engineer, KNNL, UpperTunga Project Zone. Shivamoga, for kind information.

- Copy submitted to Superintending Engineer, KNNL, Bhadra Project Circle, B.R.P for kind information.

- Copy submitted to Chief Administrative Office/Chief accounts Officers, Karnataka Neeravari Nigam Limited, Central Office, Srinagara Circle, Vijaya Complex, Haliyala Road, Dharwad for kind information.

- Copy forwarded to the Executive Engineer, No.3 & No.4, Bhadra canal Division, Malebennur&Bhadravati, for information.

- Copy forwarded to the Assistant Executive Engineer, No-1,2, 3 & 4Bhadra canal Sub-Division, Davanagere, Thyavangi and Harihara for information and necessary action.

- M/s. Marketing Consultants & Agencies Ltd., Deputy Commissioner Office, District Administration Bhavana, Room No.38A, 2nd Floor, Karur Road, Davangere.  to publish the notification in any leading News Paper for information.

- Copy to Division Account Branch

- Notice Board

Executive Engineer

KNNL, No.5 BCD Division,  Davanagere

SECTION – 2 INSTRUCTIONS TO TENDERS (ITT)

#### Section 2: Instructions to Tenderers (ITT)

Table of Clauses

| Name of Clause | DESCRIPTION | Page No. |
| --- | --- | --- |
| A | General |  |
| 1 | Scope of Tender |  |
| 2 | Eligible Tenderers |  |
| 3 | Qualification of the Tenderer |  |
| 4 | One Tender per Tenderer |  |
| 5 | Cost of Tendering |  |
| 6 | Site Visit |  |
| B | Tender Documents |  |
| 7 | Content of Tender documents |  |
| 8 | Clarification of Tender Document |  |
| 9 | Amendment of Tender documents |  |
| C | Preparation of Tenders |  |
| 10 | Documents comprising the Tender |  |
| 11 | Tender prices |  |
| 12 | Tender validity |  |
| 13 | Earnest money deposit |  |
| 14 | Format and signing of Tender |  |
| D | Submission of Tenders |  |
| 15 | Sealing and marking of Tenders |  |
| 16 | Deadline for submission of Tenders |  |
| 17 | Late Tenders |  |
| 18 | Modification and Withdrawal of Tenders |  |
| E | Tender opening and evaluation |  |
| 19 | Opening of First Cover of all Tenders and evaluation to determine Qualified Tenderers |  |
| 20 | Opening of Second Cover Tenders of qualified Tenders and evaluation |  |
| 21 | Process to be confidential |  |
| 22 | Clarification of Tenders |  |
| 23 | Examination of Tenders and determination of responsiveness |  |
| 24 | Correction of errors |  |
| 25 | Evaluation and comparison of Tenders |  |
| E | Tender opening and evaluation |  |
| 26 | Award criteria |  |
| 27 | Employer’s right to accept any Tender and to reject any or all Tenders |  |
| 28 | Notification of award and signing of Agreement |  |
| 29 | Security deposit |  |
| 30 | Advance payment and Security |  |
| 31 | Corrupt or Fraudulent Practices |  |

#### General

###### Scope of Tender

  - The Executive Engineer, KNNL, No.5 BCD Division, Davanagere, (Referred to as Employer in these documents) invites tenders following Two Cover tender procedure, from eligible Tenderers, for the construction of works (as defined in these documents and referred to as "the works") detailed in the Table given in the Invitation for Tenders (IFT). The Tenderers may submit tenders for any or all of the works detailed in the table given in IFT.

###### Eligible Tenderers

  - Tenderers shall not be under a declaration of ineligibility for corrupt and fraudulent practices issued by the Government of Karnataka.

  - Tenders from joint ventures are not acceptable. “Deleted since the work involves civil, electromechanical and electrical works.

###### Qualification of the Tenderer

  - All Tenderers shall provide the requested information accurately and sufficient detail in Section 3 : Qualification information.

  - To qualify for award of this contract, each Tenderer in its name should have in the last five years i.e. From 2021-22, 2022-23, 2023-24, 2024-25 & 2025-26

  - To qualify for award of this contract, each tenderer in his / her name should have achieved. in the last five years (2021-22 to 2025-26) should have satisfactorily completed (at least 90% of contract value) as a prime contractor, at least One Lift Irrigation scheme/Water Supply Scheme of value not less than Rs. 236.60 Lakhs. Work done certificate issued by an officer not below the rank of Executive Engineer of the concerned Division is to be uploaded for the technical bid. The cost of completed works of the previous year shall be given a weightage of 10% per year to bring it to the price level of financial year 2026-27 .

  - The annual turnover from all classes of civil engineering works should be costing not less than Rs.946.40 Lakhs, in any of the two financial years during the last five years (2021-22 to 2025-26). Audited profit and loss account certified by a practicing Chartered Accountant along with the copy of income tax returns filed for the years indicated above should be furnished. Duly mentioning UDIN on Turnover certificate (from CA). (The annual turnover of previous year shall be updated to the year of tender invitation at 10% per annum).

  - Liquid asset and/or availability of credit facilities of not less than Rs. 142.00 Lakhs for valid period upto Six Months (Unconditional credit lines/letters of credits/certificates from nationalized banks) for meeting the fund requirement etc. The contractor should upload necessary documents issued by the nationalized banks as per prescribed format enclosed as Annexure – XIV.

  - Each Tenderer should further demonstrate:

Availability by owning atleast 50% of the required / specified key and critical equipment for this work and (b) the remaining 50% can be deployed on lease / hire basis for all the works provided, the relevant documents (commitment agreements etc.) for availability for this work are furnished. The following key and critical equipment for the work. Modified as per G.O.No. FD 4 PCL 2008 dated 14/10/2008.

List of plant/machinery

| Sl No | Details of Machinery/Equipment | Total | Own | Hire/Lease |
| --- | --- | --- | --- | --- |
| 1. | Tippers | 6 | 3 | 3 |
| 2. | Excavators | 2 | 1 | 1 |
| 3. | JCB | 1 | 1 | - |
| 4. | DG set | 1 | - | 1 |
| 5. | Dewatering pumps | 3 | 1 | 2 |
| 6. | Mechanical Concrete mixer with hopper | 4 | 2 | 2 |
| 7. | Water tanker | 2 | 1 | 1 |

  - The intending bidder should have supplied, erected, tested, completed and commissioned MS/HDPE/DI pipes of not less than 225 mm dia for a length of at least 3.85 km in any one year during the last five years i.e from the year 2021-22 to 2025-26. The necessary work done certificate issued by an officer not below the rank of Executive Engineer should be uploaded.

- The intending Bidder should have executed in any one year, the following minimum quantities of work during the last 5 years(i.e., from 2021-22 to 2025-26. The necessary work done certificate issued by an officer not below the rank of Executive Engineer should be uploaded.

| Sl. No. | Item | Quantity |
| --- | --- | --- |
| 1) | Earthwork Excavation | 4350.00 Cum |
| 2) | Reinforced Cement Concrete (M-15 Grade and above) | 310.00 Cum |
| 3) | Reinforcement steel bars for RCC works | 30.00 MT |
| 4) | Design Supplying, Erection and Commissioning of Pumps and motors of Min Capacity of 40 HP & above | 2 Nos |

  - To qualify for a package of contracts made up of this and other contracts for which tenders are invited in this IFT, the Tenderer must demonstrate having experience and resources to meet the aggregate of the qualifying criteria for the individual contracts.

  - Sub-contractors’ experience and resources shall not be taken into account in determining the Tenderer’s compliance with the qualifying criteria except to the extent stated in 3.2 (d) and (e) above. Deleted as per GO No. FD 4 PCL 2008 dated 14/10/2008.

  - Tenderers who meet the above specified minimum qualifying criteria, will only be qualified, if their available tender capacity is more than the total tender value. The available tender capacity will be calculated as under:

Assessed available tender capacity = (A*N*1.5 - B)

Where;

A =Maximum value of civil engineering works executed in any one year during the last five years (updated to 2026-27 price level) taking into account the completed as well as works in progress.

N =Number of years prescribed for completion of the works for which tenders are invited.

B = Value, at 2025-26 price level, of existing commitments and on-going works to be completed during the next two years (period of completion of the works for which Tenders are invited) *

“If a bidder participates in more than one bid and technically qualifies and subsequently becomes lowest in more number of bids than his/her bid capacity, then the tenderer can give his option to select the works based on his/her preference equivalent to his bid capacity. Further for the balance bids next lowest bidders will be eligible to accept at lowest bidders rates equivalent ot their bid capacity provided if the competent authority accepts it.”

Note:  The statements showing the value of existing commitments and on-going works as well as the stipulated period of completion remaining for each of the works listed should be countersigned by the the Employer in charge, not below the rank of an Executive Engineer or equivalent.

  - Even though the Tenderers meet the above criteria, they are subject to be disqualified if they have:

- made misleading or false representations in the forms, statements and attachments submitted in proof of the qualification requirements; and/or

- record of poor performance such as abandoning the works, not properly completing the contract, inordinate delays incompletion, litigation history, or financial failures etc.; and/or

- participated in the previous Tender for the same work and had quoted unreasonably high tender prices and could not furnish rational justification.

###### One Tender per Tenderer

  - Each tenderer shall submit only one tender for one package. A tenderer who submits or participates in more than one Tender (other than as a sub-contractor or in cases of alternatives that have been permitted or requested) will cause all the proposals with the Tenderer’s participation to be disqualified.

###### Cost of Tendering

  - The tenderer shall bear all costs associated with the preparation and submission of his tender, and the Employer will in no case be responsible and liable for those costs.

###### Site Visit

6.1.  The Tenderer at his own responsibility and risk is encouraged to visit and examine the Site of Works and its surroundings and obtain all information that may be necessary for preparing the Tender and entering into a contract for construction of the Works. The cost of visiting the Site shall be at the Tenderer's own expense.

#### Tender documents

###### Content of Tender Documents: Deleted Refer Page No.6 since this is electronic tender system

  - The set of tender documents shall have all the Sections given in Page 2:

  - Both the sets should be completed and returned with the tender.

###### Clarification of Tender Documents

  - A prospective tenderer requiring any clarification of the tender documents may notify the Employer in writing or by cable (hereinafter “cable” includes telex and facsimile) at the Employer’s address indicated in the invitation to tender. The Employer will respond to any request for clarification which he receives earlier than 15 days prior to the deadline for submission of tenders. Copies of the Employer’s response will be forwarded to all purchasers of the tender documents, including a description of the enquiry but without identifying its source.

  - Pre-Tender Meeting:

    - The tenderer or his authorized representative is invited to attend a pre-tender meeting which will take place at office of The Managing Director Karnataka Neeravari Nigama Limited, Bangalore.

    - The purpose of the meeting will be to clarify issues and to answer questions on any matter that may be raised at that stage.

    - The tenderer is requested to submit any questions online through query or in writing or by cable to reach the Employer not later than the date of pre-tender meeting.

    - Minutes of the meeting, including the text of the questions raised (without identifying the source of enquiry) and the responses given will be transmitted without delay to all purchasers of the tender documents. Any modification of the tender documents listed in Sub-Clause 7.1 which may become necessary as a result of the pre-tender meeting shall be made by the Employer exclusively through the issue of an Addendum pursuant to Clause 9 and not through the minutes of the pre-tender meeting.

    - Non-attendance at the pre-tender meeting will not be a cause for disqualification of a tenderer.

###### Amendment of Tender Documents

  - Before the deadline for submission of tenders, the Employer may modify the tender documents by issuing addenda.

  - Any addendum thus issued shall be part of the tender documents and shall be published online in procurement portal only and not through any paper publications.

  - To give prospective Tenderers reasonable time in which to take an addendum into account in preparing their tenders, the Employer shall extend as necessary the deadline for submission of tenders, in accordance with Sub-Clause 16.2 below.

#### Preparation of Tenders

###### Documents Comprising the Tender: Deleted. Refer Clause. No. 1 of Data Sheet.

  - The tender submitted by the Tenderer shall be in two covers and shall contain the documents as follows:

    - First Cover:

      - Earnest Money Deposit;

      - Qualification Information as per formats given in Section 3;

    - Second Cover:

      - The Tender (in the format indicated in Section 4)

      - Priced Bill of Quantities (Section 9);

and any other materials required to be completed and submitted by Tenderers in accordance with these instructions. The documents listed under Sections 3, 4, 6 and 9 shall be filled in without exception.

  - Tenderers submitting tenders together with other contracts stated in the IFT to form a package will so indicate in the tender together with any discounts offered for the award of more than one contract.

###### Tender Prices

  - The contract shall be for the whole works as described in Sub-Clause 1.1, based on the priced Bill of Quantities submitted by the Tenderer.

  - The Tenderer shall fill in rates and prices and line item total (both in figures and words) for all items of the Works described in the Bill of Quantities along with total tender price (both in figures and words). Items for which no rate or price is entered by the Tenderer will not be paid for by the Employer when executed and shall be deemed covered by the other rates and prices in the Bill of Quantities. Corrections, if any, shall be made by crossing out, initialing, dating and rewriting. Deleted since this is turnkey tender. Refer Clause No. 2 of Data Sheet.

  - All duties, taxes, and other levies payable by the contractor under the contract, or for any other cause, shall be included in the rates, prices and total Tender Price submitted by the Tenderer. Deleted since this is turnkey tender. Refer Clause No. 2 of Data Sheet.

  - The rates and prices quoted by the Tenderer shall be subject to adjustment during the performance of the Contract in accordance with the provisions of Clause of the Conditions of Contract.

###### Tender Validity: Deleted Refer Clause No. 3 of Data Sheet.

  - Tenders shall remain valid for a period not less than ninety days after the deadline date for tender submission specified in Clause 16. A tender valid for a shorter period shall be rejected by the Employer as non-responsive.

  - In exceptional circumstances, prior to expiry of the original time limit, the Employer may request that the Tenderers may extend the period of validity for a specified additional period. The request and the Tenderers' responses shall be made in writing or by cable. A Tenderer may refuse the request without forfeiting his earnest money deposit. A Tenderer agreeing to the request will not be required or permitted to modify his tender, but will be required to extend the validity of his earnest money deposit for a period of the extension, and in compliance with Clause 13 in all respects.

###### Earnest Money Deposit:

  - The tenderer shall furnish as part of his tender, Earnest Money Deposit (EMD) at the following rates. EMD amount as % of the estimated cost of the work put to tender. Modified as per G. O. No. FD 4 PCL 2008 dated 14/10/2008.

    - Upto 20 lakhs—2.5%

    - Rs. 20 lakhs and above upto Rs. 1 crore –2% subjected to a minimum of Rs. 50,000/-

    - Rs. 1 crore and above upto Rs. 10 crores—1.5% subjected to a minimum of Rs. 2,00,000/-

    - Rs. 10 crores and above – 1% subjected to a minimum of Rs. 15,00,000/-.

  - Instruments having fixed validity issued as earnest money deposit for the tender shall be valid for 45 days beyond the validity of the tender. Refer Clause No. 22 of Data Sheet.

  - Any tender not accompanied by an acceptable earnest money deposit and not secured as indicated in Sub-Clauses 13.1 and 13.2 above shall be rejected by the Employer as non-responsive.

  - The earnest money deposit of unsuccessful Tenderers will be returned within 30 days of the end of the tender validity period specified in Sub-Clause 12.1.

  - The earnest money deposit of the successful Tenderer will be discharged when the Tenderer has signed the Agreement and furnished the required Performance Security.

  - The earnest money deposit may be forfeited:

    - if the Tenderer withdraws the Tender after tender opening during the period of tender validity;

    - if the Tenderer does not accept the correction of the Tender Price, pursuant to Clause 24; or

    - In the case of a successful Tenderer, if the Tenderer fails within the specified time limit to

      - Sign the Agreement; or

      - Furnish the required Security deposit

###### Format and Signing of Tender: Deleted since this is electronic tendering system. Refer Clause No. 4 of Data Sheet.

  - The Tenderer shall prepare one original and a copy of the documents comprising the Tender as described in Clause 10 of these Instructions to Tenderers, and clearly marked "ORIGINAL" and "COPY" as appropriate. In the event of discrepancy between them, the original shall prevail.

  - The original and a copy of the Tender shall be typed or written in indelible ink and shall be signed by a person or persons duly authorized to sign on behalf of the Tenderer. All pages of the tender where entries or amendments have been made shall be initialed by the person signing the tender

  - The Tender shall contain no alterations or additions, except those to comply with instructions issued by the Employer, or as necessary to correct errors made by the Tenderer, in which case such corrections shall be initialed by the person signing the Tender.

#### Submission of Tenders

###### Sealing and Marking of Tenders: Deleted since this is electronic tendering system. Refer Clause No. 5 of Data Sheet.

  - The Tenderer shall seal the original and a copy of the Tender in separate envelopes, duly marking the envelopes as "ORIGINAL" and "COPY". These envelopes (called as inner envelopes) shall then be put inside one outer envelope.

  - The inner and outer envelopes shall

    - be addressed to the Employer at the following address:

...............................................................

................................................................

(insert address of office for Tender submission), and

    - bear the following identification:

      - Tender for 	[name of contract]

      - Tender Reference No.	[insert number]

      - DO NOT OPEN BEFORE.	[time and date for tender opening, per Clause 19]

  - In addition to the identification required in Sub-Clause 15.2, the inner envelopes shall indicate the name and address of the Tenderer to enable the tender to be returned unopened in case it is declared late, pursuant to Clause 17.

  - If the outer envelope is not sealed and marked as above, the Employer will assume no responsibility for the misplacement or premature opening of the Tender.

###### Deadline for Submission of the Tenders

  - Tenders must be received by the Employer at the address specified above no later than	In the event of the specified date for the submission of

tenders being declared a holiday for the Employer, the tenders will be received up to the appointed time on the next working day. Deleted since this is a electronic tendering system. Refer Clause No. 6 of Data Sheet.

  - The Employer may extend the deadline for submission of tenders by issuing an amendment in accordance with Clause 9, in which case all rights and obligations of the Employer and the Tenderers previously subject to the original deadline will then be subject to the new deadline.

###### Late Tenders: Deleted since this is a electronic tendering system. Refer Clause No. 7 of Data Sheet.

17.1. Any Tender received by the Employer after the deadline prescribed in Clause 16 will be returned unopened to the Tenderer.

###### Modification and Withdrawal of Tenders: Deleted since this is a electronic tendering system. Refer Clause No. 8 of Data Sheet.

  - Tenderers may modify contents of First or Second Covers separately for each Cover or withdraw their Tenders by giving notice in writing before the deadline prescribed in Clause 16.

  - Each Tenderer's modification separately for each Cover or withdrawal notice shall be prepared, sealed, marked, and delivered in accordance with Clause 14 & 15, with the outer and inner envelopes additionally marked "MODIFICATION FOR FIRST/SECOND COVER" or "WITHDRAWAL", as appropriate.

  - No Tender may be modified after the deadline for submission of Tenders.

  - Withdrawal or modification of a Tender between the deadline for submission of Tenders and the expiration of the original period of Tender validity specified in Clause

12.1 above or as extended pursuant to Clause 12.2 may result in the forfeiture of the earnest money deposit pursuant to Clause 13.

  - Tenderers may only offer discounts to, or otherwise modify the prices of their Tenders by submitting Tender modifications in accordance with this clause, or included in the original Tender submission.

#### Tender Opening and Evaluation

###### First Electronic Document (Technical Part) of all Tenders and Evaluation to Determine Qualified Tenderers

  - The Employer will open the First Electronic Document (Technical Bid) of all the Tenders received in the presence of the Tenderers or their representatives who choose to attend on the date and the place specified in the e-procurement in the tender for works. In the event of the specified date of Tender opening being declared a holiday for the Employer, the Tenders will be opened at the appointed time and location on the next working day.

  - Envelopes marked "WITHDRAWAL" shall be opened and read out first. The First Cover of Tenders for which an acceptable notice of withdrawal has been submitted pursuant to Clause 18 shall not be opened. Deleted

  - The Tenderes names, the presence or absence of earnest money deposit (amount, format and validity), the submission of qualification information and such other information as the Employer may consider appropriate will be announced by the Employer at the opening. Late and withdrawn Tenders will be returned unopened to tenders. Deleted

  - The Employer shall prepare minutes of the Tender opening, including the information disclosed to those present in accordance with Sub-Clause 19.3. Deleted

  - The Second Cover of all the Tenderers including modifications for Second Cover shall be placed in a large cover and securely sealed in the presence of the tenderers or their representatives, who are present and also get the same signed by all those tenderers or their representatives. The large cover shall be kept in safe custody by the Employer. Deleted

  - The Employer will evaluate and determine whether each tender (a) meets the eligibility criteria defined in ITT Clause 2; (b) is accompanied by the required earnest money deposit as per stipulations in ITT Clause and (c) meets the minimum qualification criteria stipulated in ITT Clause 3. The Employer will draw out a list of qualified Tenderers.

###### Opening of Second Cover of Qualified Tenderers and Evaluation

  - The Employer will open the second Electronic Document (Financial Bid) of Qualified Tenderers at the appointed time and date in the presence of the Tenderers or their representatives who choose to attend. In the event of the specified date of Second Electronic Document opening being declared a holiday for the Employer, the Second Electronic Document will be opened at the time and location on the next working day.

  - Envelopes marked “MODIFICATION FOR SECOND COVER” shall be opened and the submissions therein read out in appropriate detail. Deleted since this clause is not applicable.

  - The Tenderers' names, the Tender prices, the total amount of each Tender, any discounts, Tender modifications and withdrawals, and such other details as the Employer may consider appropriate, will be announced by the Employer at the opening. No Tender shall be rejected at Tender opening. Deleted since this clause is not applicable.

  - The Employer shall prepare minutes of the Second Cover Tender opening, including the information disclosed to those present in accordance with Sub-Clause 20.3. Deleted since the process is to be confidential as per Clause 21 below.

###### Process to be Confidential

21.1. Information relating to the examination, clarification, evaluation, and comparison of Tenders and recommendations for the award of a contract shall not be disclosed to Tenderers or any other persons not officially concerned with such process until the award to the successful Tenderer has been announced. Any effort by a Tenderer to influence the Employer's processing of Tenders or award decisions may result in the rejection of his Tender.

###### Clarification of Tenders

  - To assist in the examination, evaluation, and comparison of Tenders, the Employer may, at his discretion, ask any Tenderer for clarification of his Tender, including breakdowns of unit rates. The request for clarification and the response shall be in writing or by cable, but no change in the price or substance of the Tender shall be sought, offered, or permitted except as required to confirm the correction of arithmetic errors discovered by the Employer in the evaluation of the Tenders in accordance with Clause 24. Deleted Refer Clause No. 9 of Data Sheet.

  - Subject to sub-clause 22.1, no Tenderer shall contact the Employer on any matter relating to its Tender from the time of the Tender opening to the time the contract is awarded. If the Tenderer wishes to bring additional information to the notice of the Employer, it should do so in writing. Deleted Refer Clause No. 9 of Data Sheet.

  - Any effort by the Tenderer to influence the Employer in the Employer’s Tender evaluation, Tender comparison or contract award decisions may result in the rejection of the Tenderers’ Tender.

###### Examination of Tenders and Determination of Responsiveness

  - Prior to the detailed evaluation of Tenders, the Employer will determine whether each Tender; (a) has been properly signed; and; (b) is substantially responsive to the requirements of the Tender documents.

  - A substantially responsive Tender is one which conforms to all the terms, conditions, and specifications of the Tender documents, without material deviation or reservation. A material deviation or reservation is one (a) which affects in any substantial way the scope, quality, or performance of the Works; (b) which limits in any substantial way, inconsistent with the Tender documents, the Employer's rights or the Tenderer's obligations under the Contract; or (c) whose rectification would affect unfairly the competitive position of other Tenderers presenting substantially responsive Tenders.

  - If a Tender is not substantially responsive, it will be rejected by the Employer, and may not subsequently be made responsive by correction or withdrawal of the nonconforming deviation or reservation.

###### Correction of Errors: Deleted since this is electronic tender system.

  - Tenders determined to be substantially responsive will be checked by the Employer for any arithmetic errors. Errors will be corrected by the Employer as follows:

    - where there is a discrepancy between the rates in figures and in words, the lower of the two will govern17; and

    - where there is a discrepancy between the unit rate and the line item total resulting from multiplying the unit rate by the quantity, the unit rate as quoted will govern.

  - The amount stated in the Tender will be adjusted by the Employer in accordance with the above procedure for the correction of errors and, with the concurrence of the Tenderer, shall be considered as binding upon the Tenderer. If the Tenderer does not accept the corrected amount the Tender will be rejected, and the earnest money deposit may be forfeited in accordance with Sub-Clause 13.6 (b).

###### Evaluation and Comparison of Tenders

  - The Employer will evaluate and compare only the Tenders determined to be substantially responsive in accordance with Clause 23.

  - In evaluating the Tenders, the Employer will determine for each Tender the evaluated Tender Price by adjusting the Tender Price as follows: Deleted since this is electronic tendering system.

    - Making any correction for errors pursuant to Clause 24; and

    - Making appropriate adjustments to reflect discounts or other price modifications offered in accordance with Sub Clause 18.5.

  - The Employer reserves the right to accept or reject any variation, deviation, or alternative offer. Variations, deviations, and alternative offers and other factors which are in excess of the requirements of the Tender documents or otherwise result in unsolicited benefits for the Employer shall not be taken into account in Tender evaluation.

  - The estimated effect of the price adjustment conditions under Clause 41 of the Conditions of Contract, during the implementation of the Contract, will not be taken into account in tender Evaluation

  - If the tender of the successful tenderer is seriously unbalanced in relation to the Employer’s estimate of the cost of the work to be performed under the contract, the Employer may require the Tenderer to produce detailed price analyses for any or all items of the Bill of Quantities, to demonstrate the internal consistency of those prices with the construction methods and schedule proposed. After evaluation of the price analyses, the Employer may require that the amount of the performance security set forth in Clause 29 be increased at the expense of the successful Tenderer to a level sufficient to protect the Employer against financial loss in the event of default of the successful under the contract.

###### Award of Contract

- Award Criteria

26.1.  Subject to Clause 27, the Employer will award the Contract to the Tenderer whose Tender has been determined to be substantially responsive to the Tender documents and who has offered the lowest evaluated Tender Price, provided that such Tenderer has been determined to be (a) eligible in accordance with the provisions of Clause 2, and (b) qualified in accordance with the provisions of Clause 3.

###### Employer's Right to Accept any Tender and to Reject any or all Tenders

27.1. Notwithstanding Clause 26, the Employer reserves the right to accept or reject any Tender, and to cancel the Tender process and reject all Tenders, at any time prior to the award of Contract, without thereby incurring any liability to the affected Tenderer or Tenderers or any obligation to inform the affected Tenderer or Tenderers of the grounds for the Employer's action.

###### Notification of Award and Signing of Agreement

  - The Tenderer whose Tender has been accepted will be notified of the award by the Employer prior to expiration of the Tender validity period by cable, telex, e-mail or facsimile confirmed by registered letter. This letter (hereinafter and in the Conditions of Contract called the "Letter of Acceptance") will state the sum that the Employer will pay the Contractor in consideration of the execution, completion, and maintenance of the Works by the Contractor as prescribed by the Contract (hereinafter and in the Contract called the "Contract Price").

  - The notification of award will constitute the formation of the Contract, subject only to the furnishing of Security deposit in accordance with the provisions of Clause 29.

  - The Agreement will incorporate all agreements between the Employer and the successful Tenderer. It will be kept ready for signature of the successful Tenderer in the office of Employer within 30 days following the notification of award along with the Letter of Acceptance. Within 20 days of receipt, the successful Tenderer will sign the Agreement and deliver it to the Employer.

  - Upon the furnishing by the successful Tenderer of the Performance Security, the Employer will promptly notify the other Tenderers that their Tenders have been unsuccessful.

###### Security Deposit

29.1 Within 20 days of receipt of the Letter of Acceptance, the successful Tenderer shall deliver to the Employer a Security deposit in any of the forms given below for an amount equivalent to 5% of the Contract price plus additional security for unbalanced tenders (Difference between amount put to tender as per current CSR and quoted amount) shall be adopted as per  Government of Karnataka Order:DE: 456:ªÉZÀÑ: 12/ 2022/ ¨ÉAUÀ¼ÀÆgÀÄ ¢£ÁAPÀ; 10.08.2022 as specified below: -

Banker’s cheque/Demand draft,/Pay Order in favour of  theExecutive

Engineer, KNNL, No.5Bhadra canal  Division, Davanagere.

  - . Payable at. Davanagere.or

Irreovacble bank guarantee, including e-bank Guarantee, insurance surety Bonds issued

by Insurance company authorized by insurance Regulatory and Development Authorised

of India  in the form given in Section 10; orSpecified Small Savings Instruments pledged

to Executive Engineer, KNNL, No.5 Bhadra canal Division, Davanagere.

  - If the security deposit is provided by the successful Tenderer in the form of a Bank Guarantee, it shall be issued either by a Nationalized/Scheduled bank.

  - The security deposit if furnished in FDR or demand draft can, if requested, be converted to interest bearing securities at the cost of the contractor.

  - Failure of the successful Tenderer to comply with the requirements of Sub-Clause 29.1 shall constitute sufficient grounds for cancellation of the award and forfeiture of the Earnest money deposit.

###### Advance Payment and Security: “Deleted as per G.O. No. Ja Sam E 127 MBI 2020 dated: 30-05-2020”.

30.1.	The Employer will provide an advance payment on the contract price as stipulated in the Conditions of Contract, subject to the maximum amount as stated in the Contract Data.

###### Corrupt or Fraudulent Practices

  - The GOK requires that the Tenderers/Suppliers/Contractors, observe the highest standard of ethics during the procurement and execution of such contracts. In pursuance of this policy, GOK:

    - will reject a proposal for award if it determines that the Tenderer recommended for award has engaged in corrupt or fraudulent practices in competing for the contract in question;

    - will declare a firm ineligible, either indefinitely or for a stated period of time, to be awarded a GOK contract if it at any time determines that the firm has engaged in corrupt or fraudulent practices in competing for, or in executing, a GOK contract.

  - Furthermore, Tenderers shall be aware of the provision stated in sub-clause 50.2 of the Conditions of Contract.

SECTION 3 QUALIFICATION INFORMATION

The information to be filled in by the Tenderer hereunder will be used for purposes of computing Tender capacity as provided for in Clause 3 of the Instructions to Tenderers. This information will not be incorporated in the Contract.

  - Constitution or legal status of Tenderer	[Attach copy]

Place of Registration

Principal place of business:

  - Total value of civil engineering construction works executed and payments received in the last five years(in Rs. Lakhs) (attach certificate from chatered accountant)

(Attach Copy)

2021-22

2022 – 23

2023 – 24

2024 – 25

2025-26

Total value of civil engineering construction works executed and payments received in the preceding five years. (in Rs Lakhs )

  - Work performed as Prime Contractor (in the same name) on works of similar nature over during the five years specified in 1.2 above.

| Project Name | Name of Employ er | Descriptio n of Work | Contract Number | Value of contra ct Rs. Lakhs | Date of Issue of work order | Specified period of completi on | Actual date of completio n | Remarks explaining reasons for delay in completio n of work |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 |

  - Quantities of work executed as prime contractor (in the same name) during the preceding last five years specified in 1.2 above:

| Year | Name of Work | Name of Employ er | Quantity of Work Performed |  |  |  |  |  | Remarks (Indicate contract reference) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | Earthwork (Excavatio n & embankme nt) | Cement Concret e | Reinforce ment Steel | Providing and laying M.S. rising main | Pumps and motors | Transmissi on line |  |
| 2021- 2022 |  |  |  |  |  |  |  |  |  |
| 2022- 2023 |  |  |  |  |  |  |  |  |  |
| 2023- 2024 |  |  |  |  |  |  |  |  |  |
| 2024- 2025 |  |  |  |  |  |  |  |  |  |
| 2025- 2026 |  |  |  |  |  |  |  |  |  |

  - Information on works for which Tenders have been submitted and works which are yet to be completed as on the date of this Tender.

- Existing commitments and on-going works:

| Description of Work | Place & State | Contract No. & Date | Name and Address of Employer | Value of Contract (Rs. lakhs) | Stipulated period of completion | Value of works remaining to be completed (Rs. lakhs) (attach certificate from Engineer in Charge) | Anticipated date of completion |
| --- | --- | --- | --- | --- | --- | --- | --- |
| (1) | (2) | ( 3) | (4) | (5) | (6) | (7) | (8) |

- Works for which Tenders already submitted:

| Description of Work | Place & State | Name and Address of Employer | Estimated value of works ( Rs. lakhs) | Stipulated period of completion | Date when decision is expected | Remarks if any |
| --- | --- | --- | --- | --- | --- | --- |
| (1) | (2) | (3) | (4) | (5) | (6) | (7) |

  - The following items of equipment are considered essential for successfully carrying out the works. The Tenderer should furnish all the information listed below.

| Item of Equipment | Requirement |  |  | Owned and available |  | Remarks |
| --- | --- | --- | --- | --- | --- | --- |
|  | No. | Capacity | Owned | Number/ Capacity | Age/ Condition |  |

  - Reports on the financial standing of the tenderer, such as profit and loss statements

and auditor’s reports for the last five years;

  - Qualification and experience of the key technical and management personnel in permanent employment with the tenderer and those that are proposed to be deployed on this contract, if awarded.

  - Name, address, and telephone, telex & fax numbers and email of the Tenderers' bankers who may provide references if contacted by the Employer.

  - Evidence of access to financial resources to meet the qualification requirement specified in ITT Clause Cash in hand, Letter of Credit etc. List them below and attach certificate from the Banker in the suggested format as under.

BANKER’S CERTIFICATE

ON BANKS LETTER HEAD

……………………………………………………………………………………................................

FORMAT OF BANKER’S CERTIFICATE/LINE OF CREDIT LETTER

[TO BE ISSUED IN THE LETTER HEAD OF THE BANK BRANCH]

Reference Number (SL.No) Place:

Date:

To:

[Name & Address of the beneficiary]

This is to certify that Mr./M/s.________________________________________________[name of

the customer] having his/their registered/administrative office at____________________________

_____________________________________________________is a customer of our Bank and is/

are engaged in ____________________________________________[name of activity]. If the

said

customer is allotted/ awarded with __________________________________________

“Survey, Investigation, design, Supply, Installation, Testing and Commissioning of Lift Irrigation system (Head Works consisting of Intake canal, Jack well cum pump house, Power supply including substations and Transmission lines, Rising Main including Thrust Block, Valve Chambers,  Delivery chamber, approach roads etc) to Filling up of Kogaluru percolation tank coming under minor irrigation department from Kogaluru tank in Channagiri Taluk Davanagere  District on Turn-key basis”

we may extend credit facilities upto Rs.142.00 lakhs, to meet his/their  working capital requirement towards the execution of the said work order as per the Loan Policy of the Bank.

This certificate is valid upto Six months from date of issue, that is upto dd/mm/yyyy.

Yours faithfully,

BRANCH MANAGER.                                  Sd/-

Name of the Bank, Senior Bank Manger

Address:……………………………….

  - Proposals for subcontracting components of works amounting to more than 20% of the contract price.”Deleted Since no Sub contracting is allowed.”

| Item of work | Value of sub-contract | Identified sub-contract (Name and address) | Experience of similar work |
| --- | --- | --- | --- |

  - Information on litigations in which the Tenderer is involved:

| Other Party (ies) | Employer | Details of dispute | Amount involved | Remarks showing present status |
| --- | --- | --- | --- | --- |

  - The proposed methodology and program of construction, backed with equipment planning and deployment, duly supported with broad calculations and quality control procedures proposed to be adopted, justifying their capability of execution and completion of the work as per technical specifications within the stipulated period of completion as per milestones.

SECTION 4

## FORMS OF TENDER, LETTER OFACCEPTANCE, NOTICE TO PROCEED WITH THE WORK AND AGREEMENT FORM

### SECTION 4:

FORMS OF TENDER, LETTER OF ACCEPTANCE, NOTICE TO PROCEED WITH THE WORK AND AGREEMENT FORM

Form of Tender

Description of the work:-

“Survey, Investigation, design, Supply, Installation, Testing and Commissioning of Lift Irrigation system (Head Works consisting of Intake canal, Jack well cum pump house, Power supply including substations and Transmission lines, Rising Main including Thrust Block, Valve Chambers,  Delivery chamber, approach roads etc) to Filling up of Kogaluru percolation tank coming under minor irrigation department from Kogaluru tank in Channagiri Taluk Davanagere  District on Turn-key basis”

To,

Executive Engineer, KNNL, No5 BCD Division, Davanagere..

GENTLEMEN,

We offer to execute the Works described above in accordance with the Conditions of Contract accompanying  this  Tender  for  the  Contract  Price  of 	   [in  figures] (	) [in letters] (inclusive of premium and exclusive of GST)

This Tender and your written acceptance of it shall constitute a binding contract between us. We understand that you are not bound to accept the lowest or any tender you receive.

The advance payment required is Rs. Nil

We undertake that, in competing for (and, if the award is made to us, in executing) the above contract, we will strictly observe the laws against fraud and corruption in force in India namely “Prevention of Corruption Act 1988”.

We hereby confirm that this Tender complies with the Tender validity and Earnest money deposit required by the Tender documents.

We attach herewith our current income-tax clearance certificate. Yours faithfully,

Authorized Signature:

Name & Title of Signatory:

Name of Tenderer		 Address:

#### Letter of Acceptance

(Letter head paper of the Employer)

[date]

To:			 [name and address of the Contractor]

Dear Sirs,

This is to notify you that your Tender dated 	for “Survey, Investigation, design, Supply, Installation, Testing and Commissioning of Lift Irrigation system (Head Works consisting of Intake canal, Jack well cum pump house, Power supply including substations and Transmission lines, Rising Main including Thrust Block, Valve Chambers,  Delivery chamber, approach roads etc) to Filling up of Kogaluru percolation tank coming under minor irrigation department from Kogaluru tank in Channagiri Taluk Davanagere  District on Turn-key basis”

for the Contract Price of Rupees 	[amount in words and figures], (inclusive of premium and exclusive of GST) as corrected and modified in accordance with the Instructions to Tenderers is hereby accepted by our Agency.

You are hereby requested to furnish Security deposit plus additional security for unbalanced tenders in accordance with of Clause 25.5 of ITT, in the form detailed in Clause 29.1 of ITT and clause 43 of the conditions of contract for an amount of Rs.—————( As defined in contract data) within 20 days of the receipt of this letter of acceptance valid up to 30 days from the date of expiry of Defects Liability Period i.e. up to	and sign the contract, failing which action as stated in Para 29.4 of ITT will be taken.

Yours faithfully,

Executive Engineer, KNNL,No5 BCD Division, Davanagere

Issue of Notice to proceed with the work

(Letter head of the Employer)

To

————— (date)

—————————————— (name and address of the Contractor)

——————————————

——————————————

Dear Sirs:

Pursuant to your furnishing the requisite security deposit as stipulated in ITT Clause 29.1 and signing of the contract agreement for the work of “Survey, Investigation, design, Supply, Installation, Testing and Commissioning of Lift Irrigation system (Head Works consisting of Intake canal, Jack well cum pump house, Power supply including substations and Transmission lines, Rising Main including Thrust Block, Valve Chambers,  Delivery chamber, approach roads etc) to Filling up of Kogaluru percolation tank coming under minor irrigation department from Kogaluru tank in Channagiri Taluk Davanagere  District on Turn-key basis”  a Tender Price of Rs.—

—————, you are hereby instructed to proceed with the execution of the said works in accordance with the contract documents.

Yours faithfully,

Executive Engineer, KNNL, No5 BCD Division, Davanagere

#### Agreement Form

###### Agreement

This agreement, made the 	day of 	20	,

between

Executive Engineer, KNNL, No5 BCD Division, Davanagere. District

(herein after called “the Employer”) of the one part and

[name and address of contractor] (herein after called “the Contractor”) of the other part.

Whereas the Employer is desirous that the Contractor execute

“Survey, Investigation, design, Supply, Installation, Testing and Commissioning of Lift Irrigation system (Head Works consisting of Intake canal, Jack well cum pump house, Power supply including substations and Transmission lines, Rising Main including Thrust Block, Valve Chambers,  Delivery chamber, approach roads etc) to Filling up of Kogaluru percolation tank coming under minor irrigation department from Kogaluru tank in Channagiri Taluk Davanagere  District on Turn-key basis” [Name and identification number of Contract] (Hereinafter called “the Works”) and the Employer has accepted the Tender by the Contractor for the execution and completion of such Works and the remedying of any defects therein at a contract price of Rupees...............................

NOW THIS AGREEMENT WITNESSETH as follows:

    - In this Agreement, words and expression shall have the same meanings as are respectively assigned to them in the Conditions of Contract hereinafter referred to, and they shall be deemed to form and be read and construed as part of this Agreement.

    - In consideration of the payments to be made by the Employer to the Contractor as hereinafter mentioned, the Contractor hereby covenants with the Employer to execute and complete the Works and remedy any defects therein in conformity in all aspects with the provisions of the Contract.

    - The Employer hereby covenants to pay the Contractor in consideration of the execution and completion of the Works and the remedying the defects wherein the Contract Price or such other sum as may become payable under the provisions of the Contract at the times and in the manner prescribed by the Contract.

    - The following documents shall be deemed to form and be read and construed as part of this Agreement, viz:

      - Letter of Acceptance;

      - Notice to proceed with the works;

      - Contractor’s Tender;

      - Contract Data;

      - Conditions of contract (including Special Conditions of Contract);

      - Specifications;

      - Drawings;

      - Bill of Quantities; and

      - Any other document listed in the Contract Data as forming part of the contract.

In witness whereof the parties thereto have caused this Agreement to be executed the day and year first before written.

The Common Seal of		 Was here unto affixed in the presence of:

Signed, Sealed and Delivered by the said

in the presence of:

Binding Signature of Employer			 Binding Signature of Contractor

# SECTION-5

# CONDITIONS OF CONTRACT

CONDITIONS OF CONTRACT TABLE OF CONTENTS

| A. General |  |  | C. Quality Control |  |  |
| --- | --- | --- | --- | --- | --- |
|  |  | Page no. |  |  | Page No. |
| 1 | Definitions | 46-46 | 29 | Identifying Defects | 53-53 |
| 2 | Interpretation | 47-47 | 30 | Tests | 53-53 |
| 3 | Law governing contract | 47-47 | 31 | Correction of Defects | 53-53 |
| 4 | Employers decisions | 47-47 | 32 | Uncorrected Defects | 53-53 |
| 5 | Delegation | 48-48 |  |  |  |
| 6 | Communications | 48-48 |  |  |  |
| 7 | Sub-contracting | 48-48 | D. Cost Control |  |  |
| 8 | Other Contractors | 48-48 | 33 | Bill of Quantities | 53-53 |
| 9 | Personnel | 48-48 | 34 | Variations | 54-54 |
| 10 | Employer’s & Contractor’s Risks | 48-48 | 35 | Payments for Variations | 54-54 |
| 11 | Employer’s Risks | 48-48 | 36 | Submission of bills for payment | 55-55 |
| 12 | Contractor’s Risks | 49-49 | 37 | Payments | 55-55 |
| 13 | Insurance | 50-50 | 38 | Compensation events | 56-56 |
| 14 | Site Investigation Reports | 50-50 | 39 | Tax | 56-56 |
| 15 | Queries about the Contract | 50-50 | 40 | Price Adjustment | 57-57 |
|  | Data | 50-50 | 41 | Liquidated Damages | 59-59 |
| 16 | Contractor to Construct the | 50-50 | 42 | Advance Payments | 59-59 |
|  | Works | 50-50 | 43 | Securities | 60-60 |
| 17 | The Works to be completed by | 50-50 | 44 | Cost of Repairs | 60-60 |
|  | the intended completion date | 50-50 |  |  |  |
| 18 | Approvals by the Employer | 50-50 | E | Finalising the Contract |  |
| 19 | Safety | 51-51 | 45 | Completion | 60-60 |
| 20 | Discoveries | 51-51 | 46 | Taking Over | 60-60 |
| 21 | Possession of the Site | 51-51 | 47 | Final Account | 60-60 |
| 22 | Access to site | 51-51 | 48 | As build drawings / Operating and Maintenance Manuals | 60-60 |
| 23 | Instructions | 51-51 | 49 | Termination | 61-61 |
| 24 | Procedure for resolution of disputes | 51-51 | 50 | Payment upon Termination | 62-62 |
|  |  |  | 51 | Property | 62-62 |
|  |  |  | 52 | Release from performance | 62-62 |
| B. Time Control |  |  | F | Special conditions of contract |  |
| 25 | Program | 52-52 |  |  |  |
| 26 | Extension of the Intended Completion date | 52-52 |  |  |  |
| 27 | Delays Ordered by the Employer | 52-52 |  |  |  |
| 28 | Management meetings | 52-52 |  |  |  |

### CONDITIONS OF CONTRACT

        - GENERAL

###### Definitions

  - Terms which are defined in the Contract Data are not also defined in the Conditions of Contract but keep their defined meanings. Bold letters are used to identify defined terms.

Bill of Quantities means the priced and completed Bill of Quantities forming part of the Tender.

Compensation events are those defined in Clause 38 hereunder.

The Completion Date is the date of completion of the Works as certified by the Employer in accordance with Sub Clause 46.1.

The Contract is the contract between the Employer and the Contractor to execute, complete and maintain the Works. It consists of the documents listed in Clause 2.2 below.

The Contract Data defines the documents and other information which comprise the Contract. The Contractor is a person or corporate body whose Tender to carry out the Works has been accepted by the Employer.

The Contractor's Tender is the completed Tender document submitted by the Contractor to the Employer.

The Contract price is the price stated in the Letter of Acceptance and thereafter as adjusted in accordance with the provisions of the Contract.

Days are calendar days; months are calendar months.

A Defect is any part of the Works not completed in accordance with the Contract.

The Defects liability period is the period named in the Contract Data and calculated from the Completion Date.

The Employer is the party who will employ the Contractor to carry out the Works.

Equipment is the Contractor's machinery and vehicles brought temporarily to the Site to construct the Works.

The Initial Contract price is the Contract Price listed in the Employer's Letter of Acceptance. The Intended Completion Date is the date on which it is intended that the Contractor shall complete the Works. The Intended Completion Date is specified in the Contract Data. The Intended Completion Date may be revised only by the Employer by issuing an extension of time.

Materials are all supplies, including consumables, used by the contractor for incorporation in the Works.

Plant is any integral part of the Works which is to have a mechanical, electrical, electronic or chemical or biological function.

The Site is the area defined as such in the Contract Data.

Specification means the Specification of the Works included in the Contract and any modification or addition made or approved by the Employer.

The Start Date is given in the Contract Data. It is the date when the Contractor shall commence execution of the works. It does not necessarily coincide with any of the Site Possession Dates.

A Subcontractor is a person or corporate body who has a Contract with the Contractor to carry out a part of work of the Contract which includes work on the Site.

A Variation is an instruction given by the Employer which varies the Works.

The Works are what the Contract requires the Contractor to construct, install, and turn over to the Employer, as defined in the Contract Data.

###### Interpretation

  - In interpreting these Conditions of Contract, singular also means plural, male also means female or neuter, and the other way around. Headings have no significance. Words have their normal meaning under the language of the Contract unless specifically defined. The Employer will provide instructions clarifying queries about the Conditions of Contract.

  - The documents forming the Contract shall be interpreted in the following order of priority:

    - Agreement

    - Letter of Acceptance, notice to proceed with the works

    - Contractor’s Tender

    - Contract Data

    - Conditions of Contract

    - Specifications

    - Drawings

    - Bill of quantities and

    - Any other document listed in the Contract Data as forming part of the Contract.

###### Law Governing Contract

  - The law governing the Contract is the Laws of India supplanted by the Karnataka Local Acts.

###### Employer's decisions

  - Except where otherwise specifically stated, the Employer will decide contractual matters between the Employer and the Contractor.

###### Delegation

  - The Employer may delegate any of his duties and responsibilities to other people after notifying the Contractor and may cancel any delegation after notifying the Contractor.

###### Communications

  - Communications between parties which are referred to in the conditions are effective only when in writing. A notice shall be effective only when it is delivered (in terms of Indian Contract Act).

- Sub-Contracting Deleted as per G. O No. FD 4 PCL 2008 dated 14/10/2008.

  - The Contractor may subcontract with the approval of the Employer but may not assign the Contract without the approval of the Employer in writing. Subcontracting does not alter the Contractor's obligations.

###### Other Contractors

  - The Contractor shall cooperate and share the Site with other contractors, public authorities, utilities, and the Employer.

###### Personnel

  - The Contractor shall employ the technical personnel (of number and qualifications) as may be stipulated by GOK from time to time during the execution of the work. The technical staff so employed shall be available at site as may be stipulated by the Employer.

  - If the Employer asks the Contractor to remove a person who is a member of the Contractor’s staff or his work force stating the reasons, the Contractor shall ensure that the person leaves the Site within seven days and has no further connection with the work in the Contract.

###### Employer’s and Contractor's risks

  - The Employer carries the risks which this Contract states are Employer’s risks, and the Contractor carries the risks which this Contract states are Contractor’s risks.

###### Employer's risks

  - The Employer is responsible for the excepted risks which are:

- Rebellion, riot commotion or disorder unless solely restricted to employees of the Contractor or his Sub-Contractors arising from the conduct of the Works; or

- a cause due solely to the design of the Works, other than the Contractor’s design; or

- any operation of the forces of nature (in so far as it occurs on the Site) which an experienced contractor:

  - could not have reasonably foreseen; or

  - could reasonably have foreseen, but against which he could not reasonably have taken at least one of the following measures;

    - prevent loss or damage to physical property from occurring by taking appropriate measures or

    - insure against such loss or damage

###### Insurance

  - The Contractor shall prior to commencing the works, effect and thereafter maintain insurances, in the joint names of the Employer and the Contractor, (cover from the first working day after the Start Date to the end of Defects Liability Period), in the amounts stated in the Contract Data: Insurance shall be for agreement amount and valid from date of agreement to till end of O & M Period.

    - for loss of or damage to the Works, Plants and Materials and the Contractor’s equipment;

    - for liability of both Parties for loss, damage, death and injury to third parties or their property arising out of the Contractor’s performance of the Contract including the Contractor’s liability for damage to the Employer’s property other than the Works and

    - for liability of both Parties and of any Employer’s representative for death and injury to the Contractor’s personnel except to the extent that liability arises from the negligence of the Employer, any Employer’s representative or their Employees.

  - Policies and certificates for insurance shall be delivered by the Contractor to the Employer for his approval before the Start Date. All such insurance shall provide for compensation to be payable to rectify the loss or damage incurred. All payments received from insurers relating to loss or damage shall be held jointly by the Parties and used for the repair of the loss or damage or as compensation for loss or damage that is not to be repaired.

  - If the Contractor fails to effect or keep in force any of the insurances referred to in the previous sub-clauses or fails to provide satisfactory evidence, policies or receipts, the Employer may without prejudice to any other right or remedy, effect insurance for the cover relevant to such default and pay the premiums due and recover the same as a deduction from any other monies due to the Contractor. If no payments are due, the payment of the premiums shall be a debt due.

  - Alterations to the terms of insurance shall not be made without the approval of the Employer.

  - Both Parties shall comply with any conditions of the insurance policies.

###### Contractor’s Risks

  - All risks of loss of or damage to physical property and of personal injury and death which arise during and in consequence of the performance of the Contract other than the excepted risks are the responsibility of the Contractor.

###### Site Investigation Reports:

  - The Contractor, in preparing the tender, shall rely on any site investigation reports referred to in the Contract data, supplemented by any information available to the Tenderer.

###### Queries about the Contract Data

  - The Employer will clarify queries on the Contract Data.

###### Contractor to construct the Works-

  - The Contractor shall construct the works in accordance withy specification and Drawings and as per the directions of the Engineer in-charge.

###### The Works to be completed by the Intended Completion Date

  - The Contractor may commence execution of the Works on the Start Date and shall carry out the Works in accordance with the program submitted by the Contractor, as updated with the approval of the Employer, and complete them by the Intended Completion Date.

###### Approval by the Employer

  - The Contractor shall submit Specification and drawings showing the proposed Temporary Works to the Employer, who is to approve them if they comply with the Specifications and Drawings.

  - The Contractor shall be responsible for the design of Temporary Works

  - The Employer’s approval shall not alter the Contractor’s responsibility for design of the

Temporary Works.

  - The Contractor shall obtain approval of third parties to the design of third parties to the design of the temporary Works where required.

  - All Drawings prepared by the Contractor for the execution of the temporary or permanent Works, are subject to prior approval by the Employer before their use.

###### Safety

  - The Contractor shall be responsible for the safety of all activities on the Site.

###### Discoveries

  - Anything of historical or other interest or of significant value unexpectedly discovered on the Site is the property of the Employer. The Contractor is to notify the Employer of such discoveries and carry out the Employer's instructions for dealing with them.

- Possession of the Site: Deleted “Refer Clause No. 12 of Data Sheet”

  - The Employer shall give possession of all parts of the Site to the Contractor. If possession of a part is not given by the date stated in the Contract Data the Employer is deemed to have delayed the start of the relevant activities and this will be Compensation Event.

###### Access to the Site

  - The Contractor shall allow the Employer and any person authorized by the Employer access to the Site, to any place where work in connection with the Contract is being carried out or is intended to be carried out and to any place where materials or plant are being manufactured / fabricated / assembled for the works.

###### Instructions

  - The Contractor shall carry out all instructions of the Employer which comply with the applicable laws where the Site is located.

###### Procedure for resolution of Disputes: Deleted Refer Clause No. 13 of

Data Sheet”

  - If the Contractor is not satisfied with the decision taken by the Employer, the dispute shall be referred by either party to Arbitration within 30 days of the notification of the Employer’s decision.

  - If neither party refers the dispute to Arbitration within the above 30 days, the

Employer’s decision will be final and binding.

  - The Arbitration shall be conducted in accordance with the arbitration procedure stated in the Special Conditions of Contract.

#### Time Control

###### Program

  - Within the time stated in the Contract Data the Contractor shall submit to the Employer for approval a Program showing the general methods, arrangements, order, and timing for all the activities in the Works.

  - The Employer's approval of the Program shall not alter the Contractor's obligations. The Contractor may revise the Program and submit it to the Employer again at any time. A revised Program is to show the effect of Variations and Compensation Events. Deleted Refer Clause No. 14 of Data Sheet.

###### Extension of the Intended Completion Date: Deleted Refer Clause No.15 of Data Sheet

  - The Employer shall extend the Intended Completion Date if a Variation is issued which makes it impossible for Completion to be achieved by the Intended Completion Date.

  - The Employer shall decide whether and by how much to extend the Intended Completion Date within 21 days of the Contractor asking the Employer for a decision upon the effect of a Compensation Event or Variation and submitting full supporting information.

###### Delays Ordered by the Employer

  - The Employer may instruct the Contractor to delay the start or progress of any activity within the Works.

###### Management Meetings

  - The Employer may require the Contractor to attend a management meeting. The business of a management meeting shall be to review the progress achieved and the plans for remaining work.

  - The responsibility of the parties for actions to be taken is to be decided by the Employer either at the management meeting or after the management meeting and stated in writing to be distributed to all who attended the meeting.

#### Quality Control

###### Identifying Defects

  - The Employer shall check the Contractor's work and notify the Contractor of any Defects that are found. Such checking shall not affect the Contractor's responsibilities. The Employer may instruct the Contractor to search for a Defect and to uncover and test any work that the Employer considers may have a Defect.

###### Tests: Deleted Refer Clause No. 16 of Data Sheet

  - If the Employer instructs the Contractor to carry out a test not specified in the Specification to check whether any work has a Defect and the test shows that it does, the Contractor shall pay for the test and any samples. If there is no Defect the test shall be a Compensation Event.

###### Correction of Defects

  - The Employer shall give notice to the Contractor of any Defects before the end of the Defects Liability Period, which begins at Completion and is defined in the Contract Data. The Defects Liability Period shall be extended for as long as Defects remain to be corrected.

  - Every time notice of a Defect is given; the Contractor shall correct the notified Defect

within the length of time specified by the Employer’s notice.

###### Uncorrected Defects

  - If the Contractor has not corrected a Defect within the time specified in the Employer’s notice, the Employer will assess the cost of having the Defect corrected, and the Contractor will pay this amount.

#### Cost Control

###### Bill of Quantities (BOQ)

  - The BOQ shall contain items for the construction, installation, testing, and commissioning work to be done by the Contractor. Deleted Refer Clause No. 17 of Data Sheet.

  - The BOQ is used to calculate the Contract Price. The Contractor is paid for the quantity of the work done at the rate in the BOQ for each item.

###### Variations: Deleted since this is turnkey tender.

  - The Employer shall have power to order the Contractor to do any or all of the following as considered necessary or advisable during the progress of the work by him

    - Increase or decrease of any item of work included in Bill of Quantities (BOQ);

    - Omit any item of work;

    - Change the character or quality or kind of any item of work;

    - Change the levels, lines, positions and dimensions of any part of the work;

    - Execute additional items of work of any kind necessary for the completion of the works; and

    - Change in any specified sequence, methods or timing of construction of any part of the work.

  - The Contractor shall be bound to carry out the work in accordance with any instructions in this connection, which may be given to him in writing by the Employer and such alteration shall not vitiate or invalidate the contract.

  - Variations shall not be made by the Contractor without an order in writing by the Employer, provided that no order in writing shall be required for increase or decrease in the quantity of an item appearing in the BOQ so long as the work executed conforms to the approved drawings.

  - The Contractor shall promptly request in writing to the Employer to confirm verbal orders and the officer issuing oral instructions shall confirm it in writing within 30 days, failing which the work shall be carried out as through there is no variation. In case variation is approved it shall be accompanied with BOQ, failing which the contractor shall be responsible for deviation if any. Further, approval of competent authority has to be obtained for the variation exceeding 5% (as per GO No.FD 4 PCL 2008 dated 14/10/2008) or as per the previling deligation of powers.

###### Payments for Variations “Deleted since this is turnkey project”

  - Payment for increase in the quantities of an item in the BOQ up to 25% of that provided in the Bill of Quantities shall be made at the rates quoted by the Contractor.

  - For quantities in excess of 125% of the tendered quantity of an item as given in the BOQ, the Contractor shall be paid at the rate entered in or derived from in the Schedule of Rates (applicable for the area of the work and current at the time of award of contract) plus or minus the overall percentage of the original tendered rates over the current Schedule of Rates prevalent at the time of award of contract.

  - If there is no rate for the additional, substituted or altered item of the work in the BOQ, efforts would be made to derive the rates from those given in the BOQ or the Schedule of Rates (applicable for the area of the work and current at the time of award of contract) and if found feasible the payment would be made at the derived rate for the item plus or minus the overall percentage of the original tendered rates over the current Schedule of Rates prevalent at the time of award of contract.

  - If the rates for additional, substituted or altered item of work cannot be determined either as at 35.1 or 35.2 or 35.3 above, the Contractor shall be requested to submit his quotation for the items supported by analysis of the rate or rates claimed, within 7 days.

  - If the Contractor's quotation is determined unreasonable, the Employer may order the Variation and make a change to the Contract Price which shall be based on Employer’s own forecast of the effects of the Variation on the Contractor's costs.

  - If the Employer decides that the urgency of varying the work would prevent a quotation being given and considered without delaying the work, no quotation shall be given and the Variation shall be treated as a Compensation Event.

  - Under no circumstances the Contractor shall suspend the work on the plea of non- settlement of rates for items falling under this Clause.

###### Submission of Bills for Payment

  - The Contractor shall submit to the Employer monthly bills of the value of the work completed less the cumulative amount paid previously.

  - The Employer shall check the Contractor's bill and determine the value of the work executed which shall comprise of (i) value of the quantities of the items in the BOQ completed and (ii) valuation of Variations and Compensation Events. “Deleted. Refer Sl.No 31 of Data Sheet”

  - The Employer may exclude any item paid in a previous bill or reduce the proportion of any item previously paid in the light of later information.

###### Payments

  - Payments shall be adjusted for deductions for advance payments, other than recoveries in terms of the contract and taxes, at source, as applicable under the law. The Employer shall pay the Contractor within 60 days of submission of bill. The contractor shall be liable to pay liquidated damages for shortfall in progress.

For progress beyond the agreed program payment is subjected to availability of funds. “Deleted. Refer Sl.No 19 of Data Sheet”

  - Items of the Works for which no rate or price has been entered in will not be paid for by the Employer and shall be deemed covered by other rates and prices in the Contract.

###### Compensation events: Deleted-Since this is a Turnkey tender

  - The following are Compensation events unless they are caused by the Contractor:

- Deleted. Since, this is turnkey tender.

- The Employer orders a delay or does not issue drawings, specifications or instructions required for execution of works on time.

- The Employer instructs the Contractor to uncover or to carry out additional tests upon work which is then found to have no Defects.

- The Employer gives an instruction for dealing with an unforeseen condition, caused by the Employer, or additional work required for safety or other reasons.

- The effect on the Contractor of any of the Employer’s Risks.

- The Employer unreasonably delays issuing a Certificate of Completion.

- Other Compensation Events listed in the Contract Data or mentioned in the Contract.

  - If a Compensation Event would cause additional cost or would prevent the work being completed before the Intended Completion Date, the Contract Price shall be increased and/or the Intended Completion Date is extended. The Employer shall decide whether and by how much the Contract Price shall be increased and whether and by how much the Intended Completion Date shall be extended.

  - As soon as information demonstrating the effect of each Compensation event upon the Contractor's forecast cost has been provided by the Contractor, it is to be assessed by the Employer and the Contract Price shall be adjusted accordingly. If the Contractor's forecast is deemed unreasonable, the Employer shall adjust the Contract Price based on Employer’s own forecast. The Employer will assume that the Contractor will react competently and promptly to the event.

  - The Contractor shall not be entitled to compensation to the extent that the Employer's interests are adversely affected by the Contractor not having given early warning or not having cooperated with the Employer.

###### Tax “Deleted Refer Clause.No 20 of Data Sheet”

  - The rates quoted by the Contractor shall be deemed to be inclusive of the sales and other taxes that the Contractor will have to pay for the performance of this Contract. The Employer will perform such duties in regard to the deduction of such taxes at source as per applicable law.

###### Price Adjustment modified as per GO FD 59 PRO CELL 2004 dated 26.11.2004, GO FD 3 PCL 2008 dated 21.11.2008 and GO 791 Exp-12

2015 dated 26.2.2016

  - Contractor price shall be adjusted for increase or decrease in rates and prices of labour, material, fuels and lubricants in accordance with the following principles and procedures and as per formulae given in the contract data.

- For all works costing more than Rs.50 lakhs, if the period of execution is more than 12 months, the price adjustment will be calculated as prescribed in Annexure to G.O. No: FD 59 PRO CELL 2004, dated: 26.11.2004. and latest amendments.

- If the period of execution is more than 6 months but less than or equal to 12 months for work costing more than Rs.50 lakhs, star rates in respect of specified materials (cement, steel and bitumen) only shal l be payable to the contractor based on the all India average wholesale price index for the said materials. The star rates adjustment shall be as per the increase or decrease in the index as applied to the said materials between the last date for receivin g bids and the date of execution as per the approved programme of works submitted by the contractor at the time of execution of agreement which shall mandatorily be a part of the agreement.

- If the period of execution is less than or equal to 6 months, for all works irrespective of the cost of the works, price adjustment or star rates shall not be applicable.

- In works contracts where price adjustment clause is provided, the price adjustment shall be admissible from the date of opening of tenders (Original or extended).

- Price adjustment clause shall not be included in Goods and Equipment tender documents. However, in respect of tender documents for procurement of Electric Cables, Transformers, Generators, Motors that have raw material component subject to price fluctuations, appropriate price adjustment clauses may be incorporated by the Tender Inviting Authority in the tender documents, with the specific approval of the concerned Head of the Department or Managing Director of the Public Sector Undertaking/ Board.

The above mentioned method of price adjustment are applicable in following conditions

Case 1: When the time extension is granted for the reasons is not attributable to the contractor.

Price adjustment is admissible as per terms of contract for the work carried out during the extension of the time granted for completion of work

Case 2: When the time extension is granted for the reasons attributable to the contractor.

Price adjustment is admissible up to the original contract period only and for the period of extension, price adjustment is not admissible and payment for such extension shall be at tendered rate only.

Case 3: When extension of time is granted for the reasons attributable to employer followed by reasons attributable to the contractor.

Price adjustment is admissible as per terms of contract for the work carried out during the original period of completion and during the extension of time granted for completion of work for reasons attributable to employer. For the work carried out durning the extension of time granted due to delay attributable to the contractor Price Adjustment is not admissible and the contractor shall be paid only at the tendered rates.

Case 4: When delay occurs initially attributable to the contractor and later attributable to Employer.

Extension of time in such cases is to be granted by first appending extension of time due to delay by employer to the original contract period, all though the delay is initially due to contractor and later by the employer. The extension of time granted due to delay by the contractor shall be considered as the last phase after extension due to delay by employer is added to the original contract period.

Price adjustment is admissible to the delay attributable to the employer. The Price Adjustment for the initial delay attributable to the contractor is not admissible and the contractor shall be paid only at the Tendered rates.

General Clarifications

- Quarter means a period of the consecutive months as detailed below:

  - For reckonning the average base price index

Three consecutive calendar months preceeding the calendar month of opening the Tender.

  - For reckonning the value of ‘R’

Three consecutive calendar months including the calendar month in which work was sarted in the first instance and thereafter next quarter shall be consecutive three months following the preceeding quarter.

- The value of R defined in Government Order reffered at G.O. No. FD 59 PRO CELL 2004, dated 26/11/2004 is redefined as below:

R = Total value or work done during the quarter. It would include the amount of secured advance for materials paid for (if any) during the quarter less the amount of the secured advance recovered during the quarter. It will exclude value for works executed under variations for which Price Adjustment (if any) will be worked out separately based on the terms mutually agreed. It will also exclude the value of work done during the quarter which was programmed to be done prior to this quarter as per the work schedule in the agreement.

  - To the extent that full compensation for any rise or fall in costs to the contractor is not covered by the provisions of this or other Clauses in the Contract, the unit rates included in the contract shall be deemed to include amounts to cover the contingency of such other rise or fall in costs.

- Liquidated Damages: Deleted. Refer Clause.13 of Special Condition of Contract

  - The Contractor shall pay liquidated damages to the Employer at the rate per day stated in the Contract Data for each day that the Completion Date is later than the Intended Completion Date (for the whole of the works or the milestone as stated in the Contract Data). The total amount of liquidated damages shall not exceed the amount defined in the Contract Data. The Employer may deduct liquidated damages from payments due to the Contractor. Payment of liquidated damages does not affect the Contractor's liabilities.

  - If the Intended Completion Date is extended after liquidated damages have been paid, the Employer shall correct any overpayment of liquidated damages by the Contractor by adjusting the next payment of bill.

###### Advance Payments: “Deleted as per G.O. No. Ja Sam E 127 MBI 2020 dated: 30-05-2020”

  - The Employer shall make payment to the Contractor of the amounts stated in the Contract Data by the date stated in the Contract Data, against provision by the Contractor of an unconditional bank guarantee in a form acceptable to the Employer issued by a Nationalized/Scheduled Bank in amounts equal to the advance payment. The guarantee shall remain effective until the advance payment has been repaid, but the amount of the guarantee shall be progressively reduced by the amounts repaid by the Contractor. Interest will not be charged on the advance payment.

  - The Contractor is to use the advance payment only to pay for Mobilization expenses required specifically for execution of the Works. The Contractor shall demonstrate that advance payment has been used in this way by supplying copies of invoices or other documents to the Employer.

  - The advance payment shall be repaid by deducting proportionate amounts from payments otherwise due to the Contractor, following the schedule of completed percentages of the Works on a payment basis. No account shall be taken of the advance payment or its repayment in assessing valuation of the work done, variations, price adjustments, compensation events or liquidated damages.

###### Securities: Deleted Refer Sl no 14 of Special Condition

###### 43.1  Within 20 days of receipt of the Letter of Acceptance, the successful Tenderer

###### shall deliver to the Employer a Security deposit in any of the forms given

###### below for an amount equivalent  to 5% of the Contract price plus additional security for unbalanced tenders (Difference between amount put to tender as per current CSR and quoted amount) shall be adopted as per  Government of Karnataka Order:DE: 456:ªÉZÀÑ: 12/ 2022/ ¨ÉAUÀ¼ÀÆgÀÄ ¢£ÁAPÀ; 10.08.2022 as specified below: -

Banker’s cheque/Demand draft,/Pay Order in favour of  theExecutive

Engineer, KNNL, No.5Bhadra canal  Division, Davanagere.

  - . Payable at. Davanagere.or

Irreovacble bank guarantee, including e-bank Guarantee, insurance surety Bonds issued by Insurance company authorized by insurance Regulatory and Development Authorised of India  in the form given in Section 10; orSpecified Small Savings Instruments pledged to Executive Engineer, KNNL, No.5 Bhadra canal Division, Davanagere.

###### Cost of Repairs

  - Loss or damage to the Works or Materials to be incorporated in the Works between the Start Date and the end of the Defects Correction periods shall be remedied by the Contractor at the Contractor's cost if the loss or damage arises from the Contractor's acts or omissions.

#### Finishing the Contract

###### Completion

  - The Contractor shall request the Employer to issue a Certificate of Completion of the Works and the Employer will do so upon deciding that the Work is completed.

###### Taking Over: Deleted. Refer Clause No. 23 of Data sheet.

  - The Employer shall take over the Site and the works within 7 days of issuing a certificate of completion.

###### Final Account “Refer Clause No. 21 of Data Sheet”

  - The Contractor shall supply to the Employer a detailed account of the total amount that the Contractor considers payable under the Contract before the end of the Defects Liability Period. The Employer shall issue a Defect Liability Certificate and certify any final payment that is due to the Contractor within 90 days of receiving the Contractor's account if it is correct and complete. If it is not, the Employer shall issue within 90 days a schedule that states the scope of the corrections or additions that are necessary. If the Final Account is still unsatisfactory after it has been resubmitted, the Employer shall decide on the amount payable to the Contractor and make payment within 60 days of receiving the Contractor’s revised account.

###### As built drawings and /or Operating and Maintenance Manuals

  - If “as built” Drawings and/or operating and maintenance manuals are required, the Contractor

shall supply them by the dates stated in the Contract Data.

  - If the Contractor does not supply the Drawings by the dates stated in the Contract Data, or they do not receive the Employer’s approval, the Employer shall withhold the amount stated in the Contract Data from payments due to the Contractor.

###### Termination

  - The Employer may terminate the Contract if the other party causes a fundamental breach of the Contract.

  - Fundamental breaches of Contract include, but shall not be limited to the following:

- the Contractor stops work for 45 days when no stoppage of work is shown on the current Program and the stoppage has not been authorized by the Employer;

- –Deleted as per GO No. FD 4 PCL 2008, Bangalore dated : 14/10/2008

- the Contractor becomes bankrupt or goes into liquidation other than for a reconstruction or amalgamation;

- –Deleted as per GO No. FD 4 PCL 2008, Bangalore dated : 14/10/2008-

- the Employer gives Notice that failure to correct a particular Defect is a fundamental breach of Contract and the Contractor fails to correct it within a reasonable period of time determined by the Employer;

- the Contractor does not maintain a security which is required;

- the Contractor has delayed the completion of works by the number of days for which the maximum amount of liquidated damages can be paid as defined in the Contract data; and

- if the Contractor, in the judgment of the Employer has engaged in corrupt or fraudulent practices in competing for or in the executing the Contract.

For the purpose of this paragraph : “corrupt practice” means the offering, giving, receiving or soliciting of anything of value to influence the action of a public official in the procurement process or in contract execution. “Fraudulent practice” means a misrepresentation of facts in order to influence a procurement process or the execution of a contract to the detriment of the Employer/Borrower, and includes collusive practice among Tenderers (prior to or after Tender submission) designed to establish Tender prices at artificial non-competitive levels and to deprive the Employee of the benefits of free and open competition.”

  - When either party to the Contract gives notice of a breach of contract to the Employer for a cause other than those listed under Sub Clause 49.2 above, the Employer shall decide whether the breach is fundamental or not.

  - Notwithstanding the above, the Employer may terminate the Contract for convenience.

  - If the Contract is terminated the Contractor shall stop work immediately, make the Site safe and secure and leave the Site as soon as reasonably possible.

###### Payment upon Termination

  - If the Contract is terminated because of a fundamental breach of Contract by the Contractor, the Employer shall prepare bill for the value of the work done up to the date of the bill, less other recoveries due in terms of the contract, less taxes due to be deducted at source as per applicable law and less the percentage to apply to the work not completed as indicated in the Contract Data. Additional Liquidated Damages shall also apply. If the total amount due to the Employer exceeds any payment due to the Contractor the difference shall be a debt payable to the Employer.

  - If the Contract is terminated at the Employer's convenience or because of a fundamental breach of Contract by the Employer, the Employer shall prepare bill for the value of the work done, the reasonable cost of removal of Equipment, repatriation of the Contractor's personnel employed solely on the Works, and the Contractor's costs of protecting and securing the Works up to the date of the certificate, less other recoveries due in terms of the contract, and less taxes due to be deducted at source as per applicable law and make payment accordingly.

###### Property

  - All materials on the Site, Plant, Equipment, Temporary Works and Works are deemed to be the property of the Employer, if the Contract is terminated because of a

Contractor’s default.

###### Release from performance

  - If the Contract is frustrated by any event entirely outside the control of either the Employer or the Contractor the Employer shall certify that the Contract has been frustrated. The Contractor shall make the Site safe and stop work as quickly as possible after receiving this certificate and shall be paid for all work carried out before receiving it and for any work carried out afterwards to which commitment was made.

#### Special Conditions of Contract

###### Labour

The Contractor shall, unless otherwise provided in the Contract, make his own arrangements for the engagement of all staff and labour, local or other, and for their payment, housing, feeding and transport.

The Contractor shall, if required by the Employer, deliver to the Employer a return in detail, in such form and at such intervals as the Employer may prescribe, showing the staff and the numbers of the several classes of labour from time to time employed by the Contractor on the Site and such other information as the Employer may require.

###### Compliance with Labour Regulations

During continuance of the contract, the Contractor and his sub-contractors shall abide at all times by all existing labour enactments and rules made there under, regulations, notifications and bye laws of the State or Central Government or local authority and any other labour law (including rules), regulations, bye laws that may be passed or notification that may be issued under any labour law in future either by the State or the Central Government or the local authority. The Contractor shall keep the Employer indemnified in case any action is taken against the Employer by the competent authority on account of contravention of any of the provisions of any Act or rules made there under, regulations or notifications including amendments. If the Employer is caused to pay or reimburse, such amounts as may be necessary to cause or observe, or for non-observance of the provisions stipulated in the notifications/bye laws/Acts/Rules/regulations including amendments, if any, on the part of the Contractor, Employer shall have the right to deduct any money due to the Contractor including his amount of security deposit. The Employer shall also have right to recover from the Contractor any sum required or estimated to be required for making good the loss or damage suffered by the Employer.

The employees of the Contractor and the Sub-Contractor in no case shall be treated as the employees of the Employer at any point of time.

###### Protection of Environment

The contractor shall take all reasonable steps to protect the environment on and off the Site and to avoid damage or nuisance to persons or to property of the public or others resulting from pollution, noise or other causes arising as a consequence of his methods of operation. During continuance of the contract, the contractor and his sub-contractors shall abide at all times by all existing enactments on environmental protection and rules made there under, regulations, notifications and bye-laws of the State or Central

Government, or local authorities and any other law, bye-law, regulations that may be passed or notification that may be issued in this respect in future by the State or Central Government or the local authority.

###### Arbitration (Clause 24 ): Deleted. Refer Clause No. 14 of Data sheet below

  - The procedure for arbitration shall be as follows:

    - In case of dispute or difference arising between the Employer and the Contractor relating to any matter arising out of or connected with this agreement it shall be settled in accordance with the Arbitration and Conciliation Act 1996. The disputes or differences shall be referred to a Sole Arbitrator. The Sole Arbitrator shall be appointed by agreement between the parties; failing such agreement, by the Appointing Authority (any one of the Organizations as per list enclosed in Annexure)

    - Arbitration proceedings shall be held at	, Karnataka, India

    - ​ The cost and expenses of arbitration proceedings will be paid as determined by the Arbitrator.

However the expenses incurred by each party in connection with the preparation, presentation, etc., shall be borne by each party itself.

    - Performance under the contract shall continue during the arbitration proceedings and payments due the Contractor by the Employer shall not be withheld, unless they are the subject matter of the arbitration proceedings.

[Add other Clauses specific to the work for which tenders are invited.]

###### Death of the Contractor

In case if the death of a contractor, after executing the agreement / commencement of the work, his legal heir, is an eligible registered contractor and is willing, can execute and complete the work, at the accepted tender rates, irrespective of the cost of the work.

###### Royalty Charges

- Royalty as per Govt. notification No.MGD/DCB/2024-25Bangalore Dated: 24.01.2025 issued by department of Mines and geology, Government of Karnataka and the subsequent government notification shall be paid by the contractor by the deduction from his bills. The schedule of royalty charges is annexed.

- The contractor shall produce the Material Dispatch Receipt (MDR) from department of Mines and Geology for exemption.

###### Workers Welfare Cess

As per GO No. CD/300/ LET/ 2006: Dated 18-12-2007, 1% excess will be deducted from the bill as per

labour welfare act as per the Karnataka Building and other Construction’s Workers Welfare Cess Act 1996.

###### Contractor to Subscribe to Worker’s and Contractors' Benevolent

Fund

The contractor shall subscribe to the Workers' and Contractor's benevolent fund at the rate of 0.10% of the gross amount of each bill payable to him in respect of the contract. The amount of subscription should be recovered out of the amount payable to him in each bill.

###### Micro, Small and Medium Enterprises Certificate (MSME)

The Contractor shall produce the Micro, Small and Medium Enterprises (MSME) certificate issued from competent authority for the first bill mandatorily while claiming any concession.

- All the works are to be carried out as per the Standard Specification issued by Employer from time to time.

###### Safety Code

- These safety provisions should be brought to the notice of all concerned by display on notice board by the Contractor at a prominent place at work spot. The persons responsible for compliance of the safety code shall be named therein by the contractor.

- To ensure effective enforcement of the rules relating to safety precautions, the arrangement made by the contractor shall be open to inspection by the Labour-Officer, Engineer or their representatives.

- All necessary personal safety equipment’s as considered adequate by the Engineer-in- Charge should be kept available for the use of persons employed at the site and maintained in a condition suitable for immediate use and the contractor should take adequate steps to ensure proper use of equipment by those concerned.

  - Workers employed on mixing concrete, cement grout, cement mortar shall be provided with protective footwear and protective goggles and protective gloves.

  - Those engaged in mixing or stacking cement or any materials injurious to the eye, nose and mouth shall be provided with a face mask and protective cover free of cost by the contractor.

  - Those engaged in welding work shall be provided with welder’s protective eye

shield and gloves.

  - Stone breakers shall be provided with protective goggle and protective clothing and seated at sufficiently safe intervals.

  - Those engaged in binding and fabricating steel shall be provided with protective gloves.

  - Those Engaged in deep cuts, Aqueducts, large rock excavation shall be provided with helmets.

- When the work is near any place where there is risk of drowning all necessary equipment’s shall be kept ready for use and all necessary steps taken for prompt rescue of any person in danger and adequate provisions should be made for prompt first aid treatment of all injuries likely to be sustained during the course of work.

- Adequate and suitable caution and danger signal boards shall be prominently exhibited at road/river crossing/high tension over head line/where heavy electrical machines are working/where overhead cranes or hoist; derricks, winches are working/where blasting zone is demarcated. The content of the board shall be in English and the local language for easy identification.

- All scaffolding, ladder, stairways, gangways, staging, centring, form work and temporary support and safety devices etc. shall be sound in strength and construction and maintained as such throughout its use.

- No materials on any site of work shall be so stacked as to cause danger or inconvenience to any persons or public.

- The contractor shall provide all necessary fencing and lighting to protect the public/working men from accident and shall be bound to bear the expense of defence of every suit action or other proceedings of law that may be brought by any person for injury sustained owing to neglect of the above precautions and to pay any damages and costs, which may be awarded in any such suit action or proceedings to any such persons or which may with consent of the contractor be paid to compensate any claims by any such persons.

- No electric cables or apparatus which is liable to be a source of danger to persons employed shall remain electrically charged unless a caution Board is put in to that effect and close approach to the same is prohibited.

- All practical steps shall be taken to prevent danger to persons employed from risk of fire or explosives or flooding. No floor, roof or other portion of any building used for residence shall be so over-loaded with debris or materials so as to render it unsafe.

- The final disposal of water used for work or removed from work spot as well as the supply used for domestic consumption shall be as directed by the Executive Engineer. The contractor shall make his own arrangement for purification of domestic water supply used by his staff and labour colony and used on the site of work to the satisfaction of the Executive Engineer.

- The source of drinking water supply/distribution system in workers colony shall be protected from chances of contamination by poisonous materials/epidemic causing infections bacteria etc., by maintaining the source and system under adequate hygienic conditions.

- Notwithstanding the above clauses from (i.) to (xii) there is nothing in this to exempt the contractor to exclude the operations of any other Act or Rules in force of the Central Government.

###### Tests

The Contractor should establish a full-pledged testing laboratory for conducting all tests required for execution of work in accordance with Technical specifications. The field laboratory so established should have calibrated/certified testing equipments to facilitate testing materials, finished items, electromechanical equipments etc.,. The field laboratory should have qualified personnel and assistants for conducting the tests as per the standards as detailed in broad scope of work. The testing laboratory should be open for inspection and testing by the KNNL authorities.

###### Liquidated Damages

Written Order to Commence Work:

13 (a) after acceptance of the tender, the Executive Engineer shall issue a written order to the successful tenderer to commence the work. The Contractor shall enter upon or commence any portion of work only with the written authority and instructions of the Executive Engineer.

Without such instructions the Contractor shall have no claim to demand for measurements of or payment for, work done by him.

Programme of work

13 (b) The time allowed for carrying out the work as entered in the tender shall be strictly observed by the contractor. It shall be reckoned from the date of issue of written orders to commence work. The work shall throughout the stipulated period of the contract be proceeded with, with all due diligence (time being deemed to be the essence of the contract on the part of the Contractor). To ensure good progress during the execution of the work, the contractor shall be bound (in all cases in which the time allowed for any work exceeds one month) to comply with the time schedule according to the programme of execution of the work as agreed upon and enclosed to the contract. In the absence of specific agreed programme the contractor shall be bound to complete.

1/10 of the work in	¼ of the time

4/10 of the work in	½ of the time

8/10 of the work in	¾ of the time

Full work in	full time

Note: The quantity of the work to be done within a particular time to be specified above when the programme chart is not annexed, shall be fixed and inserted in the blank space kept for the purpose by the officer competent upto the level of Chief Engineer to accept the contract after taking into consideration the circumstances of each case, and the contractor shall abide by the programme of detailed progress laid down	by	that	officer. The  following  proportions  usually  are  found  suitable  in  1/4,  1/2,  3/4  of  the  time:

i) Reasonable progress of earthwork that could be achieved will be 1/6, 1/2, 3/4 the respectively of total value	of	the	work	to	be	done.

(ii) Reasonable progress of masonry work and concreting that could be achieved will be 1/10th, 4/10th, 8/10ths   of   the   total   value   of   the   work   to   be   done. Review	of	progress	and   responsibility	for	delay	etc. 13 (c) (i) The progress of all works costing Rs. 1 lakh and above shall be reviewed by the Executive Engineer with the contractor during the first fortnight of every month. Such a review shall take into account the programme fixed for the previous month, obligations on the part of the KARNATAKA NEERAVARI

NIGAM LIMITED regarding necessary approvals/clearances and also the obligations on the part of the Contractor.

Apportionment  of  responsibility  for  delay  between  Contractor  and  KNNL 13 (c) (ii) In case the progress achieved falls short by more than 25 percent of the cumulative programme, the reasons for such shortfall shall be examined and a record made thereof apportioning the responsibilities for the delay between the Contractor and the KNNL. This record should be signed in full and dated both by the Executive Engineer and the Contractor.

Shortfall	in	progress	made	up	subsequently 13 (c) (iii) To the extent the shortfall is assessed as due to the delay on the part of the contractor, a notice shall be issued to him by the Executive Engineer to make up the shortfall in the succeeding month. If the shortfall is not made up before the progress of the work is reviewed during the second month succeeding the month in which the shortfall was observed, the Contractor shall be liable to pay penalty as indicated in Clause 14 (d) below.

Grant	of	extension	of	time: 13 (c) (iv)If the delay is attributable to reasons beyond the control of the Contractor, requisite extension of time shall be granted by the Executive Engineer in accordance with Clause 14 of Special Conditions of Contract after obtaining the approval of his higher authorities, wherever necessary. Review   of   progress   by   Superintending   Engineer/Chief   Engineer: 13 (c) (v) The Superintending Engineer shall review the progress once in every six months all contracts of value more than Rs.5 lakhs and up to Rs. 100 lakhs. In respect of contracts of value Rs.100 lakhs and above the review shall be done by the Chief Engineer once in six months. These reviews are in addition to the monthly reviews required to be done by the Executive Engineer. The results of the review by the higher authorities shall, wherever necessary, be incorporated in the next review by the Executive Engineer. Settlement of dispute regarding shortfall in progress:

13 (c) (vi) In case of dispute between the Executive Engineer and the Contractor regarding the responsibility for the shortfall in progress, the matter shall be referred to the Chief Engineer/ Managing Director, KNNL who shall thereupon give a decision within one month of the date of receipt of reference. The decision of the Managing Director, shall be final and binding on the Contractor and the Executive Engineer.

Penalty	for	delay: 13 (d) In respect of the shortfall in progress, assessed as due to the delay on the part of Contractor as per

Clause 15 (b) and 15 (c), the Contractor shall be liable to pay as penalty an amount equal to one percent of the estimated cost of the balance work assessed according to the programme, for every day that the due quantity of work remains incomplete, provided always that the total amount of penalty to be paid under the provisions of this clause shall not exceed 7.5 percent of the estimated cost of the entire work as shown in the tender, provided further that in the event of the contractor making up the shortfall in progress within the stipulated or extended time of completion (as approved by the competent authority), the penalty so recovered  may  be  refunded  on  an  application  in  writing  by  the  contractor. Note: If the Executive Engineer considers it necessary, he shall be entitled to take action as indicated in clause	13	(iv)	also.

Adjustment	of	excess/over	payments: 13 (e) Excess/over payments as soon as they are discovered should be adjusted in the next running account bill of the contractor and in case the final bill has already been paid, the excess/over payment made shall be recovered from the Security Deposit of the contractor together with interest at 12 percent or such other percentages as KNNL may decide from time to time, from the date of such excess or over payment to the date of recovery.

###### Securities

- The Security deposit shall be provided to the Employer no later than the date specified in the Letter of Acceptance and shall be issued in an amount and form and type of instrument acceptable to the Employer. The Security deposit shall be valid until a date 30 days from the date of expiry of Defects Liability Period shall be valid until a date 30 days from the date of issue of the certificate of completion.

- The Additional Security deposit for unbalanced tenders (less than 90%) shall be provided to the Employer no later than the date specified in the Letter of Acceptance and shall be issued in an amount and form and type of instrument acceptable to the Employer. The additional performance security will be released proportionately to the bill amount till the contractor achieves progress of the entire cost of the work as per the agreement.

- The Security deposit for unbalanced tenders in case of contractor quotes rates above 125% of the estimated rates then the amount over and above 125 % will be withheld during the progress of work and same will be released until a date 30 days from the date of issue of the certificate of completion.

- Dues To Nigam, to be Set off Against Security Deposit: All compensation or other sums of money payable by the Contractor to Nigam under the terms of this contract may be realized or deducted from any Security Deposit payable to him or from the interest arising there from, or from

any sums which may be due or may become due by Nigam to the Contractor on any account whatsoever and in the event of his security deposit being reduced by reason of any such realization or deduction as aforesaid, the Contractor shall, within ten days thereafter, make good in cash any sum or sums which have been deducted from, or raised by sale of his security deposit or any part thereof.

- Release against Bank Guarantee and Interest Bearing Securities: The Security Deposit received upfront in the form of E-cash/Demand Draft will be converted into Interest Bearing Securities provided that the depositor has expressly desired this in writing. In case upfront security deposit is received in the form of Bank Guarantee same will be retained by the employer until the completion of defect liability period.

- Action When Whole of Security Deposit is Forfeited: In any case in which under any clause or clauses of this contract the contractor shall have rendered himself liable to pay compensation and/or penalty amounting to the whole of his security deposit including the amount deducted in installments from his bills as Further Security Deposit the Executive Engineer, on behalf of the Managing Director, KNNL, shall have power to adopt any of the following courses as he may deem best suited in the interest of Nigam.

(i) Forfeiture of Security Deposit: Without prejudice to Nigam's right to recover any loss from the Contractor under Clause 15 of sub-clause (f) (ii) and (iii) of the Contract, to rescind the Contract (of which rescission notice in writing to the Contractor, under the hand of the Executive Engineer shall be conclusive evidence) and in that case, the security deposit of the contractor including whole or part of the lump sum deposited by him and also the amount deducted from his bills as Security Deposit shall stand forfeited and be absolutely at the disposal of the Nigam.

  - Debiting Cost of Labor And Materials Supplied: To employ labour paid by the Nigam and to supply materials to carry out the work or any part of the work debiting the contractor with the cost of the labour and the price of the materials (as to the correctness of which cost and price the certificate of the Executive Engineer shall be final and conclusive against the contractor) and crediting him with the value of the work done, in all respects in the same manner and at the same rates as if it had been carried out by the contractor under terms of his contract, and in that case the certificate of the Executive Engineer as to the value of the work done shall be final and conclusive against the contractor.

  - Recovery of Extra Cost on Unexecuted Work: To measure up the work of the contractor due to breach of contract and to take such part thereof as is remaining unexecuted

out of his hands, and to give it to another contractor to complete it in which case any expenses which may be incurred in excess of the sum which would have been paid to the original contractor, if the whole work had been executed by him (as to the amount of which excess expenses the certificate in writing of the Executive Engineer shall be final and conclusive) shall be borne and paid by the original contractor and shall be deducted from any money due to him by the Nigam under the contract or otherwise or from his security deposit or the proceeds of the sale thereof, or a sufficient part thereof.

  - Action against Unsatisfactory Progress: If the contractor does not maintain the rate of progress as required under Clause 14 of special conditions of contract and if the progress of any particular portion of work is unsatisfactory even after taking action under Clause 14 the Executive Engineer shall be entitled to take action under Clause 15 at his discretion in order to maintain the rate of progress after giving the contractor 10 days’ notice in writing whereupon the contractor will have no claim for any compensation for any loss sustained by him owing to such actions.

  - No Compensation for Loss Sustained on Advance Action: In the event of any of the above courses being adopted by the Executive Engineer, the contractor shall have no claim to compensation for any loss sustained by him by reason of his having purchased, or procured any materials, or entered into any engagements, or made any advances on account of or with a view to the execution of the work or the performance of the contract. And in case the contract shall be rescinded under the provision aforesaid the contractor shall not be entitled to recover or be paid any sum for any work therefore actually performed by him under his contract unless and until the Executive Engineer shall have certified in writing the performance of such work and the amount payable in respect thereof, and he shall only be entitled to be paid the amount so certified.

###### Contractor to Remain Liable to Pay Compensation if Action is not taken

In any case in which any of the powers conferred upon the Executive Engineer by Clause 15 thereof shall have become exercisable and the same shall not have been exercised, the non-exercise thereof shall not constitute a waiver of any of the conditions hereof and such powers shall not withstanding be exercisable in the event of any future case of default by the contractor for which under any Clause hereof he is declared liable to pay compensation or penalty amounting to the whole of his security deposit and the liability of the contractor for past and future compensation or penalty shall remain unaffected.

###### Power to Take Possession of or Require Removal of or Sell Contractor's Properties:

In the event of the Executive Engineer taking action under Clause-14 (f) (i), (ii), (iii), (iv) & (v), he may, if he so desires, take possession of all or any tools, plant, materials and stores in or upon works or the site thereof or belonging to the contractor, or procured by him and intended to be used for the execution of the work or any part thereof, paying or allowing for the same in account at the contract rates, or in the case of contract rates not being applicable, at current market rates, to be certified by the Executive Engineer whose certificate thereof shall be final. In the alternative, the Executive Engineer may, after giving notice in writing to the contractor or his clerk of the works, foreman or other authorized agent, require him to remove such tools, plant, materials or stores from the premises within a time to be specified in such notice; and in the event of the contractor failing to comply with any such requisitions, the Executive Engineer may remove them at the contractor's expense or sell them by auction or private sale on account of the contractor and at his risk in all respects, and the certificate of the Executive Engineer as to the expense of any such removal, and the amount of the proceeds and expense of any such sale shall be final and conclusive against the contractor.

###### Quarries and Borrow Areas

All materials for construction which are not available from excavation shall be obtained from the quarries and borrow areas which shall be got approved from the Engineer. In no case, the quarry / borrow area shall be within the acquired area of KNNL. The KNNL will not make available any quarry or borrow area. The contractor shall himself explore the quarries and borrow areas required for the work and quote his rates for finished items of work in bill of quantities accordingly with all heads and lifts. The leads considered in the sanctioned estimate are for the estimate purposes and shall not be taken as the actual leads for materials during execution. No claims whatsoever shall be made, nor entertained for any extra leads over and above the leads considered in the estimate. No claim of any compensation shall be due to the contractor, on any account whatsoever, such as the quarries and borrow areas considered in the estimate being found unsuitable or inadequate in yield, the haulage routes reckoned being found unsuitable, the leads reckoned being found incorrect, the land owners obstructing the procurement and conveyance etc. The KNNL does not undertake to acquire lands for the quarries and borrow areas. It is the responsibility of the contractor to negotiate with land owners and acquire the lands to himself, either permanently or temporarily, and procure the

required materials. If the quarries /borrow areas do not give sufficient quantity of material,

contractor shall make his own arrangements for additional quaries/borrow areas, with the approval of the Engineer and bear cost of investigations and negotiations, all leads and lifts, cost of land etc. at his own expense without claim for any payment over and above his tendered rates.

###### Rates are all Inclusive

The rates quoted in bill of quantities shall be for finished items of work, complete in all respects, inclusive of all materials all tools and plant and all labour required for the work, all leads and lift and all incidental charges such as dewatering and desilting, diversion of rain and nala flows, diversion of traffic, initial and final clearance of site, providing labour amenities etc., and all taxes, levies & royalty charges etc., (excluding GST) complete. The rates shall hold good for all conditions of site, moisture, weather etc.

###### Income Tax

Deduction at source towards Income Tax will be made from the contractor’s bills at the rates prevailing at the time of payment as fixed by the Income Tax Authorities and the tax deductions certificate will be issued at the end of the financial year.

###### Dewatering, Desilting and Diversion of Flows

Any water encountered during the execution of work shall be suitably removed by baling out or pumping and any accumulated silt due to any reason whatsoever, during the execution of work shall also be removed and disposed off. All surface flows shall be diverted outside the work area by suitably channelizing the flows, by providing cross bunds and conducting the flows in pipes, conduits, etc., or by cross bunding and pumping etc depending upon the site conditions and exigencies of work. The cost of all such operations shall be considered as included in the quoted rates of the concerned finished items of work and shall not be separately paid.

###### Procurement of Cement, Steel and Blasting Materials

The responsibility of procuring all materials including cement, steel and explosives (and license thereof) shall rest with contractor only the material may be of standard quality and got tested from the department at the cost of the contractor.

###### Clearing the Site

The area to be occupied by the work and the quarries and borrow areas shall be cleared off all vegetations, including trees, roots, ant hills and other extraneous matters. The site shall be cleared to the full width of the works as directed by the Engineer-in-charge. No separate payment is admissible for clearing the site.

###### All Properties, Precious Stones, Metal and Relics to be Handed Over to Department

All gold, silver, oil or other materials of any description what-so-ever and other similar things that may be discovered on the site shall remain the property of the Government and the contractor shall duly intimate the Engineer-in-charge or any person duly authorized by him to receive such property from time to time.

###### Preservation of Trees

The contractor shall preserve all existing trees in and adjacent to the site which do not interfere with the construction as determined by the Executive Engineer.

###### Drawings and Working Details

The work shall be carried out strictly in accordance with the sanctioned plans and estimates and specifications and as per the instructions of the Engineer-in-charge, and no deviations or changes are permitted without the written order of the Engineer. The designs and drawings enclosed with the tender documents are only typical and tentative.

The contractor has to prepare design and drawing and the working details of the several components of works and got it approved by the competent authority. The approved drawing and working details of several component of work shall be made available at site of work and the contractor shall carry out the work in accordance with such working drawings and working details.

###### Omissions and Discrepancies in Drawings and Instructions

- In all cases of omissions, doubts or discrepancies in the dimensions or discrepancies in the drawings and item of work, a reference shall be made to the Executive Engineer, whose elucidation and elaboration shall be considered as authorised. The

contractor shall be held responsible for any error that may occur in the work through lack of such reference and precautions.

- The contractor shall be responsible for accuracy for all shapes, dimensions and alignments etc, of all the components of the work.

###### Taking Initial Levels, Marking Out the Layout and Fixing the Reference Lines

Before starting the work, the contractor or his authorized agent shall be present while taking levels of the ground along and across the portion of the Canal works, which the contractor has agreed to execute. He will further be required to sign the field book and also L sections and cross sections of the works based on the ground levels taken in token of acceptance of the ground levels before the commencement of work or fresh items of excavation below a preceding item. It shall be the responsibility of the contractor to mark the line-out as per directions of the Engineer-in-charge. The contractor or his duly authorised agent shall be present at the time of setting out giving profiles etc., and shall supply all the materials and sufficient number of mazdoors required for taking measurements of works, giving line out etc., at	his	cost. The stone masonry platforms and reference pillars etc., of suitable size as directed by the Engineer-in-charge with level top shall be built and maintained by the contractor at his cost till the completion of work along the reference lines to facilitate the mark out and layout of various appurtenant works.

###### Commencement of Work

The contractor shall not enter upon or commence any portion of the work except with the written authority of the Engineer, failing which the contractor shall have no claim to ask for measurement or payment for work and shall on the other hand, be responsible for any claim of damage that may arise due to such unauthorized commencement or entry.

###### Programme of Work

The Schedule of progress mentioned under Clause-13 (b) of special conditions of contract is only indicative. The contractor has to abide by the -Milestones for Scheduled Programs showing physical and fianacial programme (Bar Chart) as in Annexure-1.

###### Plant Layout, Contractors Office, Machine Yard, Labour Camp etc.,

Within a fortnight of the date of award of the contract, the contractor shall submit to the Executive Engineer for the approval of the department the layout of the construction plant and equipment for execution of work and also the location and layout of contractors office, machine yard, workshop, stores, storage yard, labour camps etc including the layout of necessary services such as water supply, sanitation etc.

###### Access Roads, Quarry Roads Etc.,

All haulage roads, access roads to work spot, quarry roads etc. and all diversion roads found necessary during construction shall be formed and maintained by the contractor at his cost to such standards as may be directed by the Engineer-in-charge as per the requirements of the work. The contractor should make himself thoroughly conversant with the conditions of existing public roads of the area and the existing arrangements for their maintenance. If any damage to the existing public roads is caused due to any natural or other causes or due to bad maintenance, KNNL will not be held responsible for the inconveniences caused to the contractor including any extra cost or temporary stoppage of work. The existing roads, constructed and maintained by the KNNL if any shall be used by all concerned contractors. No claim of compensation from any contractor shall be entertained on the excuse of non maintenance of such roads.

- Power	Supply	for	the	Works The contractor has to make at his own cost, all necessary arrangements for the supply of power required for the work and his camps from HESCOMs or from any other source. The KNNL will not undertake any responsibility with regard to power supply and no claims due to failure, or delay in supply of power or variations in voltage in supply will be entertained by the KNNL.

###### Water for Construction

Supply of water for construction and for drinking and for his camps shall be arranged for by the contractor at his own expense.

###### Amenities	to	Labours

Basic Amenities for laborers shall be provided as per prevailing Labor’s Act.

- Lands   for   the   Use   of   the   Contractors   Camp The contractor shall have to make his own arrangements with regard to land required for construction of quarters at the work spot. However, the KNNL at its discretion may make land available. In such a case necessary charges as fixed by the Engineer-in-charge will be levied.

- Undesirable    Person    to    be    Removed    from    Site The contractor shall not employ on site any person who is undesirable. If in the opinion of the Engineer-in-charge the person or persons at site of work employed on behalf of the contractor is/are considered undesirable, the Engineer-in-Charge shall notify the contractor to this effect and the contractor will be bound by the decision of the Engineer-in-Charge to remove such person or persons from the site of work and from the labour camp. The contractor shall not be entitled to any damage or loss on this account. On the contrary, the contractor shall be liable to compensate the KNNL for any loss or damage to the KNNL property caused by the employment of such person.

- Work	Order	Book A work order book shall be maintained by the contractor at the site and all instructions shall be entered in the book in ink. The contractor shall be responsible for obtaining all the orders entered in the work order book and he or his authorized agent shall sign, acknowledging the orders issued and shall carry out orders. Copies of the orders entered in work order book shall be submitted by the contractor to the concerned officer and to the Executive Engineer within two days, for their record.

###### Hindrance	Register

Hindrance Register to be included.

###### Labour	Statistics

The	contractor	shall	submit	daily	reports	on	the	following:

- Total	No.	of	labour	imported	into	working	area.

- Total No. of labour living in the working area.

###### Execution	of	Work	During	Night	Time

The work shall normally be carried out between 8 hours and 17 hours with a break of one hour

and when permitted during night period, the second shift shall be between 17 hours and 0 hours with a break of half an hour during night. When ordered to work at night, adequate provision for lighting the working area should be made by the contractor at his cost and got approved by Engineer-in-charge.

###### Medical Aid

- The contractor shall arrange all the necessary medical facilities for his staff and labour at his own cost and to the satisfaction of Engineer-in-Charge. The contractor shall arrange in his office, work shop, work site and camps facilities of clear portable treated water and arrange for proper drainage and proper disposal of sewage. He shall abide by the rules framed on this behalf by the Engineer-in-Charge or Health Officer of the project.

- The contractor shall also provide for medical supervision of his workers against epidemics. The contractor shall comply with all the directions given by Health Officer in this regard.

###### Engineer’s Supervision

All the works shall be carried out under the direction and to the satisfaction of the Engineer and the Engineer-in-Charge. Reference lines and reference bench mark will be set-up on the site by the Engineer-in-Charge based on which the contractor shall at his cost and responsibility, locate and establish lines and grades for all structures of the works according to the drawings and specifications. The contractor shall provide, at his own cost, all labour, materials and instruments that may be required for carrying out the check. Such a check shall not, however, absolve the contractor of his responsibility from carrying out the works strictly according to drawings and specifications and as per instructions issued to him by the Engineer-in-Charge during the execution of the work.

###### Engineer’s Decision

In respect of all matters which are left to the decision of the Engineer/Engineer-in-Charge, the Engineer/Engineer-in-Charge shall if required so by the contractor give the decision in writing.

###### Maintenance of Work During Execution

It is the responsibility of the contractor to maintain the work satisfactorily until it is handed over to the KNNL in a complete manner as per the terms of agreement. Any damages caused during construction to any part of the work due to any reason arising out of his own action or negligence shall be made good at the contractor’s expenses.

###### Return of KNNL Lands in Good Condition

The lands if any, made available to the contractor for his camps by the KNNL shall be handed back to the Executive Engineer within three months after the completion of the work under this contract. Also, no land shall be held by the contractor for a longer period than necessary and the contractor shall on due notice by the Executive Engineer vacate and return the land which the Executive Engineer may certify as no longer required by the contractor for the purpose of the work. The lands shall be returned in good condition.

###### Drainage of Quarries and Borrow Pits etc.,

The several quarries or borrow pits shall be interconnected to prevent stagnation of water and breeding of mosquitoes. Similarly, if any hindrance is caused by the contractor to the natural drainage of the lands handed over to him for the work and camps it shall be satisfactorily eased out.

###### Co-Operation with other Contractors

The Contractor will have to co-operate with the other agency/agencies working in the same or adjoining area. Any inconvenience or interruption in any portion of working area does not make the contractor eligible for any claims. In case of any disputes with the adjacent contractor the decision of the Engineer-in-Charge shall be final. No extra payment is admissible on this account.

###### Establishment of Field Laboratory

The Contractor should establish a full pledged testing laboratory for conducting all tests required for execution of work in accordance with Technical specification. The testing laboratory should be open for inspection and testing by the KNNL authorities.

###### No Claim to any Payment for Compensation for Deletion of Whole or Part of Work.

- If at any time after the execution of the contract documents, the Executive Engineer or other competent authority shall, for any reason whatsoever, require the whole or any part of the work, as specified in the tender, to be stopped for any period or require the whole or part of the work (i) not to be carried out at all or (ii) not to be carried out by the tendered contractor, he shall give notice in writing of the fact to the contractor who shall thereupon suspend or stop the work totally or partially as the case may be. In any such case, except as provided hereunder, the contractor shall have no claim to any payment of compensation whatsoever on account of any profit or advantage which he might have derived from the execution of the work in full but which he did not so derive in consequence of the full amount of the work not having been carried out, or on account of any loss that he may be put on account of materials purchased or agreed to be purchased, or for unemployment of labour recruited by him. He shall not also have any claim for compensation by reason of any alterations having been made in the original specifications, drawings, designs and instructions which  may  involve  any  curtailment  of  the  work  as  originally  contemplated. Payment   for   materials   already   purchased   or   ordered   by   contractor

- Where, however, materials have already been purchased or agreed to be purchased by the contractor before receipt by him of the said notice the contractor shall be paid for such materials, at the rates determined by the Executive Engineer or other competent authority provided they are not in excess of requirements and are of approved quality and/or shall be compensated for the loss, if any, that he may be put to, in respect of materials agreed to be purchased by him, the amount of such compensation to be determined by the Executive Engineer or other competent authority whose decision shall be final.

Labour charges during stoppage of work.

- If the contractor suffers any loss on account of his having to pay labour charges during the period during which the stoppage of work has been ordered under this clause, the contractor shall on application, be entitled to such compensation on account of labour charges as the Executive Engineer or other competent authority, whose decision shall be final, may consider reasonable. Provided that the contractor shall not be entitled to any compensation on account of labour charges if in the opinion of the Executive Engineer or

other competent authority, the labour could have been employed in the same locality by the contractor for

the whole or part of the period during which the stoppage of the work has been ordered as aforesaid.

Time	limit	for	stoppage	of	work

- The period of stoppage ordered by the Executive Engineer or other competent authority should not ordinarily exceed six months. Thereafter the portion of works stopped may be treated as deleted from this agreement if a notice in writing to that effect is given to the Executive Engineer or other competent authority by the contractor within seven days after the expiry of the above period. Execution	of	work	deleted (e)The portion of work thus deleted may be got executed from the same contractor on supplemental agreement on mutually agreed rates which shall not exceed current Schedule of Rates plus or minus tender percentage.

###### Action and Penalty in Case of Bad Work

If at any time before the security deposit is refunded to the contractor, it shall appear to the Executive Engineer or other competent authority or his subordinate in charge of the works that any work has been executed with unsound, imperfect or unskillful workmanship or with materials of inferior quality, or that any materials or articles provided by him for the execution of the work are unsound, or of a quality inferior to that contracted for, or are otherwise not in accordance with the contract, it shall be lawful for the Executive Engineer or other competent authority to intimate this fact in writing to the contractor and then notwithstanding the fact that the work, materials or articles complained of may have been paid for, the contractor shall be bound forthwith to rectify, or remove and reconstruct the work so specified in whole or in part, as the case may require, or if, so required shall remove the materials or articles at his own cost, and in the event of his failing to do so within a period to be specified by the Executive Engineer or other competent authority in the written intimation aforesaid, the contractor shall be liable to pay a penalty not exceeding one percent of the amount of the estimate for every day not exceeding ten days during which the failure so continues and in the case of any such failure the Executive Engineer or other competent authority may rectify or remove and re- execute the work or remove and replace the materials or articles complained of as the case may be, at the risk and expense in all respects of the contractor. Should the Executive Engineer or other competent authority for any valid reasons consider that any such inferior work or materials as described above is to be accepted or made use of, it shall be within his discretion to accept the same at such reduced rates he may fix thereof.

###### Work to be Open to Inspection-Contractor or Responsible Agent to be Present

a.  All works under or in course of execution or executed in pursuance of the contract shall at all times be open to the inspection and supervision of the Executive Engineer or other competent authority and his subordinates, and the contractor shall at all times during the usual working hours, and at all other times at which reasonable notice of the intention of the Executive Engineer or other competent authority or his subordinate to visit the work shall have been given to the contractor, either himself be present to receive orders and instructions or have a responsible agent duly accredited in writing present for the purpose. Orders given to the contractor's duly authorised agent shall be considered to have the same force and effect as if they had been given to the contractor himself.

###### Notice to be Given Before Work is Covered Up

The contractor shall give not less than five days notice in writing to the Executive Engineer or his subordinate in charge of the work before covering up or otherwise placing beyond the reach of measurement of any work in order that the same may be measured, and correct dimensions thereof taken before the same is covered up or placed beyond the reach of measurement, and shall not cover up or place beyond the reach of measurement, any work without the consent in writing of the Executive Engineer or other competent authority or his subordinate in charge of work; and if any work shall be covered up or placed beyond the reach of measurement without such notice having been given or consent obtained, the same shall be uncovered at the contractor's expense, and in default thereof no payment or allowance shall be made for such work or for the materials with which the same was executed.

###### Contractor Liable for Damage Done and for Imperfections for Twenty Four Months after Certificate of Completion

If the contractor or his workmen or servants shall break, deface, injure or destroy any part of a building, structure, embankment or canal in which they may be working, or any building, structure, embankment canal, road, fence, enclosure or grassland or cultivated ground contiguous to the premises on which the work or any part thereof is being executed, or if any

damage shall be done to the work, while it is in progress from any cause whatever or if any imperfections become apparent in it within 18 months of the grant of a certificate of completion, final or otherwise, by the Executive Engineer or other competent authority the contractor shall make good the same at his own expense, or in default, the Executive Engineer or other competent authority may cause the same to be made good by other workmen, and deduct the expenses (of which the certificate of the Executive Engineer or other competent authority shall be final) from any sums that may be due or may thereafter become due to the contractor, or from his Security Deposit or the proceeds of sale thereof, or of a sufficient portion thereof.

###### Measures for Prevention of Fire

The contractor shall not set fire to any standing jungle, trees, brushwood or grass without a written	permit	from	the	Executive	Engineer. When such permit is given, and also in all cases when destroying cut or dug up trees, brushwood, grass, etc., by fire, the contractor shall take necessary measures to prevent such fire spreading to or otherwise damaging surrounding property.

###### Liability of Contractor for any Damages done in or Outside Work Area

Compensation for all damages done by contractor or his men whether in or beyond the limits of KNNL property including any damage caused by spreading of fire mentioned in Clause 56 shall be estimated by the Executive Engineer, and the estimate of the Executive Engineer, subject to the decision of the Superintending Engineer on appeal, shall be final and the contractor shall be bound to pay the amount of the assessed compensation on demand failing which the same will be recovered from the contractor as damages in the manner prescribed in Clause-15 or deducted by the Executive Engineer or other competent authority from any sums that may be due or become due from KNNL to the contractor under this contract or otherwise. The contractor shall bear the expenses of defending and action or other legal proceedings that may be brought by any person for injury sustained by him owing to neglect of precautions to prevent the spread of fire and shall pay any damages and cost that may be awarded by the court in consequence.

###### Employment of Female Labour

The employment of female laborers on works in the neighborhood of soldier's barracks should be avoided as far as possible.

###### Work on Notified Holiday

No work shall be done on any notified holiday without the sanction in writing of the Executive Engineer or other competent authority.

###### Approval of Executive Engineer necessary for Changing the Constitution of a Firm or Before Entering into Partnership Agreement- Consequences of not Obtaining Prior Approval

Where the contractor is a partnership firm, the previous approval in writing of the Executive Engineer shall be obtained before any change is made in the Constitution of the Firm. Where the Contractor is an individual or a Hindu undivided family business/concern, such approval as aforesaid, shall likewise be obtained before the contractor enters into any partnership agreement where under the partnership firm would have the right to carry out the work hereby undertaken by the contractor. If previous approval as aforesaid is not obtained, the contract shall be deemed to have been assigned in contravention of hereof and the same action may be taken and the same consequences shall ensure as provided.

###### Contractor to Pay Compensation under Workmen's Compensation Act

The contractor shall be responsible for and shall pay any compensation to his own workmen payable under the Workmen's Compensation Act. 1923 (VIII of 1923) (hereinafter called the said Act) for injuries caused to the workmen. If such compensation is paid by KNNL as principal under sub-section (1) of Section 12 of the said Act on behalf of the contractor, it shall be recoverable by KNNL from the contractor under sub-Section (2) of the said Section. Such compensation shall be recovered in the manner laid down in Clause 1 above. Contractor   to   pay   expenses   of   providing   medical   aid   to   workmen

(b) The contractor shall be responsible for and shall pay the expenses of providing medical aid to any workmen who may suffer a bodily injury as a result of an accident. If such expenses are

incurred by KNNL, the same shall be recoverable from the contractor forthwith and be deducted without prejudice to any other remedy of KNNL from any amount due or that may become due to the contractor.

###### Contractor to Provide Personal Safety Equipment, First Aid Apparatus, Treatment etc.

The contractor shall provide all necessary personal safety equipment and first aid apparatus for the use of the persons employed on the site, and shall maintain the same in good condition suitable for immediate use, at any time and shall comply with the following regulations in connection therewith—

- The workers shall be required to use the equipment so provided by the contractor and the contractor shall take adequate steps to ensure proper use of the equipment by those concerned.

- When work is carried on in proximity to any place where there is a risk of drowning, all necessary steps shall be taken for the prompt rescue of any person in danger.

- Adequate provision shall be made for prompt first-aid treatment of all injuries likely to be sustained during the course of the work.

###### Minimum Age of Persons Employed by Contractor

- No contractor shall employ

  - any person who is under age of 18 years. or as prescribed in the prevailing

“Prevention of child labour act”

  - who does not produce a valid certificate of vaccination against small-pox in respect of himself/herself as well as the members of his/her family.

Employment of donkeys and other animals

- No contractor shall employ donkeys or other animals with breaching of string or thin rope. The breaching must be atleast three inches wide and should be of tape.

- No animals suffering from sores, lameness or emaciation or which is immature shall be employed on the work.

- The contractor shall provide pure potable drinking water facilities to the workers. similar amenities shall be provided to the workers engaged on large works in urban area.

Removal of person not satisfying conditions (a) to (c)

- The Executive Engineer or other authority is authorised to direct the removal or to remove through his own agency, from the work any person referred to in sub-clauses

(a) to (c) above not satisfying these conditions and no responsibility shall be accepted by the KNNL for any delay caused in the completion of the work by such directions for removal.

Payment of fair and reasonable wages by contractor

- The contractor shall pay fair and reasonable wages which shall not be less than the minimum wages fixed by Government from time to time to the workmen employed by him in the contract undertaken by him. In the event of any dispute arising between the contractor and his workmen on the ground that the wages paid are not fair and reasonable the dispute shall be referred without delay to the Executive Engineer or other competent authority, who shall decide the same. The decision shall not in any way affect the conditions in the contract regarding the payment to be made by KNNL at the agreed tender rates.

- The Contractor should keep his employees covered under the provision of the EPF Act and the employers state insurance Act. The contractor shall keep the KNNL its Employees/ Officers indemnified from any loss or damages suffered by KNNL/staff. Officers for any violation of the provision of the said Act by the contractor notwithstanding the above the KNNL shall have the right/remedy available to it under section B (a) of the Employees PF and Miscellaneous Act and the relevant provisions of the Employees State Insurance Act.

###### Employment of Scarcity Labour etc.,

- If Government declares a state of scarcity or famine to exist in any village situated within 16 kilometers (10 miles) of the work, the contractor shall employ upon such parts of the work as are suitable for unskilled labour, any person certified to him by the

Executive Engineer, or by any person to whom the Executive Engineer may have delegated this duty in writing to be in need of relief and shall be bound to pay to such persons wages not below the minimum which Government may have fixed in this behalf. Any dispute which may arise in connection with the implementation of this clause shall be decided by the Executive Engineer or other competent authority whose decision shall be final and binding on the contractor.

- The contractor shall employ any famine, convict or other labour of a particular kind or class, if ordered in writing to do so by the Executive Engineer or other competent authority.

- Contractor not Entitled to any Claim or Compensation for Delay in Execution   of   Work   Due   to   Water   in   Borrow   Pits The contractor shall not be entitled to claim compensation if there is any delay in the execution of the work on account of water standing in borrow pits and compartments. The rates of borrowing earth and of excavation hold good for all situations such as hard or cracked soils, excavation in mud, subsoil water or water standing in borrow pits and no claim for extra rate shall be entertained, unless otherwise expressly specified.

###### Method	of	Payment	of	Bills

Payment to contractors shall be made by cheques/online payment.

- Set  Off  Against  any  Claim  of  KNNL/  under  other  Contracts Any sum of money due and payable to the contractor (including the security deposit returnable to him) under this contract may be appropriated by the KNNL and set off against any claim of KNNL/ Government in respect of a payment of a sum of money arising out of or under any other contract made by the contractor with the KNNL/Government.

###### Rates Excluding of GST, etc.,

- The rates to be quoted by the contractor must be exclusive of GST

Contractor to pay quarry fees, royalty, etc.,

- All quarry fees, royalties, octroi dues levied by the State Government or any local body or authority and ground rent, if any, charged by the Executive Engineer for stacking materials, should be paid by the contractor.

###### Contractor to Obtain Labour etc., from nearest Employment Exchange

The contractor should as far as possible obtain his requirement of labour, skilled and unskilled from the nearest Employment Exchange. The contractor should give preference to the employment of released bonded labour on the work entrusted to him.

###### Dues to be Recovered as if they were Arrears of Land Revenue

All money due from the contractor under this contract may be recovered by Government without prejudice to the other remedies, as if they were arrears of Land Revenue.

###### Contractor to Comply with the Provisions of Apprentice Act

The contractor shall comply with the provisions of the Apprentice Act 1961 and Rules and Orders issued there under from time to time. If he fails to do so, his failure will be a breach of contract and the Superintending Engineer may at his discretion cancel the contract. The contractor shall also be liable for any pecuniary liability arising on account of any violation by him of the provisions of the Act.

###### Compliance with the Provision of Hoarding and Profiteering Prevention Act

If the price quoted exceeds controlled price or price permissible under Hoarding and Profiteering Prevention Act, the contractor will specifically mention this fact in his tender along with the reasons for quoting such higher price. The purchaser at his discretion will in such case exercise the right of revising the price at any stage so as to conform to the controlled price or the price permissible under the Hoarding and Profiteering Prevention Act. This discretion will be exercised without prejudice to any other action that may be taken against the contractor.

###### Other Terms and Conditions.

- Joint venture/Tie-up is acceptable. The intending bidder can submit bids as an Individual/ Joint Venture bidder along with Tie –up of pump manufacturer. The Tie –up is to be formed prior to the bidding. In case of Joint Venture bidding, the lead partner should have at least 51% partnership.

- The intending bidders shall submit bids as an Individual bidder along with Tie –up of pump manufacturer. The Tie –up is to be formed prior to the bidding.

However, tenders from a Tie-up proposed in this bid, the bidder shall upload an agreement with only one pump manufactures on Rs 200-00 stamp paper in the prescribed format which shall be concluded prior to bidding and enclosed to the bid document. For proof of the Tie up in the Technical bid in the prescribed format under section 2 of instruction to bidder (multiple tie –up not allowed).

NOTE:- The criteria above applies to the Individual bidder/Firm. Certificate regarding the same duly signed by an officer not below the rank of the Executive Engineer and countersigned by the superior officer not below the rank of Superintending Engineer should be submitted along with the technical bid.

- Bidders shall not be under a declaration of ineligibility for corrupt and fraudulent practices issued by any State Government / Government of India /Union Territory.

- It shall be the responsibility of the Bidder to ensure credit of Tender Processing Fee and EMD into the respective receiving bank accounts of e-Procurement on or before the last date and time of bid submission.

- The bidder is required to ensure browser compatibility of the computer well in advance to the last date and time for receipt of tenders. The departments shall not be responsible for non-accessibility of e-Procurement portal due to internet connectivity issues and technical glitches at bidder's end.

- EMD Payments through e-Payment mode shall be made as one single transaction and payments made in part are liable for rejection.

- Bidder shall pay Contract Management Module processing fees as per e-procurement

norms.

- Conditional tenders will not be accepted.

- The under signed reserves the right to either postpone or to cancel the entire process of the tender without assigning any reasons.

- Defect Liability period should be for a period of 2 years after commissioning and Operation & Maintenances period should be for a period of 5 years after successful completion of Defect Liability Period.

- The tenderer shall bear all costs associated with the preparation and submission of his tender, and the employer will in no case be responsible and liable for those costs.

- The Tender processing fee shall not be refundable.

- All Government orders/circulars prevailing and issued from time to time related to tenders shall be applicable.

- All scanned documents to be uploaded shall be in original and the Executive Engineer reserves the right to verify the documents before approval.

- All safety precautions, warning signs, night illumination, reflectors, deployment of security guards has to be ensured so that no untoward incident happens on account of negligence or any project activity. Contractor should indemnify the client to that extent.

- All the items in the tender include all lead, lifts, loading unloading, transportation, dewatering and desilting, labor, hire charges of machinery curing for concrete works, cost and conveyance of all material and all other such incidental charges necessary for successful completion of works as per the detailed technical specification and direction of Engineer in charge of this work.

- Amount put to tender also includes cost of cement, Steel and other materials for finished item of work.

- All precautions should be taken by the contractor so that there are no damages to such public/ private properties.

- Contractor should also take all precautions to ensure that no damage is caused to the existing structures which have been constructed by other agencies/Nigam during project execution. If any damage is caused, it has to be rectified at his own risk and cost.

- Contractor should take all precautionary measures to avoid any damage to the utilities during excavation as well as utility shifting. To that extent the contractor should indemnify the client.

- Contractor should follow strictly the prevailing rules of labor act.

- Further particulars, if any, required by the Contractor can be had from the office of the Executive Engineer, KNNL, No 5 Bhadra Canal Division, Davanagere., during office hours on all working days.

- The intending bidders are requested to note that they should abide by the detailed instructions and conditions contained in the Standard Tender documents.

- The necessary certificates/ documents in support fulfilling qualification criteria stipulated separately shall be scanned and attached to e-procurement document. The original document shall be produced at the time of opening of technical bid /during evaluation of Technical Bid.

- The evaluation of the technical bid will be done based on the information provided by the contractor as per uploaded documents, duly verified if necessary. If the employer finds that any certificates/ information furnished is false, such bidders will be disqualified, barred from participation in the bid and his EMD will be forfeited.

- The land acquisition proposals are to be prepared as per latest Land Acquisition Act in the prescribed format by the bidder.

- Engaging third party for quality control assessment is mandatory as per G. O. No. FD 55 Pro Cell 2004 dated 17/02/2005 and G.O. FD 205 EXP – 12/2021 dated 26/04/2021 apart from the KNNL quality control and field tests. The contractor should co-operate with both Quality control authorities and the third party.

- Defect Liability period should be for a period of 2 years after commissioning and Operation & Maintenances period should be for a period of 5 years after successful completion of Defect Liability Period.

- The successful bidder shall submit the tie-up agreement at the time of concluding the agreement for the work in the format prescribed in the bid document, failing which the EMD amount will be forfeited and contract will be rescinded at his risk and cost and liable for penal action including black listing. If one of the JV is pump manufacturer then tie-up with pump manufacturer is not necessary.

- The tie-up arrangement will be generally permitted with the pump manufacturer whose data parameters are uploaded and in conformity with the details submitted in the data sheet of the bid document at the time of bidding. However, the successful bidder will be permitted to have tie-up agreement with other pump manufacturer provided his data parameters are unaltered with the uploaded parameters.

- During technical evaluation KNNL find that any certification / information is false, such bidders will be disqualified and barred from participation in the bid their EMD will be forfeited.

- The bid shall be technically evaluated based on the specifications indicated in Section-6

titled “Contract Data and Scope of work” in bid document.

- The Bidder/JV partner/ Tie up partner shall not be under Corporate Debt Restructuring (CDR) / Strategic Debt Restructuring (SDR) or Bureau of Industrial and Financial Reconstruction (BIFR) in the last 5 Years prior to bid submission date. In this regard, the Bidder shall submit along with Bid, a certificate from their Statutory Auditor with a declaration that, the Bidder is not under CDR / SDR or BIFR.

- Bids not satisfying minimum duty point parameters, efficiency parameters of pumps and motors and velocity parameters as specified in bid document shall be rejected.

- During technical evaluation, if the employer finds that any certificates / information furnished is false, such bidders will be disqualified and barred from participation in the bid.

- If any bidder fails to satisfy the conditions mentioned above, such bids will be rejected and their financial bids will not be opened.

- The work of the construction of transmission line should be got done through a Government Licensed, Super Grade Electrical contractor CEIG approved, who have the experience of carrying out such works. They should have constructed at least one similar single power line equal to 80% of the length of power line for the work tendered in a single contract. The details of the transmission line construction contractor with registration certificate and certificates of experience signed by an officer of not below the rank of Executive Engineer of KPTCL shall be submitted for KNNL’s verification post award of the work.

- The Bidder to participate in the tender under single bid basis only. Any violation will attract disqualification of the bid.

- The contractor/authorized signatory should attach his/her scanned signature to the Schedule-B before uploading and also submitting their tenders.

- If any of the dates mentioned above happen to be a general holiday, the next working day holds good.

- The diameters of the rising main and thickness of the rising main shall not be less than the figures indicated in the enclosed schematic diagram. Further any discrepancies in the above shall not account to financial implications to the employer.

- If the percentage quoted by the contractor for the work is below ninety percent of the updated recast estimated amount put to tender, then the contractor shall furnish an “additional performance security” in the form of Bank Guarantee for an amount equivalent to the difference between the cost as per quoted percentage and 90% of the updated cost put to tender. In case of contractor quoting above 125% of updated cost put to tender, then the over and above 125% of the updated cost put to tender will be withheld during the progress of work. The additional performance will be released proportionately to the bill amount till the contractor achieves progress of the entire cost of the work as per agreement. The withheld amount in the later case will be released only after entire work contracted is fully completed and so certified by the Executive Engineer. (If BG submitted while issuing fresh BG or extending any existing BG, claim period of a minimum one year from the date of expiry of validity period of BG is to be specified invariably)

- The contractor is responsible for any damages due to natural calamity. The Government or Nigam will not give any compensation for until the completion of maintenance period.

- The intending bidder/firm/company are advised to visit the work site before submission of the tenders.

- The intending bidder should note that if they happen to be lowest bidder and awarded with the work, during the current financial year i.e. 2022-23, they should start only the Jack well work. Only after 50% completion of the Jack well work, the remaining works should be started by the agency.

- Typographical errors if any will not be the ground for any claims by the bidder/firm/company.

- All the works are to be carried out as per the Standard specification Issued from time to time.

- The eligibility clauses and sub contract clause in all the tender documents used for procurement of goods, works and services including consultancy services as detailed below (as per G. O. FD 455 Exp-12 2020 Bengaluru dated 25/08/2020):

  - Any bidder from a country which shares a land with India will be eligible to bid in this tender only if the bidder is registered with the Competent Authority.

    - “Bidder” (including the term ‘tender’, ‘consultant’ or’ service provider’ in certain contexts) means any person or firm or company, including any member of a consortium or joint venture (that is an association of several persons, or firms or companies), every artificial juridical person not falling in any of the descriptions of bidders stated hereinbefore, including any agency branch or office controlled by such person, participating in a procurement process.

    - “Bidder from a country which shares a land border with India” for the purpose

of this Order means:-

      - An entity incorporated, established or registered in such a country; or

      - A subsidiary of an entity incorporated, established or registered in such a country ; or

      - An entity substantially controlled through entities incorporated, established or registered in such a country; or

      - An entity whose beneficial owner is situated in such a country; or

      - An Indian (or other) agent of such an entity; or

      - A natural person who is a citizen of such a country; or

      - A consortium or joint venture where any member of the consortium or joint venture falls under any of the above

    - I.    The beneficial owner for the purpose of above clause will be as under:

- In case of a company or Limited Liability Partnership, the beneficial owner is the natural person(s), who, whether acting alone or together, or through one or more juridical person, has a controlling ownership interest or who exercise control through other means.

Explanation-

  - “Controlling ownership interest” means ownership of or entitlement to more than

twenty-five percent of shares or capital or profits of the company;

  - “Control” shall include the right to appoint majority of the directions or to control the management or policy decisions including by virtue of their shareholding or management rights or shareholders agreements or voting agreements;

- In case of a partnership firm, the beneficial owner is the natural person(s) who, whether acting alone or together, or through one or more juridical person, has ownership of entitlement to more than fifteen percent of capital or profits of the partnership;

- In case of an unincorporated association or body of individuals, the beneficial owner is the natural person(s), who, whether acting alone or together, or through one or more juridical person, has ownership of or entitlement to more than fifteen percent of the property or capital or profits of such association or body of individuals;

- Where no natural person is identified under (i) or (ii) or (iii) above, the beneficial owner is the relevant natural person who holds the position of senior managing official;

- In case of a trust, the identification of beneficial owner(s) shall include identification of the author of the trust, the trustee, the beneficiaries with fifteen percent or more interest in the trust and any other natural person exercising ultimate effective control over the trust through a chain of control or ownership.

    - An Agent is a person employed to do any act for another, or to represent another in dealings with third person.

    - A certificate for having read the above clauses is required to be submitted / uploaded by the tenderer separately in the following format:

“I have read the clause regarding restrictions on procurement from a bidder of a country which shares a land border with India; I certify that this bidder is not from such a country or, if from such a country, has been registered with the Competent Authority. I hereby certify that this bidder fulfils all requirements in this regard and is eligible to be considered. (Where applicable, evidence of valid registration by the Competent Authority shall be attached.)”.

    - IN CASES WHERE SUB CONTRACTING IS PROVIDED:

A certificate is required to be submitted / uploaded by the Tenderer in respect of sub-contracting separately in the following format:

“I have read the clause regarding restrictions on procurement from a bidder of a country which shares a land border with India and on sub-contracting to contractors from such countries; I certify that this border is not from such country or, if from such a country, has been registered with the Competent Authority and will not sub-contract any work to a contractor from such countries unless such contractor is registered with the Competent Authority. I hereby certify that this bidder fulfils all requirements in this regard and is eligible to be considered. [Where applicable, evidence of valid registration by the Competent Authority shall be attached.]”

###### Terms of Payments

- Terms of Payment:-

  - Payment Towards Civil Works

Payments will be made for civil works to the extent of 95 % of the value of the finished work done by the contractor. The balance 5 % of such bills will be retained in the hands of the employer subject to the maximum of 5% of contract value.

  - Payment toward SUPPLY AND erection of EQUIPMENT AND plants: no Payments shall be released towards electromechanical equipment’s till civil works of jack well cum pump house is complete up to 60%.

- 50% of the price breakup furnished with schedule "B' on prorata basis on receipt of equipment at site.

- 30% of the price breakup furnished with schedule "B' on prorata basis on erection of equipment and plant in final position.

- 10% of the price breakup furnished with schedule "B' on prorata basis of each item after successful commissioning of entire scheme and 5% on completion of entire scheme and Balance 5% to be retained till final payment.

  - in case of item of supplying, laying, jointing, testing and commissioning of pipes and specials the rates quoted shall he paid in part as under:

| Sl. No. | Description | Rate of Payment |
| --- | --- | --- |
| 1. | Supplying MS/HDPE/DI Pipes and specials including necessary shop tests and Stacking at Contractors’ yard at site & transporting the pipes to work spot. | 40 % of the quoted rate for pipes and others |
| 2. | Laying, jointing and testing as directed and as per specifications. | 45 % of the quoted rate for pipeline. |
| 3. | On satisfactory commissioning. | 10 % of the quoted rate for pipeline.. |
| 4. | Final payments | 5% at the time of final bill |

NOTE: The amount due under Sl. No.1 will be paid as follows:

- For the first and second consignment of pipes: Payment when the pipes and specials are accepted in the pipe yard by the Engineer.

- For the third and subsequent consignments: Payment when the pipes and specials are accepted in the pipe yard by the Engineer and at least 50% of the pipes and specials supplied on previous consignments are laid, jointed and tested to the satisfaction of the Engineer.

No separate payment for dewatering shall be made while executing any of the items of works and contractors shall quote accordingly.

- Guarantee / Warranty:

The Contractor shall warrant that all the equipments and works executed in accordance with the contract are free from defects in material and workmanship for a period of (60) Sixty calendar months commencing after satisfactory commissioning  and issue of completion certificate. The contractor shall submit warranty / guarantee certificates in respect of all equipments/ installations before requesting for issue of completion certificate.

Contractor shall undertake to replace any defective parts in the equipment at his own cost under normal operation and arising solely from faulty design, material and/or workmanship during five years warranty period.

- Operation & Maintenance

Contractor shall be responsible for proper operation of the installations during 5 years maintenance period, by engaging suitable qualified and sufficient manpower. The employer shall arrange necessary power supply and water required for operation.

Successful bidder shall be responsible for making payments towards electricity charges against bill received from supply agency and same is reimbursable by KNNL during maintenance period. Contractor shall be responsible to arrange all consumable items like, Lubricants, Gland packings and any other consumables.

The spares & tools shall be kept in stock and handed over to employer for their use after successful completion of 5 years maintenance period. In case of emergency, employer may permit use of spare parts from the stock subject to replacement by contractor at the earliest time.

The Contractor shall be responsible for O & M of the entire LIS system for a period of 5 years from the date of issue of completion certificate.

The contractor should be responsible for O & M of the Aycut roads for the period of 2 years from the date of completion of phase-II works.

He shall provide necessary experienced engineering personnel, skilled and unskilled work force to operate & maintain the pump house and other systems ensuring smooth operation and maintenance of equipments.

The intake channel shall be desilted every year. The pumps shall be overhauled at least twice in a period of 5 years. All the cost towards preventive and breakdown maintenance shall be to the account of the contractor. All the electrical protection relays shall be got checked and calibrated every year. The insulation value of the transformer oil shall be checked every year and corrective actions shall be taken wherever necessary.

Painting of the building shall be done at the end of 4th year of the O & M Contract. The equipment painting shall be done twice during the O & M period. Jungle clearance around the pump house and the rising mains shall be done every year.

- Replacement of Defective Parts and Materials

In case, contractor fails to attend to the defects during two years warranty period, employer may, on giving the contractor seven(7) days notice in writing of his intentions to do so, proceed to get the defective parts replaced or repairs carried out at the cost of the contractor and recover the same from the security deposit or any amounts due to him.

BIDDER shall comply with the pump parameters as specified.

  - BID EVALUATION FACTORS

The efficiency is reckoned as wire to water, which means the losses in pump, coupling, vertical column, and filters all included.

For the purpose of Bid evaluation and present performance guarantee, the duty point for pump sets shall be considering the total discharge requirement as detailed below –

| Description | Details |
| --- | --- |
| Discharge (cumecs) | 0.028 Cumecs(0.992 Cusecs) |
| Static head (m) | 27.00 m |
| Friction losses in pipe and Other minor Losses in pipe (m) | 27.00 m |
| Length of Rising Main (Km) (Approx) | 4.80 Km |

The friction and minor losses in the pipes mentioned above is only for evaluation purposes. However, the successful bidder has to submit final calculations of design head, pump capacities etc., after detailed survey of the pipe alignment up to Delivery Chamber at Ch: 4+800   m.

The bidder shall compute the total losses considering the above data. The bidder shall indicate the minimum guaranteed pump efficiency at the above specified duty point. For bid evaluation, loading will be at as per norms, per pump set for each KW differential among various bids received in the guaranteed power input to motor at the duty point.

Bidder shall furnish motor efficiency which shall not be subject to any tolerance and guaranteed power input to the motor corresponding to this efficiency.

Power input to pump and motor shall be calculated as follows:

Power input to pump = motor out put = (Q x H) / (367.2 x ep) Power input to motor in KW	= (Motor out put) / (em) Where

Q	=	in M3 / hr.

H	=	in m. head plus losses in the pump and hydraulic system up to the delivery pond. ep	=		pump efficiency at duty point

em	=	Motor efficiency at duty point

The purchaser reserves the right to reject the motor if the efficiency of the motor at the duty point and full load during test is less than the guaranteed value, even if the power input to motor is within the guaranteed value.

The bidder shall note that the duty point indicated is only for the purpose of evaluation. The bidder shall arrive at the kW rating of the motor such that the pump sets shall be capable of meeting the head and discharge requirements.

- Penalty for Shortfall in Performance: Pumps

For each KW differential in the actual motor input over the guaranteed motor input at duty point indicated in the technical specifications (without any further tolerance), penalty will be levied at as per norms per kW per pump set.

For fractional KW losses exceeding guaranteed values, pro-rata rates will be applicable

For this purpose the power input measured during performance test on the full size pump at the employer’s

site will be considered.

Should the performance test results deviate from the guaranteed values subject to the tolerances indicated, the Contractor shall correct his equipment at no extra cost to the Engineer and repeat the performance tests within a reasonable period as agreed to by the Engineer. As regards the power consumption, if the Contractor fails to meet the guaranteed values, the Engineer will levy a penalty as indicated under this Clause. However, if the deviation in power consumption exceeds 5% of the guaranteed value or the Contractor is unable to meet the guarantee for items under correction, the Engineer retains the option to reject the equipment in which case contractor shall replace the entire equipment with one that meets the guaranteed values.

- Capitalisation of Losses: Power Transformers

The no-load loss in Kilowatts at rated voltage and rated frequency and the load loss in Kilowatts at rated output, rated voltage and rated frequency specified and at a temperature of 75 deg. C shall be guaranteed.

For the purpose of comparison of tenders, the minimum of the losses quoted by the bidders will be considered as base and the difference over and above the minimum will be capitalized and added to quoted price

Load losses at 25%, 50%, 70%, 90%, 100% & 110% rated load & rated voltage shall also be indicated in the bid.

The Bidders shall note that the value assigned for the capitalisation of losses is based on the present worth.

- Penalty for Non-Fulfilment of Guaranteed Losses

The quoted load losses & iron losses will be compared with the guaranteed load loss and iron loss offered by the bidders & loaded to the quoted cost.

The values of no-load and load losses obtained during tests will be compared with the guaranteed figures as per Clause 24.1. In case the test values exceed the guaranteed figures (without tolerance), penalty will be imposed as per norms

For fractional KW losses exceeding guaranteed values, pro-rata rates will be applicable

- Performance within Maintenance Period

The purchaser reserves the right to carry out further test to check the performance and efficiency of the plant at the end of maintenance period. Adjustments to the plant as may be considered part of normal operating routine shall be carried out prior to these tests.

Should the results of such repeat tests carried out by the Purchaser indicate that performance values deviate from Guaranteed value or the power consumption exceeds 1.0 % of the guaranteed value, then the contractor shall be given opportunity to take corrective measures and carry out further test, all at his own expense. Should the test indicate performance and Power consumption values below the guaranteed value then a reduction in the contract price may be issued by the Engineer.

# SECTION – 6

# CONTRACT DATA

### SECTION 6: CONTRACT DATA

###### Items marked "N/A" do not apply in this Contract.

The following documents are also part of the Contract:	Clause Reference

- The Schedule of Operating and Maintenance Manuals	[48]

- The Methodology and Program of Construction	[25]

- Site Investigation Reports	[14]

- The Schedule of Key and Critical Equipment to be deployed

on the work as per agreed program of construction.	[25] The Employer is:

Name: The Executive Engineer,

KNNL,No 5 Bhadra Canal Division, Davanagere.

Name of authorized Representative: 	 The name and identification number of the Contract is as under:

“Survey, Investigation, design, Supply, Installation, Testing and Commissioning of Lift Irrigation system (Head Works consisting of Intake canal, Jack well cum pump house, Power supply including substations and Transmission lines, Rising Main including Thrust Block, Valve Chambers,  Delivery chamber, approach roads etc) to Filling up of Kogaluru percolation tank coming under minor irrigation department from Kogaluru tank in Channagiri Taluk Davanagere  District on Turn-key basis” (Indent No.      )

The work consist of	The broad scope of work is enclosed under Data Sheet. (Brief summary, including relationship to other contracts under the project)

The start date shall be the date of issue of notice to proceed with the work.   [1.1]

The Intended Completion Date for the whole of the Works is 11 MONTHS INCLUDING MONSOON with the following milestones -	[17, 26]

Milestone dates:

| Milestone dates | Physical works to be completed | Period from the date of issue of Notice to proceed with the work |
| --- | --- | --- |
| Milestone 1 | Submissions of Design Drawings approvals of Equipments placing orders to manufacturers. Delivery of equipments at site including spares and Tools.-20% | 3 months |
| Milestone 2 | Civil Works – Intake forebay, Jackwell cum pump house, Electrical substation, control room and stores, approach road Etc-25% | 3 months |
| Milestone 3 | Erection of pumps, EOT crane, -and delivery pipes, valves, Manifold & delivery pipes, Electrical works in the pump House-25% | 3 months |
| Milestone 4 | O&M manual, Factory Held test report acceptance test Guarantee Warranty Certificate & KPTCL approvals, commissioning and PG test-30% | 2 months |

Refer Bar chart enclosed in Annexure I of Broad Scope of Work.

The Site Possession Date is: 7 days + from the date of issue of work order	[21] The Site is located at Channagiri Taluk & and is defined in Index map.

The Defects Liability Period is 60 months	[31]

Insurance requirements are as under:	[13]

| Sl No | Type of Cover | Minimum cover for Insurance |
| --- | --- | --- |
| (i) | Works and of Plant and materials | The sum stated in the Agreement plus 20% |
| (ii) | Loss or damage to equipment | Full replacement cost |
| (iii) | Loss or damage to property of Third Party | Full replacement cost |
| (iv) | Personal injury or death insurance (a) for Third Party | Rs.20 lakhs to cover 4 persons @Rs.5 lakhs each. |
|  | (b) for Contractor’s employees or labour | In accordance with the statutory requirements applicable to Karnataka |

The liquidated damages for the whole of the works Deleted. Refer Sl. No.13 of Special Conditions of Contract

The liquidated damages for the whole of the works are

Rs.—————————— (amount) per day and that for the milestones are as under:

For Milestone 1:	Rs.	………	per	day

[41]

For Milestone 2:	Rs.	per day

For Milestone 3:	Rs.	Per day

The maximum amount of liquidated damages for the whole of the works	[41] is ten percent of final contract price.

The amounts of the advance payment are:” Deleted as per GO Ja Sam E 127 MBI 2020 dated 30/05/2020”

The amounts of the advance payment are:	[42]

Nature of	Amount (Rs.)	Conditions to be fulfilled

1.	5% of the Contract price	On submission of un-conditional Bank Guarantee.

Mobilization

(to be drawn before end of 20% of Contract period)

(The advance payment will be paid to the Contractor no later than 30 days after fulfillment of the above conditions).

Repayment of advance payment for mobilization	:

[42]

The advance loan shall be repaid with percentage deductions from the interim

payments certified by the Engineer under the Contract. Deductions shall commence in

the next Interim Payment Certificate following that in which the total of all such payments to the Contractor has reached not less than 15 percent of the Contract Price

or —— months from the date of payment of first installment of advance, whichever period concludes earlier, and shall be made at the rate of 7.5% percent of the amounts of all Interim Payment Certificates until such time as the loan has been repaid, always provided that the loan shall be completely repaid prior to the expiry of the original time for completion pursuant to Clauses 17 and 26.

The date by which “as-built” drawings (in scale as directed by Engineer-In-Charge) in 2 sets are required is within 30 days of issue of certificate of completion of Whole or Section of the Work as the case may be.

The date by which Operating and Maintenance Manuals are required is within 30 days of issue of certificate of completion of Whole or Section of the Work as the case may be.

The amount to be withheld for failing to supply “as built” drawings or supply of Operation and Maintenance Manuals

The following events shall also be fundamental breach of the contract :

- The contractor has contravened Sub-clause 7.1 and Clause 9 of CC.

The percentage to apply to the value of the work not completed representing the Employer's additional cost for completing the Works shall be 30 percent.

## DATA SHEET

| ClauseNo. | Description |
| --- | --- |
| 1. | C. Preparation of Tenders - Documents comprising the Tender - The tender submitted by the Tenderer shall be in two documents (Electronic Document First and Second ) and shall contain the documents as follows:: - First electronic document: (Technical Bid) - A copy of the valid PWD class –II & avove Registration certificate - Copy of the Employees Provident fund Registration certificate - Copy of the GST registration certificate - Earnest Money Deposit& tender Processing fee; on line payment through e- Procurement platform. - Qualification Information as per proformas with supporting documents in Section- 3 (1 to 10) as uploaded separately and to comply the task created in the e- Procurement Portal under General terms and Conditions and Technical parameters and Documents required from Tenderer. 10.1.2 Second electronic document: (Financial Bid) - The Tender (in the format indicated in Section 4) - Priced Bill of Quantities (Section 9); online through e-procurement portal, no hardcopy of commercials should be attached or disclosed. And any other materials required to be completed and submitted by Tenderers in accordance with these instructions. The documents listed under Sections 3, 4, 6 and 9 shall be filled in without exception. 10.2. Tenderers submitting tenders together with other contracts stated in the IFT to form a package will so indicate in the tender together with any discounts offered for the award offered for the award of more than one contract* *Delete the clause if it is only a single work |
| 2. | - Tender prices - The Tenderer shall quote percentage for all Items.Items for which no rate or price is entered by the Tenderer will not be paid for by the Employer when executed and shall be deemed covered by the other rates and prices in the Bill of Quantities. Corrections, if any, shall be made by crossing out, initialing, dating and rewriting. (Refer special conditions of contract) - All duties, taxes, and other levies payable by the contractor under the contract, or for any other cause except GST be included in the rates, prices. The contractor shall quote excluding the GST. GST shall be paid at the prevailing rates on the date of recording in the measurement book and certified by the AEE and recorded in the Sub divisional Bills register. (Refer special conditions of contract) |

| ClauseNo. | Description |
| --- | --- |
| 3. | - Tender validity - Tenders shall remain valid for a period not less than one hundred and eighty days after the deadline date for tender submission specified in Clause 16. A tender valid for a shorter period shall be rejected by the Employer as non-responsive. - In exceptional circumstances, prior to expiry of the original time limit, the Employer may request that the Tenderers may extend the period of validity for a specified additional period. The request and the Tenderers' responses shall be made in writing or by e-mail. A Tenderer may refuse the request without forfeiting his earnest money deposit. A Tenderer agreeing to the request will not be required or permitted to modify his tender, but will be required to extend the validity of his earnest money deposit for a period of the extension, and in compliance with Clause 13 in all respects. |
| 4. | 14. Format and signing of Tender Tenderer shall submit the Bid electronically before the submission date and time published in e-procurement portal. |
| 5. | Submission of Tenders 15. Tenderer shall submit the Bid electronically in the e-procurement portal before the submission date and time published. |
| 6. | - Deadline for submission of the Tenders - Tenders must be submitted on line in the e-Procurement portal by the tenderer before the notified date and time. |
| 7. | - Late Tenders - In online e-procurement system, tenderer will not be able to submit the bid after the bid submission time and date as the icon or the task in the e-procurement portal will not be available. The tender inviting authority will not be responsible for any glitches in the system. |
| 8. | - Modification and Withdrawal of Tenders. - Tender can modify and correct and upload any relevant document in the portal till Bid submission date and time, as published in the e-procurement portal. - The Tenderer may withdraw his tender before the notified last date and time of tender submission |
| 9. | - To assist in the examination, evaluation, and comparison of Tenders, the Employer may, at his discretion, ask any Tenderer for clarification of his Tender, including breakdowns of unit rates. The request for clarification and the response shall be in writing or by electronic mail, but no change in the price or substance of the Tender shall be sought, offered, or permitted. - Subject to sub-clause 22.1, no Tenderer shall contact the Employer on any matter relating to its Tender from the time of the Tender opening to the time of the contract is awarded. If the Tenderer wishes to bring additional information to the notice of the Employer, it should do so in writing. Tenderer can also submit online clarification through e-procurement portal through query option. For any clarification related to e- procurement process the intending bidder shall contact e-procurement help desk from 9 AM to 9 PM (Monday to Saturday) on working days at phone no. 080-25501227. |
| 10 | - Within 20 days of receipt of the Letter of Acceptance, the successful Tenderer shall deliver to the Employer a Security deposit in any of the forms given below for an amount equivalent to 5% of the Contract price plus |

| ClauseNo. | Description |
| --- | --- |
|  | additional security for unbalanced tenders in accordance with Clause 25.5 of ITT and Clause 44 of the Conditions of Contract. 98 - Fixed Deposit Receipt/ Term Deposit Receipt in favour of the Executive Engineer, KNNL, No 5 Bhadra Canal Division, Davanagere.. - A secured Financial Messaging System (SFMS) bank guarantee in the form given in Section 10. |
| 11 | “CHIEF ENGINEER”, “SUPERINTENDING ENGINEER”, “EXECUTIVE ENGINEER” shall mean the “Chief Engineer”, “Superintending Engineer”, “Executive Engineer” in charge of the work. The Engineer were named as the final authority for decision shall only mean the Chie Engineer in-charge of work. The Engineer in Charge is the Jurisdictional Executive Engineer of KNNL who will be in charge of work. |
| 12 | - Possession of the Site - The intending bidders should note that, if any of the land either in part/parts or in whole required from the work is not yet acquired by the Nigama, it shall be the responsibility of the bidder to take possession of the such land and start the work by consent of the land owners before commencement of work at no extra cost to the nigama and no claim what so ever relating to non-availability of land would be entertained. Further, Nigam shall co-operate in getting the required for the work by inisiating LAQ proposal as per Land Aquisision Act. Any delay in obtaining consent of the land owners shall not be considered for any additional compensation. In case of any obstruction from the land owner during the construction period or during the maintenance period, the contractor has to make his own arrangements to get the dispute settled and to bear the extra cost, if any, on that account. |
| 13. | - SETTLEMENT OF DISPUTES- TIME LIMIT FOR DECISION - If any dispute or difference of any kind whatsoever was to arise between the Executive Engineer/Superintending Engineer and the contractor regarding the following matters namely, - The meaning of the specifications, designs, drawings and instructions here in before mentioned; - The quality of workmanship or materials used on the work and - Any other question, claim, right, matter, thing whatsoever, in any way arising out of or relating to the contract, designs, drawings, specifications, estimates, instructions, or orders, or those conditions or failure to execute the same whether arising during the progress of the work, or after the completion, termination or abandonment thereof, the dispute shall, in the first place, be referred to the Chief Engineer who has jurisdiction over the work specified in the contract. The Chief Engineer shall, within a period of sixty days from the date of being requested by the Contractor to do so, give written notice of his decision to the Contractor. If the Contractor is aggrieved by the decision of the Chief Engineer, or if the Chief Engineer fails to give written notice of his decision within the above said period of sixty days, the contractor may appeal to the Managing Director, KNNL, within 60 days from the receipt of written notice of Chief Engineer's decision or from the expiry of first named period of 60 days. - Subject to the Managing Director's decision on appeal and subject to other form of settlement hereafter provided, the Chief Engineer's decision in respect of every dispute or difference so referred shall be final and binding upon the contractor. The said decision shall forthwith be given effect to and contractor shall proceed with the |

| ClauseNo. | Description |
| --- | --- |
|  | execution of the work with all due diligence. Remedy when Managing Director's decision on appeal is not acceptable to contractor - In case the decision of the Managing Director is not acceptable to the contractor, he may approach the Law Courts at Shimoga for settlement of dispute after giving due written notice in this regard to the Managing Director within a period of ninety days from the date of receipt of the written notice of the decision of the Managing Director. Time limit for notice to approach law court by contractor - If the Managing Director has given written notice to the contractor of his decision on his appeal and no written notice to approach the law court has been communicated to him by the contractor within a period of ninety days from receipt of such notice, the said decision shall be final and binding upon the contractor Time limit for notice to approach law court by contractor when decision is not given by Managing Director. - If the Managing Director fails to give notice of his decision within a period of ninety days from the receipt of the contractor's appeal, the Contractor may within ninety days after the expiry of the above named period of ninety days approach the Law Courts at Shimoga giving due notice to the Managing Director. - Whether the claim is referred to the Chief Engineer or Managing Director or to the Law Courts, as the case may be, the contractor shall proceed to execute and complete the works with all due diligence pending settlement of the said dispute of differences. Obligations of the Executive Engineer and contractor shall remain unaltered during considerations of dispute - The reference of any dispute or difference to the Chief Engineer or Managing Director or the Law Court may proceed not withstanding that the works shall then be or be alleged to be complete, provided always that the obligations of the Executive Engineer and the contractor shall not be altered by reason of the said dispute or difference being referred to the Chief Engineer or Managing Director or the Law Court during the progress of the works. Aggrevated Contractor to Approach Civil Court 24.8. It is clearly understood and agreed upon by both the parties that no part of the above clause shall be construed to be an arbitration clause. In the event of any dispute or difference arising between the parties to this contract, upon exhausting the remedies under clauses 29(a) to (g). The only remedy available shall be to approach the jurisdictional Civil court by filing a suit in accordance with law. |
| 14 | 25.2. The Employer's approval of the Program shall not alter the Contractor's obligations. The Contractor may revise the Program and submit it to the Employer again at any time. A revised Program is to show the effect of Variations. |
| 15. | Extension of the Intended Completion Date 26.1 If the contractor shall desire an extension of the time for completion of the work on the ground of his having been unavoidably hindered in its execution or on any other ground, he shall apply in writing to the Executive Engineer before the expiration of the period stipulated in the tender or before the expiration of 30 days from the date or which he was hindered as aforesaid or on which the cause for asking extension occurred, whichever is earlier and the Executive Engineer or other competent authority may, if in his opinion there are reasonable grounds for granting an |

| ClauseNo. | Description |
| --- | --- |
|  | extension, grant such extension as he thinks necessary or proper. The decision of such competent authority in this matter shall be final. 26.2 The time limit for completion of the work shall be extended commensurate with its increase in cost occasioned by alterations or additions and the certificate of the Executive Engineer or other competent authority as to such proportion shall be conclusive. |
| 16. | - Tests - If the Employer instructs the Contractor to carry out a test not specified in the Specification to check whether any work has a Defect and the test shows that it does, the Contractor shall pay for the test and any samples. |
| 17. | - Bill of Quantities (BOQ) - The BOQ shall contain items for the construction, installation, testing, commissioning, Operation & Maintaince works to be done by the Contractor. |
| 18. | 36. Submission of Bills for Payment 36.2 The Employer shall check the Contractor's bill and determine the value of the work executed which shall comprise of (i) value of the quantities of the items in the BOQ completed and (ii) valuation of Variations. |
| 19. | - Payments 37.1 Payments shall be adjusted for deductions for advance payments, other recoveries in terms of the contract and taxes, at source, as applicable under the law. The Employer shallAs for as possiblepay the Contractor within 60 days of submission of billas per availability of grant. The contractor shall be liable to pay liquidated damages for shortfall in progress. For progress beyond the agreed programme payment is subject to availability of the grants. 37.2 Items of the Works for which no rate or price has been entered in will not be paid for by the Employer and shall be deemed covered by other rates and prices in the Contract. |
| 20. | - Tax - The rates quoted by the Contractor shall be deemed to be exclusive of G.S.T which shall be paid at the rate prevailing on the date on recording. The employer will perform such duties in regard to the deduction of such taxes at source as per applicable law. |
| 21. | - Final account - The Contractor shall supply to the Employer a detailed account of the total amount that the Contractor considers payable under the Contract before the end of the Defects Liability Period. The Employer shall issue a Defect Liability Certificate and certify any final payment that is due to the Contractor within 90 days of receiving the Contractor's account if it is correct and complete. If it is not, the Employer shall issue within 90 days a schedule that states the scope of the corrections or additions that are necessary. If the Final Account is still unsatisfactory after it has been resubmitted, the Employer shall decide on the amount payable to the Contractor and make payment as per availability of grant. |
| 22. | 13.2. Instruments having fixed validity issued as earnest money deposit for the tender shall be valid for 180+45 days beyond the validity of the tender. |
| 23. | 46.1. The Employer shall take over the Site and the works after maintenance period. |

Broad Scope of Work

##### TABLE OF CONTENTS

| No. | CONTENTS |
| --- | --- |
|  | Note/Scope of works/ site information |
| 1. | Site Information |
| 2. | Proposal under Kogalur Tank Filling Scheme |
| 3. | Assessment of Tanks |
|  | Project components |
| 4. | Rising Main |
| 5. | Pressure Distribution Network |
| 6. | Gravity Main |
| 7. | Broad Scope of work in the present Tender |
| 8. | Pumping Machinery |
| 9. | Civil works |
| 10. | Mechanical Works |
| 11. | Electrical works |
| 12. | Electrical Sub - Station |
| 13. | General |
| 14. | Deliverables |
| 15. | Key Personnel |
| 16. | Employer |

###### Site Information

| No. | Particulars |  |  | Details |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | Location |  |  | The intake point is at Kogaluru Lake |  |  |  |
| 1.1 | River Basin | a) Name |  | Krishna Basin |  |  |  |
|  |  | - Located in - State(s) - Countries (if international river) |  | Karnataka India |  |  |  |
| 1.2 | River /Tributary |  |  | Tunga Bhadra River |  |  |  |
| 1.3 | State(s)/District(s) Taluk(s) or Tehsils in which the following are Located. |  |  | State | District |  | Taluka |
|  | a) River-Krishna |  |  | Karnataka | Davanagere. |  | Channagiri |
|  | b) Headwork |  |  | Karnataka | Davanagere. |  | Channagiri |
|  | c) Tanks Beniftted |  |  | Karnataka | Davanagere. |  | Channagiri. |
| 1.4 | Name of the village near the Headwork |  |  | Anveri Village of Bhadravati taluk & Shimoga |  |  |  |
| 1.5 | Location of Head Works |  | a) Longitude | 75057’11.89” |  |  |  |
|  |  |  | b) Latitude | 14011’11.48” |  |  |  |
|  |  |  | c) Agro climatic Zone | Agro climatic Zone - IV - Central Dry Zone(Tumkur) |  |  |  |
| 1.6 | Project area Reference to |  |  |  |  |  |  |
| 1.7 | a) Degree Sheets |  |  | 48 N/12, (Scale: 1:50,000) |  |  |  |
| 1.8 | b) Index Plan |  |  | Enclosed |  |  |  |
| 1.9 | Access to the Project |  |  | Name |  | Distance from project site |  |
|  | a) Airport |  |  | Shivamoga |  | 90 Km's |  |
|  | b) Rail head |  |  | Davanagere Railway Station |  | 30 Km's |  |
|  | c) Road head |  |  | Approachable by asphalted road |  |  |  |
| 1.10 | Temperature |  |  |  |  |  |  |
|  | a) Maximum Temperature during May |  |  | 39.0 |  |  |  |
|  | b) Minimum Temperature during December |  |  | 18.0 |  |  |  |
|  | c) Mean Temperature |  |  | 28.5 |  |  |  |
|  | Nearest Power Station |  |  | Santhebennur Sub-Substation |  |  |  |

- Introduction

Tanks identified under the scheme are falling under Tungabhadra river catchment and absence of any perennial source of water for drinking purposes for the populace as well as livestock in the region. The

ground water table in these regions has reached alarming depths due to over exploitation, as a consequence of which the available ground water is contaminated. Furthermore, there are several MI tanks in this region which are not receiving sufficient quantum of inflow in the past several years. Drinking water for livestock are mainly dependent on these tanks in this region.

It is a long standing demand of the people in the region that a permanent and dependable source need to be identified and these areas are supplied with drinking water facility besides filling of existing MI tanks.

On the study of toposheet the nearest dependable source is Kogalur halla & the water can be lifted from right bank of Kogalur Halla near kogalur Village of channagiri taluk & Davanagere district. The Geographical location of lifting point will be Latitude: 14011’11.48” Longitude: 75057’11.89”

Therefore, it is proposed to take up Kogaluru TANK FILLING SCHEME to promote the for sustainability of the livelihood of the area in the shortest time possible. Accordingly, the present proposal envisages lifting of water from Kogaluru lake for filling of percolation tanks of Kogaluru village coming under MI for recharging groundwater and supplying drinking water for the farmers of the proposed area in Channagiri Taluk. The quantity of water required for this scheme 7.072 Mcft for filling of Tanks.

###### Assessment of Tanks

The farmers of the area have been insisting for taking up the tank filling work of Kogalur tanks in the Channagiri taluk in Davanagere District. As part of the scheme it is proposed to fill the tanks.

The total water requirement for filling up of tanks by Pumping water from Kogaluru lake in Channagiri taluk in Davanagere District by considering 70% of live capacity of tanks works out to be 6.188  Mcft and considering additional 10% evaporation losses works out to be 0.884 Mcft.

###### List of Tanks Proposed under the Scheme:

| PARTICULARS OF THE TANKS CONSIDERED FOR FILLING |  |  |  |  |
| --- | --- | --- | --- | --- |
| Sl no | Name of the tank | Capacity in MCft | 80% of Capacity in Mcft | Discharge with 90 days and 22 hours Pumping in Cusecs |
| 1 | Hirekogaluru tank -1 | 4.24 | 3.392 | 0.476 |
| 2 | Hirekogaluru tank -2 | 4.60 | 3.680 | 0.516 |
| Total |  | 8.84 | 7.072 | 0.992 |

Peak discharge for the scheme is 0.028 Cumecs.

The scheme shall be designed to carry design discharge as shown below.

| Description | Details |
| --- | --- |
| Length of Raising Main (Km) | 4.80 Km |
| Static Head (m) | 27.00 m |
| Peak Discharge (Cumecs) | 0.028 Cumecs |

This proposal is for filling of percolation tanks of Kogaluru village under the Kogaluru Tank Filling Scheme. The discharge required for the proposed scheme is  0.028 Cumecs

The above considerations shall be adopted by the turnkey agency while planning the present scheme.

- Intake structure shall be planned for carrying discharge of 0.056 Cumecs (0.028 Cumecs for Tank Filling = 0.028 Cumecs x 2 = 0.056 Cumecs.

- The proposed Jack well is to be constructed for of 2 No’s of Submersible Pumps (1 working + 1 Standby).

- Pumps to be designed for design discharge with standby of equal capacity.

- Bidder shall arrive at pump head by adding losses on all accounts.

- Submersible Pumps shall be considered for design.

###### Rising Main

HDPE  pipes shall be considered for the design of Rising Main. The design of the Rising Main shall not be less than the values given in the following table.

| Details of Rising main from PH to DC |  |  |
| --- | --- | --- |
| No | Particulars | Rising main |
| 1 | Length of the Rising Main (m) | 4.80 km |
| 2 | Peak Discharge (Cumecs) | 0.028 |
| 3 | Number of Rows (No) | 1 |
| 4 | Pipe material | HDPE |
| 5 | Velocity considered (m/s) | 0.93 m/s |
| 6 | Outer Diameter of Pipe (mm) | 225 mm |
| 7 | Grade of Pipe (mm) / Class of Pipe | HDPE, PN-10, PE-100 |

###### Broad Scope of Works

The scope of work included in the proposed bid is as under:

- Detailed Survey, investigation, fixing alignment of raising main up to DC, arriving the static/pump head, design of electromechanical works comprising pumps and motors, electrical works, design of raising main and its appurtenance works. The necessary surge analysis and surge protection works will be done by phase-II certification. However necessary data should be provided by this contractor.

- Construction of Intake structure for carrying discharge of 0.056 Cumecs.

- Jack well cum pump house and its allied works (Approach road, embankment) at end of Intake Canal to accommodate present requirement of 2 No’s of Submersible Pumps (1 working + 1 Standby ). The pump and motor floor shall be located above the HFL. The HFL of 619.50 m shall be considered for the project.

- Supply, Installation, testing and commissioning of Pumping Machinery with 2 No’s of Submersible Pumps (1 working + 1 Standby ) of 0.028 Cumecs at duty point head of 54 m  along with pump house electrical works.

- Design, fabrication, supply, assembling, testing and commissioning of LT pump panel board made of sheet metal duly painted with recess for cable entries at bottom suitable for 415 V equipped with Air circuit breaker of suitable capacity for 1 number incoming with required Amp and 2 numbers 250A MCCB along with 2 No's of OG Feeder for 40 Hp LT motor thyristor based digital soft starter outgoing of suitable capacity with capacitor, aluminium bus bars of required Amp metering panel, protection relays, current transformers of suitable rating and out goinhg TPN switches of rating 4X63A, 4X32A, 4X16A and outgoing capcitor bank with APFC panel wire through timedelay suitable rating contractor connected to out going terminals of soft starter with all other accerceries complete with wiring as per approved drawings and specificatios.

- Design, manufacture, supply, erection, trail running, performance testing and commissioning of submersible pumps of approved make conforming to IS: 1710 having specified pump output of 101.14 m3 /hr under specified operating head of 54.00m coupled to LT motor of 40 HP rating operating at 415 V with flexible coupling, discharge Tee with flanged end for connecting delivary pipe with all other standard accessories, nut & bolts, plateand safety devices etc., complete as per specifications, terms and conditions of contract.

- Construction of RCC platform structure for substation shall be made for 1 no. of transformer (1 working + 0 standby transformer).

- Supply, Jointing, Laying, Testing and Commissioning of HDPE Rising Main for a length of 4.80 KM with relevant structures.

- Supply, Jointing, Laying, Testing and Commissioning of pressure distribution network with relevant structures.

- Operation and maintenance for 5 years after completion.

The location of Head Works, Intake Canal and pump houses have to be identified on topo sheet and also on the ground. The bidder after surveys and investigations may suggest locations at the said elevations which can be advantageous, to the Government.

From the pump house, the delivery pipes shall be connected to the manifolds of suitable numbers. From the manifold outlet to rising main shall be provided.

Electro-mechanical equipment to be provided shall be designed for a required pumping capacity considering all the losses. The bidder has to provide suitable numbers of required capacity of vertical turbine pumps in the pump house designed for peak discharge and in addition to working pumps, there has to be a standby pump of equal capacity. The pump house size shall be suitable to accommodate the proposed number of pumps including stand by pump. Space shall also be provided for locating the control panel and other accessories with service bay and maintenance bay. The Jackwell, Intake Canal and transition shall match the size of the pump house.

The proposed lift scheme is planned to provide filling of 2 no’s of tanks. The total length of raising main is

4.80 Km (approx).

Further, as mentioned in the scope of work it is the responsibility of the bidder to carry out detailed survey, investigation, designs, drawings for entire lift scheme comprising total length of rising main for filling of tanks including preparation of longitudinal sections, hydraulic design of rising main and feeders, design of pumping machinery, electrical substation, power line etc., and obtain approval as directed by Engineer- in-Charge.

All the designs of the various components shall be as per the relevant IS Codes and specifications and are subject to approval of the Chief Engineer. Detailed specifications for electro-mechanical works, Intake structure, Jackwell-cum-pump house, Delivery pipe, Manifold, electrical substation and powerline are given in the bid documents and have to be complied with.

These are broad outlines for the scope of work. The requirements of LIS which are common are described in the bid documents.

The proposed Jack well shall be made for present requirement of 2 No’s of Submersible Pumps (1 working + 1 Standby).

power transmission line to be drawn from the existing KPTCL / ESCOMS substation to the proposed electrical substation near the Jackwell cum pump house.

All the designs of the various components shall be as per the relevant IS Codes and specifications and are subject to approval of the Chief Engineer. Detailed specifications for electro-mechanical works, Intake structure, Jackwell-cum-pump house, Delivery pipe, Manifold, electrical substation and powerline are given in the bid documents and have to be complied with.

These are broad outlines for the scope of work. The requirements of LIS which are common are described in the bid documents.

###### Pumping Machinery

Design, supply, installation, testing and commissioning with suitable pumps coupled to motors of required numbers of equal capacity suitable for parallel operation designed for peak discharge, including one standby pump. Scope includes electrically actuated Butterfly valve, dual plate check valve, MS manifold, dismantling joint, EOT crane of suitable capacity with main/auxiliary hoists. Scope includes surge analysis and providing suitable surge protection equipment as per requirement.

Design, supplying, installation, testing and commissioning of Electrical panel, soft starters, capacitor, cabling, earthing, Auxiliary supply AC with LTAC panel, Auxiliary transformers, DC supply with battery charger cum DCDB, battery bank, control cabling, valve actuator panel, APFC panel for improvement of power factor, level indicator, Pump house lighting inside and outside, small power outlets, Circulating cooling water pumps, header piping, valves, filters for cooling of motors/pumps.

Pumps to be designed for peak discharge with required number of equal capacity of discharge with one number stand by pump.

Bidder shall arrive at pump head by adding losses on all accounts. VT pumps shall be considered for design.

###### Civil Works

Scope includes construction of Intake structure, jack well cum pump house. and civil works of

11 KV electrical substation, power line, construction of approach road to headworks.

###### Construction of Intake canal & structures

Intake canal is from Kogalur nala near kogalur village. Intake canal is to be designed for 100% extra discharge. The Intake structure is closed conduct as per relevant IS codes. Necessary service roads and inspection paths are to be provided. Along the service road of Intake structure, asphalt road as per MORTH Standards is to be designed from off take point up to Jack Well cum Pump House and got approved by the Chief Engineer and shall be executed accordingly.

The drawing of the Intake canal / structure and the map of area surrounding the Intake canal/ structure including proposed development shall be got approved before construction / development.

###### Construction of Jackwell cum Pump House for accommodating Pumps

Intake arrangements shall consist of a Forebay, sump, surge pool and pump house of suitable size to accommodate the required number of pumps in the pump house. The floor level of the pump house shall not be below the Maximum Water Level / HFL of the river. For intake fore bay, trash racks have to be provided for each compartment of the pump house. Suitable Stop log gate arrangements are to be made. There shall also be a moving gantry mounted on rail, covering all the vents of jack well.

Pump house shall be of suitable size, to accommodate the required number of pumps with sufficient working space around each pump. It shall be of size so as to accommodate the electrical control panel, repair bay and any other equipment or accessory connected with operation of pumping machinery.

In the pump house an EOT crane of appropriate capacity mounted on rail shall be provided. Design of pump house and jack well shall also take into account the loads due to operation and movement EOT crane. Providing suitable number and size of Aluminum windows and ventilators shall suitably ventilate the pump house. The opening of the pump house on the approach road shall be of sufficient size to permit movement of vehicle with pump accessories. The opening shall be provided with rolling shutters. In addition to providing proper illumination inside the pump house, illumination shall be provided for outside portion also. The roof of pump house shall be corrugated galvalume sheets. Flooring shall be with anti skid tiles of superior quality, which shall got approved by the Engineer-In-Charge. These items shall be executed as per relevant IS specifications of latest version.

Entire area accommodating the installations such as pump house, sub-station, portion of rising main and manifold including area around the pump house shall be provided with suitable chain link fencing with gate arrangement. It shall be graded / levelled suitably. Wherever necessary anti-reptile fixtures/arrangement

shall be provided along with chain link fencing. Grade of concrete for all structural concrete works shall be not less than M 30 and Minimum grade of steel Fe 550.

The General Arrangement Drawing of the pump house and the map of area surrounding the pump house including proposed development shall be got approved by the Chief Engineer before construction / development.

###### Construction of Approach Road

Investigation, Survey, Design, and Construction of approach roads shall be carried out by the agency. Internal roads near the head works / electrical substation are to be provided with concrete.

###### Construction of Valve Chambers

Design, construction of valve chambers shall be as per the requirement to accommodate the required number of suitable valves on the rising main at suitable locations as per the design requirements.

Grade of concrete for all structural concrete works shall be not less than - M 25 and Minimum grade of steel Fe 550. The drawings of the valve chambers shall be got approved by the Chief Engineer before construction.

###### Construction of Anchor / Thrust Blocks

Design, construction of Anchor / Thrust blocks shall be as per the requirement, Anchor / Thrust blocks should be provided where there is a vertical/horizontal bends along the rising main.

Grade of concrete for all structural concrete works shall be not less than - M 20 and Minimum grade of steel Fe 500. The drawings of the Anchor / Thrust blocks shall be got approved by the Chief Engineer before construction.

###### Railway / National Highway / State Highway Crossings:

Investigation, Survey, Design, Construction of Railway / National Highway / State Highway Crossings shall be carried out by the agency. Horizontal Pushing method shall be adopted for executing the construction by the agency after seeking approach from concern authorities.

###### Mechanical Works

  - HDPE Rising Main:

The scope includes installation of raising mains, including necessary kinetic air valves, scour valves, etc. as per ground profile and design considerations. The scope includes Supplying, laying and jointing HDPE pipes of specified grade and conforming to IS 4984-2016 with latest ammendments and conveying to work site including loading and unloading at both destinations and rolling and lowering into trenches, laying true to line and jointing of pipes and specials with electrofusion welding, giving hydraulic test as per relevant ISS with all lead and lifts including encasing the pipe alround to a depth of not less than 15 cms. with soft gravel or selected earth available from the excation, testing and commissioning. The rate is inclusive of required specials and fittings wherever necessary like saddle Tee, stub ends, flanged sets, bedns, reducers etc. complete (Contractor will make his own arrangements for procuring water for testing).

For design of Rising Main the following criteria shall be followed:

- Velocity shall be limited to 0.93 m/sec.

- Grade of HDPE Pipe for Rising Main shall be  PE-100 PN-10 .

- The OD of rising main shall not be less than 225 mm.

- Design of Rising Main should be done by considering the above grade.

- Diameter, wall thickness and grade of Steel shall not be less than the figures indicated in the schematic diagram.

###### Pump House Electrical Works

Scope includes Design, Supply, install, test and commissioning of following

- 11 kV LT panel board along with Variable frequency drive panel and Running panel.

- Motor control and protection panel.

- Pump and motor cooling arrangement.

- HT/LT cabling.

- Illumination inside and outside pump house

- Earth grid with Earth station and connection to all electrical equipment’s.

- Supplying, Installation, testing and commissioning C & R panel and wiring.

- Supplying, Installation, testing and commissioning of SCADA arrangement inside pump house.

- Any other miscellaneous electrical works.

###### Electrical Substation

The scope includes construction of reference transformer bay (11/415 V step down transformer) near the existing Escom electrical substation and Supply of material & Erection of 11 KV Single Circuit Line to supply power to the Jack well cum pump house and construction of  11 KV / 415 V Electrical Sub-station with required capacity (1 working ) at Jack well Cum Pump House.

The substation equipment shall consist broadly of the following:

- Design, supply, erection, testing and commissioning of power transformer of capacity not less than 0.10 MVA to meet the load requirement of pumping stations for 11 kV / 415 V, ONAN /, DYN11 vector group with copper winding, oil filled with OLTC and RTCC panels, with radiator banks, conservator oil tank, buckholtz relay, surge relay with valves, piping, HV & LV bushings, and LV cable core, outdoor type with neutral CT, NGT & NGR all as required and as per IS: 2026. One transformer of equal rating shall be provided as hot standby.

- Supply, install, test & commissioning outer door type SF6 circuit breakers 11 KV for line protection and for transformer protection and including all necessary mounting structures, foundations, marshalling box complete.

- Isolator: Double Break Type - 400 kV Assembly, erection, alignment and wiring including movement from the point of unloading to the point of erection

- SITC capacitor voltage transformer(CVTS), current transformer(CTS), electromagnetic voltage transformers (EMVTs), lighting arrestors as required as per KPTCL requirements.

- Provide 11 KV ACSR bar formation & bus bar connectors and associated equipments.

- Providing earth mat as per KPTCL/ESCOM design and provide earth stations & connectors.

- GI tape for mounting structures and marshalling boxes

- 11 kV HT Metering cubicle of different CT Ratio, Both side cable entry type with 3 CT & 3 PT, With Transparent Cover TTB, with 30x8 mm Copper Busbar, Modem & 2 No of Meters for 3 Phase 4 Wire Metering without Load Break Switch (HT Metering Box Fabricated out of 3 mm MS Sheet duly epoxy powder coated) as per revised Specification (Dwg No. BESCOM/GM/QS&S/-- Dtd 24.11.2018)

- Provide C & R panels for line protection & transformer protection.

- BATTERY SET : Plante/Grid Plate Type 110 V, 200 AH with all necessary interconnections.

- Provide control earthing from C & R panel to various equipments.

- Provide power cabling a) from both transformer to 11kv/433 V panel in pump house b) from Panels to motors and soft starters.

- Provide switchyard lighting.

- Provide safety equipment with CO2 foam & water type fire extinguishers, sand buckets, insulator rubber matt, insulated hand gloves, Hickery rod, safety instrument, danger boards, artificial respiration charts in English and kannada, first aid box etc.

- The scope includes submission electrical drawings to CEIG and obtaining approvals, getting the approval of KPTCL for switch yards, getting the clearance from MRT cell. Obtaining RR No from ESCOM and commissioning of installation.

- Supply of recommended spares for above equipments.

- Provide Civil works comprising of

  - Provide concrete approach road to sub-station with internal road upto control room.

  - Provide cable duct with precast covers from control room to various equipments

  - Provide foundation for transformer & other mounting structures.Construct firewall between Two transformers for fire safety.

  - Construct oil soak pit as per required volume of oil quantity to be drained.

  - Spreading of gravel of 20/25 mm size 150mm depth in the& future switch yard area.

  - Construct concrete man holes with cover for earth stations.

- Scope includes watering arrangements to each earthing pits through pipe line with over head tank & pumping arrangement for the entire Sub-Station and Pump House.

The scope of work involves Supply of material and  construction of 11kv/415 V Reference transformer bay, and Construction of 11 kV power Line.

The transmission line designs are to be got approved from KPTCL / ESCOMS by the successful tenderer. The tenderer should note that if any alternate size of section indicated in the drawings due to the non availability of any specific size, the same size shall be on the account of the contractor. All the material required for the construction of the Transmission Line specially mentioned in these specifications or not shall have to be supplied and erected by the successful bidder as per the specification contained herein.

THE SCOPE OF WORKS INCLUDES THE FOLLOWING:

- Detailed survey of the route of Transmission line as per the route map.

- Preparation of Profile sheets and RCC poles spot.

- Estimate for 11/415 V Reference transformer bay, 11 kV line is to be got approved from KPTCL / ESCOMS.

- Work is to be executed as per the KPTCL / ESCOMS guidelines.

- Poles shall be manufactured as per KPTCL Specifications. The pole erection and base concrete and earth shall be as per KPTCL Specification and got clearance from TA & QC of ESCOMS.

- Irrespective of anything said or omitted here in the materials shall be suitable for the purpose intended for 11 kV and shall confirm to the latest addition of the relevant ESCOMS /KPTCL/ Indian standard specification.

- Procurement of ACSR conductor as per relevant IS and as per ESCOMS /KPTCL/ standard specification.

- Procurement of Insulator, Insulator string and the associated hardware as per the specifications.

- Procurement of Conductor accessories etc, as per Specifications

- Excavation, Poles erection and Concreting Back filling and consolidation of Poles foundation including Soil Testing and Foundation Protection works wherever required.

- Erection of Superstructure and all associate accessories such as Danger Board Plates, Phase plates, number plates, etc.,

- Stringing of Power Conductors as per the Sag Tension charts including hoisting of Insulators, Clipping in and providing the necessary jumpers at the strain points and hooking on the Station Gantries.

- Conducting pre commissioning tests and obtaining the approval of the Chief Electrical Inspectorate to the Government of Karnataka and ESCOMS.

- All the materials are to be procured after getting inspection and approval from KPTCL TA & QC.

Before submitting the offer, the tenderer shall inspect the proposed route of the line and make himself conversant with the field conditions.

The Contractor’s shall be responsible to obtain approvals for all the necessary way leaves and clearance required from various authorities such as Railway, Highways, Telecommunication Authorities (PTCC approvals) etc, at his cost. KNNL will give the required assistance in the form of letters to be addressed to the concerned authorities wherever required. If any compensation is to be provided to any party or individual for the loss sustained by them by way of tree cutting, damages to the crops or other materials, the same shall be paid by the Contractor at his cost. The quoted cost shall include such costs.

The Contractor’s proposals shall be based upon the use of all the materials complying fully with the requirements as per the relevant standards. Such materials shall meet the performance requirements specified and be acceptable to ESCOMS, KNNL reserves the right to accept or reject such proposals without assigning any reasons thereon.

The transmission line shall be complete in every respect with all mountings, fittings, fixtures and standard accessories normally provided for such Transmission line and/ or needed for erecting, completion and safe operation of the same as required in applicable codes and as per the specifications mentioned in the requirement of ESCOMS and 11 KV line is to be charged from ESCOMS and CEIG.

Supply of Spares and Tools:

The scope includes supply of recommended spares and set of tools as specified in the Bid document.

Operation and Maintenance:

The Operation and Maintenance of the scheme for a period of 5 years after successful Completion and establishing the performance guarantee as per tender clauses.

###### General

The scope also includes operation and maintenance of head works for a period of 5 years after successful commissioning of work, KPTCL Supply with and establishing the design parameters as per relevant IS standards. Maintenance also includes silt removing in the sump annually along with maintenance of trash rack and stop log gates & cranes annually.

- Log books are to be maintained for recording up to date information related to day-to-day operation & maintenance activities (Quantum of water pumped to the delivery chambers, Pump operations at all locations including information on performance of pump in comparison with design requirements, test results, Preventive maintenance, occurrence of major breakdowns, examining & ensuring the correctness of Electricity bills in a well defined structured formats.

- The Agency shall comply with all applicable health and safety regulations in all his activities under the contract. The Agency is responsible for ensuring the health and safety of his personnel.

- Sufficient Stock of Consumables for, Daily maintenance of Electrical & Mechanical components should be always maintained at required locations in the Head work

- The Agency shall plan adequately for any accidents and shall make suitable arrangements with KNNL staff and local authorities, including the provision for training some of his staff in first aid, transport so that, in the event of an accident, any injured personnel will be provided with all reasonable emergency care and evacuated expeditiously to a hospital.

- A Complaint register/registers for recording complaints and actions taken thereon shall be maintained in the form prescribed by KNNL Engineer and the monthly abstracts shall be furnished to the JC in the form of reports.

- Any activity not specifically mentioned herein but deemed to be fairly contingent to the intent and spirit of contracted work, in the opinion of the Engineer, will form part of responsibility of the Agency.

- House keeping - Premises of all components of the scheme Viz. Head works, pumping stations, Transformer yards, Pump sets & Motors, All Units are to be maintained neat, free of dust, corrosion, dampness, Cob webs & vegetation, as applicable and the agency shall ensure easy access for inspection of each of the components.

- Maintenance also includes silt removal in sump annually along with trash rack and stop log gates.

Technical Datas to be furnished compulsorily by the bidder are as below:

- Design discharge per pump

- Total head developed by the pump at design discharge

- Finished inner diameter, thickness and number of rows of rising main.

- Drawings

- How the pumps are connected to the rising main and positions of fittings on the discharge in the pump house with size of diameter of fittings.

- Disposition of the rows of the rising main including the discharge level at the Receiving/Delivery chamber.

###### Deliverables

- Submission of Detailed designs, relevant drawings including technical reports etc, based on detailed survey.

- Soft copy of Hydraulic and Structural designs, drawings to be given.

- Preparation of Village map based on total station survey, levels co-related to Mean sea level, Jack well and Chain link fencing, etc drawings.

- Soil investigation at hydraulic structures. SBC of soil at hydraulic structure sites should be conducted in the labs approved by the Executive Engineer and test result should be attached to designs.

- Testing of concrete quality, pipe material quality, hydraulic testing of pipe line and hydraulic structures during the project period, modification of designs if any during execution.

- Highway Crossings and Permissions.

- Permission required from competent authority for crossings with necessary.

###### The Schedule of contractors Key Personnel

During construction:

| Particulars | Qualification | Nos. |
| --- | --- | --- |
| 1. Project Manager | B.E. (Civil) with min. of 5 years experience and should have been Project Manager for at least one Project/Work of size similar to the present contract. Period – Entire contract period | 1 |
| 2. Key Personnel: |  |  |
| i.Civil Engineer | B.E. (Civil) with minimum of 5 years experience of which a min. of 2 years of specific experience should be in pipe laying and construction of pumping stations/intakes. | 1 |
| ii.Mechanical Engineer | B.E. (Mech.) with minimum of 5 years experience of which a minimum of 2 years specific experience should be in installing pump sets and other machinery in pumping stations | 1 |
| iii. Electrical Engineer | B.E. (Elec.) with minimum of 5 years experience of which a minimum of 2 years specific experience should be in installing power drawal, motors, DG sets, transformers and instrumentation. | 1 |

| Particulars | Qualification | Nos. |
| --- | --- | --- |
| iv. Engineer quality control | BE(Elec/Mech) with minimum 5 years of experience in quality control related to electrical and mechanical equipments, piping and substations. | 1 |
| Penalty for not employing Project Manager and other Key Personnel, which is not refundable Project Manager Other Key Personnel | Rs.50, 000/month Rs.25,000/month |  |

List of Technical manpower required for operation and maintenance of transformer centre, sub-station and pump house equipments for 5 years period.

During operation period:

| Sl No. | Category | Qualification and Experience | No. of persons to be deployed |
| --- | --- | --- | --- |
| 1. | General Manager | BE Mechanical / Electrical with Min. 5 years experience in O&M of pumps and mechanical equipments | 1 |
| 2. | Shift Engineer | Diploma in Electrical Engineering with Min.5 years experience. | 1 |
| 3. | Electrician | ITI certificate course in Electrical trade with Min. 3 years of experience in O&M of substation equipments. | 1 |
| 4. | Pump Operator/ Fitter (Mech) | ITI certificate course in fitter trade with Min. 3 years of experience in pumps, valves etc. | 2 |
| 5. | Helper (E&M) General | Having sufficient experience to assist electricians and fitters in O&M of sub-station and pump house. | 1 |
| 6. | Security staff | Necessary watch &ward of substation pump house. To work in shifts including Sundays and holidays. | 1 |

NOTE:-The above manpower at Sl No. 2 to 5 shall work in 2 shifts including Sundays and Holidays on rotation basis and Sl No. 6 shall work in 3 shifts including Sundays and Holidays on rotation basis.

During non- operation period:

| Sl No. | Category | Qualification and Experience | No. of persons to be deployed |
| --- | --- | --- | --- |
| 1. | Shift Engineer | Diploma in Electrical Engineering with Min.5 years experience. | 1 |
| 2. | Electrician | ITI certificate course in Electrical trade with Min. 3 years of experience in O&M of substation equipments. | 2 |
| 3. | Security staff | Necessary watch &ward of substation pump house. To work in shifts including Sundays and holidays. | 1 |

NOTE:-The above manpower shall work in 3 shifts including Sundays and Holidays on rotation basis.

###### The Employer

Name	: Karnataka Neeravari Nigam Ltd, Address	: 4thfloor,Coffee Board Building, No.1,

Dr. AmbedkarVeedhi, Bengaluru – 560 001

Name of authorized Representative: Chief Engineer, KNNL,UTP Zone, Shimoga. The Engineer is: Executive Engineer, KNNL, No 5 Bhadra Canal Division, Davanagere.

Name	:

Name of Authorized Representative:

Bar Chart-Milestones for Scheduled Programs

| No | Description of work | 1 Month | 5 Month | 8 Month | 11 Month |
| --- | --- | --- | --- | --- | --- |
| 1 | Submissions of Design Drawings approvals of Equipments placing orders to manufacturers. Delivery of equipments at site including spares and Tools. |  |  |  |  |
| 2 | Civil Works – Intake forebay, Jackwell cum pump house, Laying of Raising Main, Electrical substation, control room and stores, approach road etc |  |  |  |  |
| 3 | Erection of pumps, EOT crane, -and delivery chambers, valves, Manifold & delivery pipes, Electrical works in the pump house |  |  |  |  |
| 4 | O&M manual, Factory Held test report acceptance test Guarantee/Warranty Certificate & KPTCL approvals, commissioning and PG test |  |  |  |  |

# SECTION -7

DETAILED TECHNICAL SPECIFICATIONS

## TECHNICAL SPECIFICATIONS FOR ELECTRO-MECHANICAL & ELECTRICAL WORKS

- General Instructions on Technical Specifications

- Technical specifications appended are of general in nature for guidance to the bidders.

- The bidders shall submit the Single Line Diagram of the Electrical system along with the tender.

- The Voltage class of transmission system, switchyard system, pump house equipments etc., will be specific and different for each of the pumping stations.

- The voltage class of transmission system shall be as per the norms and requirement of M/s KPTCL / HESCOM.

- The transmission system, take-off bay at the sending end substation, tariff metering equipments and earth mat designs shall be as per the norms and requirements of M/s KPTCL / concerned HESCOMs.

- The selection of voltage class of motors shall be as per IS / IEC standards.

- The voltage of HV and LV side of the power and auxiliary transformers shall suit the above requirement.

- All the components used in the scope of the bid shall conform to the IS / IEC specifications. Wherever there is any variation in the description in the specification, the conditions mentioned in the IS / IEC specification prevail.

- The successful contractor, before proceeding with placement of orders for various equipments, is advised to seek vendor approval from the Engineer. Any actions of the Contractor without vendor approval will be at his risk and cost.

- All the drawings shall be got approved before proceeding with the manufacture / Construction works.

- The QAP of all the components shall be got approved before proceeding for inspection / witness of acceptance tests.

SUBMERSIBLE PUMPS

GENERAL:

These components shall be from pump manufacturers only. The complete assembly consisting of steel base frames, sole plate and bottom pieces shall be stress relieved after fabrication and before machining. Test certificate from manufacturer regarding stress relieving with observation sheets from column pipe, discharge head, base frame, motor stool etc., shall be furnished. All necessary details regarding pump and motor mounting shall be furnished well in advance by the contractor for prior approval and to ensure necessary pockets in civil works. Work of erection pumps, motors including laying under this section, specifications of submersible pumps are outlined. The submersible pumps shall generally conform to IS 1710 of 1989.

The specifications given in this section are for the following type of SUBMERSIBLE pumps.

Submersible Pumps-self water lubricated-surface discharge type.

Submersible Pumps-self water lubricated-sub surface discharge type.

Submersible Pumps-forced water lubricated-surface discharge type.

Submersible. Pumps-forced water lubricated-sub surface discharge type.

    - PUMP DUTIES:

      - DUTY POINT DISCHARGE:

The pump shall have to give a discharge at normal water level conditions at duty head and shall give corresponding higher discharge for the lesser heads.

      - DUTY POINT PUMP HEAD:

Duty point pump heads for pumps, as corresponding to normal W.L. shall be designed by the bidders.

No loss of head what-so-ever in entry, strainer, bell mouth, bowl assembly, column pipes and discharge tee is accounted for in the calculations of pump head. The bidder/manufacturer shall have to account for these losses while designing the pumps. However, head loss delivery pipe, valves fittings, rising mains and velocity head beyond discharge flange on discharge head/pumps casing are to be included. Thrust bearing loss may be declare separately by the manufacturer.

      - DUTY POINT EFFICIENCIES:

The Tenderer should evaluate the above efficiencies and specify the same in their offer along with calculations. The curves for both types of efficiencies viz., pump efficiency and overall efficiency for entire starting from shut off to the static head should be invariably submitted along with the offer.

      - HEAD RANGE AND PARALLEL OPERATIONS:

The pumps will satisfy the head requirement as per the system resistance curves, while operating in solo and in any combination, as per design requirement. The pumps should be suitable for operation in head range. The system resistance curves of the pumps shall be submitted by the bidders.

      - POWER MARGIN:

The pumps shall be capable of operating in the range without being overloaded at any point and keeping a margin of at least 5% of power in the motor pump over entire operating range. Requirement of power at shut off should not exceed power requirement at duty point. The pump should be capable of starting against fully closed Butterfly valve without being overloaded at any point up to valve fully open.

    - PUMP CHARACTERISTICS:

The pump characteristics shall be of stable nature and such that the efficiency is fairly steady for the water level variations as mentioned in the foregoing clauses. The maximum efficiency point will be nearer to the duly point and fairly constant for larger range on either side. The pumps should run smoothly from lowest head to shut off point, without cavitations and vibration (within H.L.S. limitations for vibrations). The variation in the efficiencies for any point of operation in the entire operating range should be minimum.

      - NPSH CONDITIONS (NET POSITIVE SUCTION HEAD CONDITIONS):

NPSH required by pumps offered by the Tenderer should be lesser by at least 0.5 meters than

N.P.S.H.A. at duty point and shall not exceed the N.P.S.H. available at any point of operation in the range, with solo and parallel operations. The Tenderer shall take following values of the corresponding parameters for the purpose of calculation of N.P.S.H.A. at the site.

- Atmospheric	:   9.6 Meter column of water

- Vapour pressure of water	:  0.6674 Meters (at 37.80 C Normal temperature) column f water.

      - SPEED:

Pump speed should be decided by the tenderers based on optimum and cost economic consideration.

      - SOLID HANDLING CAPACITY:

The pumps shall be suitable for pumping of raw river water containing silt coarse sand and gravel / suspended solids upto 20 mm size. Tenderer to get water analysis done and suitable preventive special alloy coating needs to be provided to the impellers and casings to avoid any damage due to abrasive material in raw water.

      - CLASS OF OPERATION:

The pumps shall be suitable for non-stop continuous 24 hours’ operation without interruption.

    - SUMP MODEL TESTING:

      - Objectives

The objectives of model studies is to

- ensure swirl free flow conditions at suction bell mouth of stage

- observe levels in sump along with velocity of approach

- to ensure swirl free suction condition of booster pumps (where offered by Bidder) by providing appropriate hydraulic elements. The behaviour would be studied for various operation heads.

It is obligatory on the part of the Contractor to carry out Sump Model tests at C.W.P.R.S. Pune or Indian Institute of Science Bangalore or any such reputed laboratory with prior approval of the Engineer, at his own cost and at the earliest after issue of Work Order. The Contractor must fully satisfy himself about the suitability of the proposed design and layout of the sump, to ensure vortex free and cavitations free operations of the pumps.

      - Model

The composite model shall be made to a scale of 1:10 .The suction side piping needs to be made of transparent material to enable visual inspection of flow conditions. Necessary instrument such as vortex meter for measurement of swirl conditions shall be provided along with other measuring devices/instruments. The methodology for carrying out model experiment shall be approved by the Engineer.

The sump model studies include,

        - Construction of scaled model of sump chamber,

        - Simulation of pump flow conditions as per site requirement and operating conditions,

        - Study of flow conditions in the existing sump design conditions,

        - Incorporation of recommended modifications/appurtenances in the scaled model and restudying the flow conditions and improvements,

        - Preparation of report and submission and

        - Suggestions of possible modifications to the existing civil structure inclusion of appurtenances in the scope of supply.

    - DEFINITIONS OF EFFICIENCES:

For all purpose of this contract, the various efficiencies will have the same meaning and effect as defined in the IS 1710-1972 (page 5) which are reproduced below.

      - BOWL EFFICIENCY:

The ratio of bowl assembly output to bowl assembly input expressed as percentage.

      - PUMP EFFICIENCY:

The ratio of pump output to pump input expressed as percentage.

      - OVERALL EFFICIENCY:

The ratio of pump output to driver input expressed as percentage.

    - CONSTRUCTION FEATURES SUBMERSIBLE PUMPS:

The pump shall vertical, spindle suspended and non-pullout type. Number of stages should be decided by the tenderers. The pumps shall comprise of Bowl Assembly, line shaft enclosing tubes, line shaft bearings, line shaft bearing holders, discharge head thrust bearings, sole plates, base frames, flexible coupling etc.

1.5 A)  The pump shall be self water lubricated type or

1.5 B)  The pump shall be forced water lubricated type as the case may be

The pump bowl/bowls shall be flanged with machined mating faces. The bowl shall be flange joined to the discharge nozzle or suction nozzle. Bowl wearing rings be of replaceable type. The casing shall be provided with water lubricated bearings.

A Ni-Cl bell mouth shall be fitted to suction nozzle to reduce inlet velocity to 1.5 mtrs/sec. Maximum. The suction strainer shall be of galvanized MS and sufficiently strong to stand the suction pressure. Area of opening shall not be less than 2.5 times bell mouth area.

Impellers shall be enclosed type, cast in one piece and balanced both statistically and dynamically.

The impellers shall be provided with wearing

ring on it. The interior surfaces and passages shall be smoothly finished to obtain the highest efficiency and shall be designed to ensure smooth operation free from any cavitation or vibrations. As raw water is being pumped, balancing holes/ devices will not be accepted for balancing the hydraulic thrust.

The pump height (i.e., impellers) should be adjustable from the top of pump head. There should be a sufficient vertical clearance between the bowl and impeller to accommodate for the line shaft elongation due to hydraulic thrust, while in operation.

The impeller shaft will not have overhung at the bottom and will be rotating in bearing support at its bottom.

The line shaft shall be solid type and will be designed to take all types of loads such as torsion, tensile and dynamic etc. Impeller shaft will have muffled coupling arrangements.

The line shafts bearing shall be water lubricated type with cutlass rubber, grooved to facilitate lubrication. Line shaft bearing shall be provided at suitable intervals to ensure that first critical speed is at least 25% more than rated speed. Suitable steel sleeves be provided to line shafts.

The line shaft protection tubes shall be provided for forced water lubrication to line shaft bearings. The line shaft protection tubes should be of heavy duty seamless steel tubes and shall withstand all mechanical and hydraulic forces exerted on it with an allowance for corrosion and wearing.

The column pipe shall be of extra heavy weight, electrical fusion welded (EFW) single longitudinal joint, or electrical resistance welded (ERW) pipes with both ends flanged, machined on surfaces, edges and spigotted to facilitate the alignment. The flanges shall have grooves to accommodate the rubber rings.

The discharge head/motor stool shall be of full dia, flanged at ends, flanged surfaces and Tee ends machined, fabricated out of MS in smooth 900 bend to have minimum loss of head in and stress relieved before machining. The pump discharge head shall be fabricated and suitably reinforced to withstand all types of static, dynamic loads, hydraulic thrust, torsional loads imposed by the pump, motor and to limit vibrations. The pump discharge head/motor stool shall house thrust bearings with cooling arrangement and contain cast iron stuffing box in which the pump top shaft shall be sealed. A

sufficient opening should be provided so as to have an easy access and workability on stuffing box. Non-reverse rotation ratchet arrangement is to be provided either in pump or in motor so as to prevent the pump from rotating in reverse direction.

The column assembly shall be in standard lengths as far as possible.

The clearance between bell mouth, strainer and sump floor and nearing walls should be such that the vortex free operation is obtained. Any changes in this clearance if required other than those specified shall be clearly mentioned in the offer, with reasoning thereof.

The pump shall be subsurface discharge type with discharge-head with integrated or separate motor stools suitable for mounting in the R.C.C. floor of pump house. The construction should be such that the pump discharge head with thrust bearings, motor stool along with the motor shall be resting on the pump floor only.

Steel sole plates of adequate thickness shall be provided under the pump discharge head/pump head/motor stool, together with all necessary anchor bolts, nuts and washers to provide precise horizontal and vertical alignment. The sole plate shall be fixed on steel based frames to be anchored in

R.C.C. floors. The surfaces of base frame, sole plate and base plate shall be smoothly and snugly fitted so that no vibration shall occur. The fastening of base frame to sole plate and sole plate to base of pump/motor shall be through nut bolts or headed studs.

The opening in the sole plates and the base frame shall be of sufficient dia to pass the complete bowl assembly including suction bell and strainer.

The erection and dismantling of both the pumps and motors shall be possible from the motor floor, with EOT / HOT crane available in the motor hall. The motor or the pump discharge head shall not be rested either on the pump floor or motor floor while erecting or dismantling on places other than respective base frames/sole plates. The above components should always be carried from or to the service bays directly, while assembling, or dismantling. The contractor will be responsible to get design from the pump manufacturer and approved from ENGINEER. The steel base frames fabricated from plates together with machined bottom pieces, sole plates, all anchoring arrangement, support etc., for pump and motor mounting. These components shall be forms manufactures. The complete assembly consisting of steel base frames, sole plate, bottom pieces shall be stress relived after fabrication and before machining. Test certificate from manufacturer regarding stress reliving with observation sheets from column pipe, discharge head, base frame, motor stool etc., shall be furnished. All necessary

details regarding pump and motor maintaining shall be furnished well in advance by the contractor for prior approval and to ensure necessary pocket in civil works.

Work of erection pumps, motors, including layers of foundation, grouting, shaft alignment, doweling and painting etc., shall be done by the contractor at his own cost as per general and miscellaneous specifications mentioned earlier.

The thrust bearing shall be anti friction heavy duty type. The bearing shall be designed to accommodate all possible loads under normal operations or shut of condition and shall be suitable for reverse rotation up to at least 1.5 times the normal forward speed. The bearing shall be oil lubricated type and shall be provided with oil level gauge and temperature measuring and sensing system and cooling system as given below.

One no. temperature probe suitable for dial type thermometer with dial temperature.

One no. 3 wire platinum element having DC resistance f 100 ohms at 00 C suitable for use with a digital temperature, scanner as specified in electrical section.

The cooling water supply for the pump thrust bearing if required, shall be taken from a adequate tapping from the pump discharge head or line shaft bearing lubrication (forced water). Necessary valves, strainers and non-flow sensors and annunciation system on panel board shall be provided for this cooling system. The life of thrust bearings shall not be less than 40000 hours of operation.

    - FORCED WATER LUBRICATION AND COOLING SYSTEM:

The forced water lubrication system for transmission bearing and supply of cooling water to pump thrust bearing and for motor cooling shall be generally as mentioned below.

Set of manual type Pressure filters along with differential pressure switches, pressure gauge built in valves etc., are to be provided to clean stream of water from main header containing fine, un-dissolved solids like sand, dust, abrasives etc. The raw water should be made to enter into the inlet of Pressure filter at sufficient pressure. The contaminant should be separated and should pass downwards and ultimately discharging out of the drain of the Pressure filter. The clean and solids free water free from the outlet of filter should be used for the thrust bearing cooling and lubrication of line shaft/transmission rubber bearings of the submersible Pumps and for cooling of motors.

The system shall comprise of following:

One set of manual Pressure filter of adequate size for each pump shall be provided having sufficient design capacity of V.T. Pump lubrication and cooling to thrust bearing and motor cooling.

Booster pump sets complete with motor, base plate, switches and starter etc. (One working + One stand bye) suitable for group of 5 or less V.T. pumps sets shall be provided having adequate capacity in discharge and head with sufficient margin.

Suction pipe for Booster pumps with valves etc., for raw water to be taken off from the R.C.C. storage tank being provided for the purpose by the Contractor.

All Pumping valves, gauges press switches, Solenoid valves etc., shall be provided as per schematic drawing.

Electrical interlocks with suitable sensors must invariable be provided for forced water lubrication system and cooling system. The arrangement should trip the main pump motor in the event of failure of water supply from booster line to either of line shaft lubrication system thrust bearing cooling or motor cooling. The arrangement for tripping the main pump motor should be such as to allow contains time lay for the stand by booster to take over.

Automation with all relays, sensors, switch gears and solenoid valves etc., shall be provided so that if any Booster pumps trips or fails to deliver water the stand-bye set should start automatically and feed

V.T. Pumps sets the lubrication and cooling system and stop the defective Booster pumps.

The water storage tank provided to initial start could be made the only source of water for feeding the booster pumps. These tanks could be continuously fed with water from the delivery system so as to keep the water level more or less constant. So, that the tank could feed the booster pump on a continuous basis. To avoid head load on pressure filtration system water to be drawn from the storage tanks at a level not lower than the middle level of the tank.

A suitable arrangement to take out the entrapped air in the pump column discharge tee shall be provided with pipe fitted in the tapping at suitable place in the pump, with valve, etc., complete the make the system work satisfactorily.

Suitable topping appropriate place shall be provided for mounting a delivery pressure gauge. The pressure gauge shall be Bourdon type and shall be provided with piping U type and tabulating socket etc. This pressure gauge shall be provided and located at operating level i.e., motor floor level. Gauge range shall be twice the head to be measured. Drain cocks should be placed immediately below the gauged so that frequent tests could be made to determine whether pipe connections of the gauge are filled with water. The bourdon type gauge shall be fixed in such a way that no strain is placed on its

case so that readings are not affected. Gauge shall be calibrated prior to after the tests and shall be fixed in upright position.

In case of emergency i.e. failure of Booster pumps of filtration system, necessary system shall be installed by the contractor for supply of raw water for lubrication of Pumps and motor by necessary tapping from pump delivery line, by passing the regular cooling/lubrication system.

    - MATERIALS OF CONSTRUCTION FOR V.T. PUMPS/BOOSTER PUMPS:

| Bell mouth, pump bowls, suction casingAnd discharge nozzle | Ni-CI conforming to IS 210 grade 20 |
| --- | --- |
| Impellers shaft for V.T. Pumps and Booster Pumps | Stainless steel AISI SI 410 |
| Column pipes | Mild steel IS 2062 EFW/ERW pipes |
| Line shaft protection tubes | Seamless MS |
| Flexible coupling | Forged steel conforming to IS 3495 |
| Wearing rings for V.T. Pumps and Booster pumps | Gun metal/stainless steel as Appropriate |
| Column flanges | Mild steel IS 2062 |
| Nut bolts and washers upto bottom of Discharges lead | Stainless steel AIST ST 304/316 |
| Line shaft Line Shaft coupling | Stainless steel AISI-410 |
| Line shaft bearing | Stainless steel AISI – 410 |
| Pump shaft bearing | Thordon |
| BOWL | Mild Steel fabricated IS 2062 |
| Strainer | Gun Metal |
| Casing of Booster Pumps | Ni-CI or galvanised steel |
| Pressure filters | Ni-CI conforming to IS 210 grade 20 |
| Body and flanges Filter media | MS fabricated S304 |
| Sealing material | Suitable design |

    - PRESSURE FILTER:

| Design Duty Degree of filtration | 50 Micron |
| --- | --- |
| End connections | 2” NB 150 |
| Fluid | Water |
| Viscosity | 1 cp |
| Flow rate | Adequate with sufficient margin |
| Design pressure | Adequate |
| Pressure drop | 0.2 kg/cm 2 (Clean condition) |
| Hydrants Pressure | 1.5 Times of design pressure |
| Applicable standard | IS 2825 |

    - PUMPS STARTING/CLOSING LOGICS AND INTERLOCKS:HSN

      - LOGIC OF PUMPS STARTING:

After single push button command, following operations shall take place in sequence.Taped water lubrication system/pre-lubrication starts.After a time delay, the main pump motor will start and capacitor cubicle circuit will be ON.The delivery valve start opening.

      - LOGIC OF PUMP CLOSING:

The delivery valves will be closed.After closing of valves completely, the main pump motor will STOP and capacitors cubicle circuit will be OFF.Forced water lubrication and cooling system will be closed.

      - INTERLOCKS:

V.T. Pumps will not start if lubrication system and cooling has not started functioning.V.T. Pumps will not start unless valve opening command in passed on.

      - TESTING AND INSPECTION FOR V.T. PUMPS:

All the nos. of vertical turbine pumps proposed shall be inspected and tested at the manufacturing works and site as below in the presence of Engineer’s representatives.HYDROSTIATIC TEST / DYNAMIC BALANCING / DYE PENETRATION TEST FOR V.T. PUMPS:

All pumps bowl assemblies shall be subjected to Hydrostatic test at manufacturer’s works. The test pressure shall be either One and One Half times the shut off head developed by pump level assembly or twice the rated head, whichever is greater and applied for standard time.

All pumps discharge heads and columns upto 10% shall be subjected to hydrostatic test pressure as specified at (a) above.

Dynamic balancing test of impellers and impeller shafts together shall be arranged at manufacturer’s

works, which will be witnessed by engineers (as per IS 1940-1973 II)

Dye penetration test for impellers shall be arranged at manufacturer’s works, which will be witnessed by

the engineer.

      - PERFORMANCE TEST AT FACTORY FOR V.T. PUMPS:

All pumps shall subjected to performance test as IS 1710 of 1972 at manufacturer’s works at full load and full speed by shifting one of electric motors for respective pumps to be supplied under this contract as primer mover. Performance testing shall include determination of head, discharge, power demand and efficiency over a range of cutoff to shut off head.

Site conditions for minimum no positive suction head shall be simulated as near as possible for testing purpose. The tenderer shall furnish the facility available agency and place for conducting above test.

The following values of parameters applicable for the site may be considered for calculation for NPSH by the contractor.

| Atmospheric pressure |  | 9.60 meters column of water |
| --- | --- | --- |
| Vapor pressure of water |  |  |
| (at 37.80 C normal temp.) |  | 0.6674 meters column of water |

      - OTHER INSPECTIONS AT FACTORY FOR V.T. PUMPS:

Contractor shall arrange for following inspections at manufactures works.Inspection for critical dimensions to components viz. dia, of line shaft, dia and wall thickness of column pipe, flange thickness of column pipe, thickness of sole plate etc.Inspection for verification of metallurgy of various components by reviewing metallurgical tests carried out by the manufacturer.

Inspection for machining or finish quality and undue wear of fast moving parts after trial runs by stripping down the machine.Inspection for verification of test observations and reports for stress relieving of components, specified earlier in detailed specifications.

X Ray test for impeller shafts shall be arranged at Manufacturers works, which will be witnessed by Engineer.

Vibration and noise level tests

      - TEST REPORT AND OTHER DOCUMENTS FOR V.T. PUMPS:

Contractor shall furnish to the Engineer the following documents before dispatch of material.

Test reports for chemical analysis of materials of construction for major components like impellers, pump shaft, line shafts bowl assembly etc.

Pump performance test reports with sample calculations and actual pump performance curves and pump performance test acceptance report.

Other test and inspection reports as above. Final construction drawings of the pump.

Operation, maintenance and spare parts manual for pumps.

##### DE-WATERING PUMP

One submersible / Horizontal Centrifugal type sludge type pump for dewatering the turbine pit shall be provided to handle water having high turbidity.

## SPECIFICATIONS FOR MECHANICAL EQUIPMENTS

##### DUAL PLATE CHECK VALVE:

- Type of Valve:

  - On the individual delivery line of the pump, Dual plate / Multi-door swing type of valves shall be provided.

  - On the common discharge header, the NRV shall be related and offered by the bidder to suit the surge characteristics and to ensure Closure before closing of NRV’s on individual delivery of pumps

- The valves shall be suitable for mounting on a horizontal pipeline and flow direction shall beclearly embossed on the valve body.

- Valves shall possess high speed closing characteristics and be designed for minimum slamcondition when closing.

- Multi-door Swing Type Valves:

- The valve shall be double flanged and conform to IS: 5312 (Part II).

- In case of multi-door swing type check valve, the non-slam characteristic shall beachieved by providing suitable combination of door and hydraulic passages withoutany external clamping arrangements or passages. The angle of sealing and doorweight shall be designed to provide the most efficient working with least restriction toflow.

- Valve of diameter greater than 450 mm shall be provided, in addition to others,supporting feet and jacking screws. Hinge pins / shaft shall preferably be square insection to ensure positive location of flaps and provide for secure fixing.

- Dual Plate Type Valves:

Dual plate check valves shall conform to API 594 and API 598. They shall have metal to metal sealing. The spring action shall optimize the equal closing rates of each plate especially when the friction coefficients are uneven due to one plate resting upon one another. The plates shall not drag on the seat while opening. The plates shall not vibrate under full or partial flow condition.

MATERIALS OF CONSTRUCTION:

| Body, cover, door, hinges | Cast Steel |
| --- | --- |
| Hinge, pins, door pins, Suspension pins | Stainless Steel, SS:304 |
| Disc facing | Leaded in Bronze IS 318 GR LTB 2G |
| Seating in body | Leaded in Bronze IS 318 GR LTB 2 |

| Bearing bushes, Body rings, | Leaded in Bronze IS 318 |
| --- | --- |
| Door faces | GR LTB 2 |
| Bolts and nuts | Carbon Steel |

TESTING

The valves shall be subjected to seat and body test in accordance with IS 5312 at the manufacturer’s works. These tests shall be carried out at manufacturer’s work in presence of Engineer or his representative, before delivery test certificate shall be furnished in triplicate. The valve rating, disc test pressure seat test pressure and body test pressure shall be as per IS or other international standards and shall be furnished along with bid.

The closing period of NRV should be mentioned by the manufacturer. Also the velocity range in which NRV open and closes should also be mentioned by manufacture. The NRV should be tested for closing and opening characteristics.

##### DOUBLE KINETIC AIR VALVES:

    - GENERAL:

  - The valve shall be capable of exhausting air form pipe work automatically when beingfilled.

  - The air being released at a sufficiently high rate to prevent the restriction of the inflowrate.

  - Similarly the valve shall be capable of ventilating pipe work automatically whenbeing emptied, the air inflow rate being sufficiently high to prevent the developmentof a vacuum in the pipelines. The valve shall also automatically release airaccumulating in pipe work during normal working conditions.

  - Air valve shall be of the double orifice type with a large orifice for ventilationexhaust of the pipeline and smaller orifice for automatic release of air under normal working pressure.

  - The valve shall be suitable for the maximum working pressures in the systems. All air valves shall be provided with isolating valve and flanged end connections.

  - Air valve shall be designed to prevent premature closure prior to all air having beendischarged from the line. The orifice shall be positively sealed in the closed positionbut the float (ball) shall only be raised by the liquid and not by a mixture of air

andliquid spray. The seating shall be designed to prevent the floats sticking after longperiods in the closed position

Kinetic Air Valve for vertical turbine pump set shall be provided and installed on the delivery pipe coming out from each vertical turbine pump. The valves shall be provided at suitable locations. Kinetic Air Valve shall be of two orifice type, the small orifice releasing air from pipe carrying water under pressure under normal working condition while the large orifice shall admit or release air when the pipe is being emptied or filled. The air valve shall be designed to operate satisfactorily at normal working pressure of the system. Each air valve shall be provided with an isolating sluice valve and having cast iron hand wheels for manual operations. Sluice valve shall be in conformation with IS 780 with gun metal spindle (Non-rising type.)

The testing of valve shall be done as per IS or any international standards.

Testing –

MATERIALS OF CONSTRUCTION:

Float chamber bowl	cast steel

And cover	Cast steel

Small Orifice Float	Stainless steel

Orifice	SS, AISI 304

Valve Seat, Nut	Leaded Bronze

The air valve along with the isolating valve shall be tested at manufacturer’s works in the presence of

KNNL’s representative as per the approved QAP.

##### DELIVERY PIPES/MANIFOLD

The scope of work includes:

Design of delivery pipes, manifold and rising main with respect to following aspects.

- Selection of diameter with wall thickness and number of rows of pipes to carry required quantity of water up to delivery with head loss calculations and total head requirement.

- Velocity of flow shall not exceed 2 m/sec in the rising main.

- Operating pressure, maximum gauge pressure and designed test pressure of system.

- Stability of pipe system.

- Protection against corrosion.

Supply, installation, jointing of delivery pipe from each pump to manifold including necessary butterfly valve, non-return valve and air valve including expansion joints.

Fabrication and installation of MS manifold out of MS pipe of sufficient diameter with required number

of inlets and outlets with flanges drafted end inspection manhole of suitable diameter with blank flanges with gaskets with a wall thickness to suit the maximum pressure.

Construction and installation of MS rising mains of suitable type diameter with required number of rows from manifold upto delivery chamber with anchor blocks saddles as required. Entire process right from design to commissioning shall be carried out as per relevant IS Standard. Rising main design shall conform to IS: 5822 and IS: 3589 (latest edition).

The contractor shall provide all the material required such as tapers, distance pieces, bends, nut bolts gaskets. The work of joining delivery pipelines to the respective manifolds for turbulence free smooth flow is included in this tender. Flanged joints shall be adopted for valves and but welding joints of flanged joints in jointing of delivery pipe.

Concrete saddles for valves and pipe work inside pump house shall be provided by the contractor as per design and drawings furnished by him and approved by Engineer.

The scope should include necessary excavation foundation with anchor supports concrete thrust blocks, outside the pump house for all delivery pipes/manifold rising mains.

    - MATERIAL OF CONSTRUCTION:

All the pipes and specials shall be fabricated out of steel plates confirming IS 2062.

The fabrication of pipe should generally confirm IS 1582-1966. The fasteners required for delivery pipe connections shall be of carbon steel.

The flange thickness shall be as per BS-1504.

    - PAINTING

The interior of the pipe work and specials shall be provided with coal tar epoxy inner lining and external pipe wrapping of thickness as per IS 1916:1989/IS: 3589-2001 (latest version).

GENERAL GUIDELINES

Manufacturing of MS pipes shall be done in conformity with IS: 3589 subject to following:

The pipe shall be fabricated out of steel plates or strips of mild steel conforming to IS: 2062 and having minimum specified tensile strength of 410 Mpa. MS pipelines shall be of grade 410, helical seams/spiral longitudinally welded with Straight seams, without circumferential joints with beveled ends as per IS 3589. The pipes shall be manufactured in an approved factory/fabrication yard having quality control system, well equipped testing laboratory.

The end of the pipes, short pipes shall be beveled end for welding.

- Manufacturing process shall ensure that

  - Base material i.e., HR coils/ steel plates shall be of required Quality.

  - Production equipment is well designed automatic machine.

  - Quality control is comprehensive.

  - Hydro test of each pipe before lining.

- The thickness of the pipe line shall be decided by the bidder to meet the requirements. Also the thickness calculations shall be furnished for approval of the owner before procurement.

C Flanges should be machined on both faces. Fabrication of flanges from segment plates should be avoided. However, if under special circumstances flanges from segment plates are to be provided, on specific instructions of the Owner, such flanges should be completely stress relieved after welding and all welds shall be subject to dye penetration test. These flanges should also be machined.

- All welds are to be continuous single V butt welds with finished head of size equal to thickness of plate. All welding shall be as per provisions laid in IS-816/equivalent standard (latest revision). Welding shall be done by experienced and good operators who have been qualified by tests as specified in IS-817/equivalent standard (latest revision). Welding shall be by automatic machine and shall be carried out by using approved electrode with compatible flux.

- Bolts and nuts shall be of hexagonal head conforming to -1367/equivalent standard (latest revision).

- The pipe sections shall be carefully placed on the sand bed prepared as per specification. All joints before welding shall be thoroughly cleaned and requisite welding gap maintained.

- Welding sequence shall be done in such a way so as to minimise the distortion due to welding shrinkage. Any distortion will be duly rectified by the bidder without additional cost.

- Welding shall not be carried out when the surface of the parts to be welded are wet for any cause and during periods of rain and strong winds unless the welder and work are properly shielded.

- Precaution shall be taken to prevent any crack or damage in the external coating during installation. Pipes shall be laid in trenches excavated along the route and the over-ground portion shall be installed as per final layout drawings.

- The damaged portion of External coating or internal lining of the pipe Length at the joints due to welding shall be made good by manual application of external coating/internal lining to the required thickness and shall form a smooth continuous surface particularly with internal lining of the two adjacent pipes welded so that the flow through the pipeline is not affected due to manually applied

coating.

- On completion of all welding in the pipe lines, the same shall be tested hydrostatically and after successful testing, shall be covered by sand wrapping and backfilling with earth where the pipes are laid in trenches

- Installed pipe shall be closed up at both ends at the end of each day by water tight plug or other means approved by the Owner to prevent debris/animals/human beings from entering the pipe.

- Specific Guidelines for Spirally/Longitudinally Welded MS Piping: All spirally/Longitudinally welded MS pipes proposed to be procured under this section shall be fabricated out of steel plates or strips of mild steel coils (HR coils) conforming to IS 2062 and to the requirements of IS-3589 or equivalent standard and shall have minimum thickness as per recommendations of standards which shall be got approved by the contractor. There shall be no negative tolerance in the thickness of the Plates used.

  - Tolerance on outside dia of pipes (12.3.1 – IS 3589-2001: Table 6)

Outside dia Tolerance (For all sizes)

For seamless pipes	±1% For Electric resistance Welded Pipes (ERW) & Submerged Arc

Welded (SAW) (including spirally Welded pipes) ±0.75%

Tolerance for straightness of pipeline (12.5.1 – IS 3589 –2001)

Each of the finished pipe shall not deviate from straightness by more than 0.2% of the total length. Checking shall be carried out using a taught string or wire from end to end along the side of the pipe to measure the greatest deviation.

Ovality (Clause 12.3.3 – IS 3589 –2001)

Ovality shall not exceed 0.75% of the specified outside diameter of the pipes.

- TESTING OF PIPES

The pipes shall be tested to the following requirements.

- Continuous monitoring of dia. Thickness, fabrication.

- Visual inspection of all pipes from inside and outside for permissible tolerances as per IS: 3589

- Online ultrasonic testing of weld and body as per IS: 4260 during welding

- Radiographic testing as per IS: 4853

- Each pipe shall be hydraulically tested IS 3589 at the manufacturer’s works

- Mechanical test of finished pipes as per IS: 3589.

- MARKING

Each pipe shall be legibly marked as per clause 18 of IS: 3589 with following details :

- Manufacturer’s name or trademark.

- Outside diameter & specified wall thickness

- Pipe designation

- QUALITY ASSURANCE

During the whole process of manufacturing, Owner’s representative shall have authority to supervise the Quality assurance process and witness the tests performed and also to get any pipe selected at random for repetition of tests and the Contractor shall carry out the tests at no extra cost to the Owner.

- FABRICATION OF MS SPECIALS AND FITTINGS

Unless and otherwise mentioned in the para below all MS specials and fittings (bends, tees, reducers, enlargers etc.) shall be fabricated using MS plate/sheet conforming to IS: 2062. the thickness shall be adequate to sustain field test pressure but shall not be less than the thickness of the pipe at that point. The Contractor shall submit the detailed drawing for each special to be used in the pipeline. On approval of the same by the Owner, the Contractor will take-up the manufacturing. All specials shall be manufactured and coated at the manufacturer’s premises. In exceptional circumstances when welding in trench is unavoidable a flanged opening shall be provided for access inside the special for welding. The Contractor has to ensure the timely manufacturing of the MS specials so that they can be laid in synchronization with the pipe laying. The joints of adjacent pipe stretches have to be made with gap pieces approved by the Owner.

On completion of the manufacturing, the coating and lining for the special will be done by the Contractor as per the specifications for coating mentioned in specification. The Owner or his representative may at his discretion check the same and if the lining and coating are found defective in quality or thickness, the Contractor shall carryout the tests on all the remaining pipes not laid, again in the presence of the Owner or his representative.

  - FLANGED BRANCHES

Flanged branches shall be fabricated in accordance with the general specification and to the Owner’s requirement. Flanged branches for air valves shall be welded into pipe in the required position. The branch for an air valve shall be vertical and at right angle to the longitudinal axis of pipe.

All the flanges shall be machined to standard thickness, square to the axis of the pipe.

  - BENDS

Bends to provide change of alignment in pipe laying shall be manufactured to suit the site conditions from manufactured and tested pipes by angle cutting of the barrel or by such other standard procedure

and re-welding. Bends shall be lined internally and coated externally as specified that for the pipes.

a) Bends shall be fabricated taking into account the vertical and horizontal angles for each case.

- The bends shall have welded joints and the upstream and downstream ends of each bend shall have a straight piece of variable lengths as required.

CI. When the point of intersection of a horizontal angle coincides with that of a vertical angle, or when these points can be made to coincide, a single combined or compound bend shall be used.

  - TAPERS

Tapers shall be manufactured out of steel plates and lined internally and coated externally. Stiffener rings shall be provided to afford rigidity to pipe. They shall be manufactured generally in accordance with IS: 7322.

  - MS FLANGES

Welding neck flanges confirming to IS 6392 be used in accordance to the design pressure at the place appurtenance with which they are to Be used. The flange drilling shall conform to IS: 1538.

The Contractor shall assemble the flanges in the exact position by marginal cutting, if necessary so as to get the desired position of the sluice valves etc., either vertical or horizontal and shall then fully weld the flanges from both sides in such a way that no part of the welding protrudes beyond the face of the flanges. In case the welding protrudes beyond the flanges and if the Owner orders that such protrusions shall be removed, the Contractor shall file or chip them off. If required and when desired by the Owner, the Contractor shall provide and weld gusset stiffeners, as directed on site.

  - BLIND FLANGES

Blank flanges shall be provided at all ends left unattended for the temporary closure of work and also for commissioning a section of the pipeline or for testing the pipeline laid. For temporary closure, non- pressure blank flanges consisting of mild steel plates, tack welded at the pipe ends may be used. For pipes subjected to pressures, the blank flanges or domes suitably designed as per Owner’s requirement shall be provided. The thickness of the blank flanges shall be as defined in IS: 6392 for the nominal size and design pressure at the place of installation, the flange drilling for all flanges upto 1500 mm shall conform to the provision of IS: 1538 and those above 1500 mm shall conform to IS: 6392.

  - STIFFENER RINGS

The Contractor shall provide stiffener rings wherever required as per designs. The Contractor shall weld the same to the pipes with one circumferential run on each side.

  - MANHOLES

For manhole installation, a fabricated tee with one side flanged must be used. The size of manhole shall not be less than 600 mm and it shall project at least 27.5 cm above the pipe crown. The 600 mm

end must be provided with blind flanges.

  - CLOSING OR MAKEUP SECTIONS

Closing or make up sections shall be furnished at appropriate locations on the line to permit field adjustments in pipeline length to compensate for shrinkage in field welded joints, differences between actual and theoretical lengths and discrepancies in measurements.

  - TEST HEADS

Test heads may be ellipsoidal, standard dished as per relevant ASME code or hemispherical heads. They shall be welded and removed after the test. Allowance shall be made in the length of the pipe section receiving the test head for the welding and removal of the head and preparation of the plate edges for the final weld after testing.

xi) DISMANTLING JOINT

All butterfly, or any other online valves etc. shall be installed between flanges with a flexible MS dismantling joint at one side. The joint must allow dismantling of the valve etc. without causing stress to the joints of the attached pipes. The minimum clearance of the dismantling joint shall be five (5) cm. The pressure class of the dismantling joint shall be the same as that of the pipe. Drawings of the dismantling joint shall be submitted to the Owner for approval. The nuts and bolts of the joint shall be galvanized. The joints shall be painted/ coated as per specification given for exposed pipes.

- INSPECTION AND TESTS ON PIPE AND FITTINGS / SPECIALS

The hydraulic test pressure shall be as per clause 13 of IS: 3589 for specials. Dye penetration test as prescribed in IS: 7322 and VT is acceptable in lieu of hydraulic test for bends only.

All works and material under specification will be rigidly inspected during all phases of manufacture and testing and such inspection shall not relieve the Contractor of his responsibility to furnish material and perform work in accordance with these specifications.

The Owner or the authorized inspection agency shall have free access to those parts of the plants that are concerned with the furnishing of materials of the performance of work under this specification. The bidder shall furnish the Owner reasonable facilities and space without charge for inspection, testing and obtaining of any information he desires in respect of the quality of material used and the progress and manner of work.

Contractor shall provide and operate suitable equipment capable of conducting the specified hydraulic test pressure to the inside surfaces of the pipe and of sustaining the required period.

PAINTING & COATING

Lining:

The inner surface of over ground/buried pipe shall be provided with epoxy paint.	The following are the procedures generally adopted.

Cleaning:

Pipe surfaces shall be thoroughly cleaned and dried before the application of lining / coating, and shall be free of dirt, grease, oil rust, scale or other foreign matter. The pipe shall be cleaned by any one of the following methods:

- Grit/shot blasting

- Sand blasting, and

- Mechanical cleaning

Before sand or shot/ grit blasting, all oil and grease if present on the metal surface should be removed by using suitable solvent and clean rags. Other foreign matters which cannot be removed by blast cleaning should be removed by suitable means. Surfaces then should be thoroughly cleaned by blast cleaning and the operation should remove scale, rust or any other superficial impurities from the surfaces exposing base metal presenting a grayish matter appearance except that slight shadows, streaks or discoloration caused by rust stings or mill scale oxides need not be removed.

Adequate moisture separators should be used so as to remove effectively oil and moisture from the air supply of the blasting unit. After cleaning, the pipes shall be protected from and maintained free from all oil, grease and dust that may fall on the pipes from outside sources till the pipe has received lining / coating.

Any pipe, that show deep pitting after blasting has been done, should be set aside pending examination by the Owner or his representative for approval for reconditioning or rejection.

INNER EPOXY COATING:

The MS pipes after fabrication and cleaning as described above should be epoxy coated in the internal surface. The surface is to be provided with 1 coats of 40micron thick zinc rich epoxy primer and 3 coats of 122 micron thick each coat coal tar epoxy paint.

EXTERNAL TAPE COATING FOR MS PIPE

Outside surface of buried / over ground steel pipes and fittings shall be protected by the application of Pipe coating of fibres, coal tar and solvent based rubber modified bituminous primer of density 0.92 gms/cm and viscosity of 1000-2000 cps @ 150 gms/sqm followed by seven layers (4 mm thick) of polythene polymerized bitumen and polyester of total 7 layers pipe coat 4 mm should conform to requirement of IS-10221 and AWWA C-203 for prefabricated tapes.

- CEMENT MORTAR COATING REINFORCEMENT

Unless otherwise specified by the Owner, the reinforcement for the coating of pipe sections shall be spiral wire

fabric/mesh of approved gauge size (ribbon mesh). Reinforcements shall be free of oil, grease, and

other contaminants that might reduce the adherence between the coating and reinforcement. All reinforcement shall be placed in the middle third of the coating. When cement mortar coating is applied over a dielectric undercoat, the reinforcement shall not be attached to or otherwise be in contact with the steel pipe.

SPIRAL WIRE AND WIRE MESH

Attachments of ends and splices in the wire shall be by welding or other suitable means acceptable to the Owner. Maximum spacing of the wire shall be 35 mm. The wires on 50 mm spacing on the 50mm x 100mm fabric shall extend circumferentially around the pipe.

Attachment of ends and splices in the wire shall be approved by the Owner. In 25mm x 25mm fabric, the spiral lap shall be 35mm and the sliced lap shall be 110 mm minimum.

APPLICATION OF MORTAR COATING

Mortar coating shall be applied by mechanical or steam pneumatic placement to the specified thickness in one or more continuous application and shall consist of not more than 3 parts sand to 1 part cement by weight.

The water in the mixture shall be carefully controlled so that mortar will not run, sag or segregate.

The soluble chloride-ion (Cl) content of the cement mortar mix shall not exceed 0.15 percent expressed as a percentage of cement weight.

Allowance shall be made for splices of reinforcing wire. When reinforcement of special wire type is used, the end of the wire at the edges of the portion to be left uncoated shall be attached to the pipe shell by welding or other suitable means.

If applied in more than one course, the interval between the first and last course shall be not more than 2 hrs. The mortar shall be projected at high velocity against the exterior surfaces of the pipe or shall be applied by an equivalent method to produce a hard , tight adhering coating of the specified thickness in one or more continuous applications.

DEFECTIVE COATING

If any sand pockets and porous spots occur they shall be completely cut out and replaced by pneumatic placement or hand application of mortar in the proportion of 2 parts sand to 1 part cement, by weight.

COATING CRACKS

Care shall be exercised to minimize the occurrence of cracks in the mortar coating. Repair procedures shall include the brushing or wiping of near cement into cracks, autogenously healing of the cracks by additional moist curing the painting of the cracks with an epoxy coating, or combination of these methods.

DAMAGES TO LINING/COATING

During the process of welding the pipe joints or any other location, the inner lining and outer coating may get damaged. At all such locations, the damaged or peeled off portion of the lining/coating shall be restored by Hand application of lining/coating material. Such application shall also ensure smooth continuous surface at all the joints to ensure smooth flow of water.

CURING OF COATING

After the initial set has taken place, the mortar coating shall be cured by the moist or accelerated curing methods or unless otherwise specified by the purchaser, a membrane material may be applied immediately following the coating application. Moist and accelerated curing may be used interchangeably on a time ratio basis of 5 hrs or moist curing to 1 hr of accelerated curing, except curing temperatures shall not exceed the maximum allowable for dielectric undercoat material.

The coating shall be kept continually moist by intermittent or continuous spraying for a period of at least four days. Moist curing may be used only if the minimum ambient temperature exceeds 5 deg-c continuously during the minimum required curing period, and no credit shall be allowed for any time during which the temperature drops below 10 deg-c.

ACCELERATED CURING

Accelerated curing of the pipe or special may begin immediately after completion of the coating operation or within 6 hrs thereafter. The temperature of the pipe or special shall not exceed 30 deg C until the cement mortar coating has taken its initial set or until a period of 3 hrs has elapsed, whichever occurs first. The relative humidity shall be not less than 85% at a temperature between 45 deg C to 65 deg C for at least 18 hrs.

Coating of Specials- Mortar coating for pipe bends & other special section shall be reinforced with wire fabric or ribbon mesh. Fabric shall be applied over surface of pipe to be coated and shall be held away from pipe shell with self-furring mesh, furring clips etc. The application of coating shall conform to clause 5.6 of AWWA C-205 with the exception that hand application shall be substituted for mechanical/ pneumatic placement. Thickness shall be as required for straight section.

MEMBRANE CURING

Membrane curing shall consist of the complete encapsulation of the coating by application of a material that will retain the moisture of the applied cement mortar coating.

PRECAUTIONS

During the entire period of the application of the lining and coating and the curing thereof, the section shall be carefully supported and handled to avoid damage to the mortar. If a pipe section must be moved such an operation shall be done with every reasonable precaution to protect against damage.

Any damaged portion of the lining or coating shall be cut out and replaced.

DRAWINGS, CURVES AND INFORMATION REQUIRED

The various drawings/data and documents to be furnished by the successful BIDDER after award of contract shall include the following

- A complete list of all piping and fittings of various sizes including but not limited to transition, bends, taper pieces, bulkheads, manhole arrangement with their quantities and details eg. nominal size, O.D, I.D (as applicable), thickness, design pressure, material of construction/code/standards etc.

- GA of piping system based on tender drawings on verification of site condition.

- A complete list of all valves and specials with their Data Sheets

- Manufacturer's catalogue indicating complete range of available size and rating of pipes and fittings and other procured items.

- Descriptive literature on the manufacturing process and quality control procedures highlighting the manufacturing, fabricating and testing facilities available in the shop.

  - Detailed fabrication drawing showing the sizes, materials and weld edge preparation etc. The fabrication drawings shall give all necessary information for fabrication, erection and painting of steel work in accordance with provisions of this specification. Welding symbols used shall be in accordance with the requirements of IS:813 latest revision and shall be consistent throughout. Weld lengths called on the drawings shall be net effective lengths.

- Welder’s Qualification record.

  - Bidder shall submit working drawing for excavation, sand-Filling and backfilling purpose as mentioned earlier.

  - Any other drawings or calculations that may be required for the clarification of work.

  - Instruction Manuals covering maintenance, repair and replacement of equipment fabricated and supplied by the BIDDER.

TESTING

All the tests mentioned in the following shall be arranged by CONTRACTOR.

    - RADIOGRAPHY: The Longitudinal & circumferential joints will be random radio graphed limited to 2% of the total number of pipes for longitudinal joints and 5% of number of joints in case of circumferential joints at the discretion of the OWNER. The testing shall be arranged by the CONTRACTOR. Necessary labour & materials for welding of support etc. required for carrying out X- raying shall be provided by the CONTRACTOR for carrying out the test.

    - ULTRASONIC TESTING:

Longitudinal and circumferential joints will be subjected to ultrasonic sound test randomly to the extent of 2% of number of pipes for longitudinal joints and 5% of the number of circumferential joints. Necessary labour, equipment ad material required shall be provided by the CONTRACTOR for carrying out the test.

    - Dye penetration test on the root runs shall be carried on 100% joints after grinding before proceeding with filler runs.

vi)	RECTIFICATION & RETESTING:

Any defect noticed by radiographic / U.T shall be provided by the CONTRACTOR free of cost. The re- testing charges will be to the account of the CONTRACTOR.

HYDRAULIC TESTING OF PIPELINE Each pipe shall be hydraulically tested after the pipe is internally cement mortar lined / externally coated in accordance with AWWA M11. Water required for testing shall be arranged by the BIDDER at his own cost.

All the longitudinal and circumferential welded seams shall be subjected to chalk and kerosene test prior to hydraulic testing of the complete pipe line. This shall be done in the presence of the Owner. In addition to this, test coupons shall have to be provided for each longitudinal seam for mechanical tests (tensile and bend), if considered necessary by the Owner. The test coupons are to be broken in presence of the Owner. Bidder shall satisfy the Owner that work is being carried out in accordance with the specification drawings and other conditions. Owner shall have full access to the Contractor's working area.

Testing shall be done before backfilling & under dewatered condition. However, the bidder shall backfill & compact the soil in the region of bends to avoid undue thrust on the anchor blocks. Any temporary arrangements that may be required to ensure stability of pipeline are also deemed to have included in the quoted rate.

The hydraulic test pressure is usually applied for a period of 24 hours before the test is assumed to begin, primarily to allow for the lining material to absorb as much water as is possible. After that the pipeline should be inspected for evidence of leakage.

BACKFILLING OF PIPE LINE TRENCHS:

This section covers specification for the work consists of backfilling the pipeline trenches with selected soil from excavated/selected soil from borrow area in layers of 150mm thickness including watering and compacting the backfill to the desired compaction etc., complete with all leads and lifts.

All fill material will be subject to OWNER’s approval. If any material is rejected by OWNER, Bidder shall remove the same forth with from the site at no extra cost. Surplus fill material shall be deposited / disposed off as directed by OWNER after the fill work is completed.

No earthfill shall commence until surface water discharges and streams have been properly intercepted

or otherwise dealt with as directed by OWNER.

Material to the extent available, selected surplus soils from excavated materials shall be used as backfill. Fill material shall be free from clods, salts, sulphates, organic or other foreign material. All clods of earth shall be broken or removed. Where excavated material is mostly rock, the boulders shall be broken into pieces not larger than 150mm size, mixed with properly graded fine material consisting of murum or earth to fill up the voids and the mixture used for filling.

If any selected fill material is required to be borrowed, Bidder shall make arrangements for bringing such material from outside borrow areas. The material and source shall be subject to prior approval of OWNER. The approved borrow area shall be cleared of all bushes, roots of trees, plants, rubbish etc., top soil containing salts / sulphate and other foreign materials. The materials so removed shall be burnt or disposed off suitably as directed by OWNER. Bidder shall make necessary access roads to borrow areas and maintain the same, at his cost, till completion of the work.

FILLING IN TRENCHES

After laying and testing of the pipeline and construction of valve cistern, anchor blocks, thrust blocks etc., the filling in trenches shall be commenced immediately with soft selected excavated materials. This shall be done without any delay. The materials shall be laid, adequately watered and tamped in layers of 23 cms with a small tamper under, around and over the pipes and specials upto the original ground level taking due care that no damage is caused to the pipes, specials, structures etc. The compaction shall comply with the specified density at moisture content, differing not more than 4% from the optimum moisture content. The Contractor shall arrange for sampling and testing of the filling as directed by the Owner to ascertain whether specified density has been achieved. The cost of all such sampling and tests shall be borne by the Contractor and is deemed to be included in the rates quoted. Filling of the trenches shall be carried simultaneously on both sides of the pipe to avoid unequal pressure on the pipe.

Backfill shall not be dropped directly upon or against any structure / facility where there is a danger of displacement or damage. Trucks or heavy equipment for depositing or compacting backfill shall not be used within 1.5m of head walls, piers or other facilities which may be damaged by their weights or operation method of compaction. The method of depositing and compacting backfill shall be approved by owner.

SURGE ANALYSIS AND PROTECTION:

The Contractor shall carry out surge analysis duly taking in to account the characteristics of the

pumping units, the length of rising mains and its configuration up to the delivery pond including valves, Dismantling joints, etc. and propose a system suitable to take care of the surges during tripping of power supply.

The surge shall be calculated as per standard procedure considering at least the following events -

- Water hammer in pump discharge line caused by power balance.

- Due to sudden failure of single pump where multiple pumps are in parallel

- Due to variation in discharge.

- Due to sudden stoppage of pump due power supply failure.

Adequate surge protection to the rising mains and the entire system shall be provided, subject to the approval of KNNL.

  - BUTTERFLY VALVES & DISMANTLING JOINTS

GENERAL

Each pump shall be provided with a butterfly valve in the delivery pipe. The butterfly valve shall be flanged water works pattern, eccentrically pivoted and shall be electrically actuated. The actuators shall suitable for opening and closing against the maximum head realized under operating conditions and any necessary spur or other gearing and links etc. shall be incorporated. The actuator motors shall be complete with limit switches, interlock switches for remote control and contacts for close, open, in operation and percentage opening position indications. The actuators shall be suitable for operation with DOL starting on 415 V, 3 phase, 50 Hz AC power supply. Necessary arrangement with hand wheels shall be provided for emergency manual operation with suitable interlocking mechanism to prevent the actuator operation when the valve is being operated manually and vice versa. The actuator shall be located at motor floor and so also the manual operation of valve shall be from motor floor. The valves shall generally conform to BS 5155.

The closing time for electrical actuator shall be from decided suiting to the design requirements. The actuator shall incorporate Backlash hammer blow feature.

The broad specification of the butterfly valve is as detailed below –

| Body / Disc | Fabricated / cast steel ASTM 516 or IS 2002 Gr. 2A |
| --- | --- |
| Shaft | St. Steel (BS 970 431 S29) |

| Clamping Ring Segment: | St.Steel ( ASTMA 479 Type 304/ A 351CF8) |
| --- | --- |
| Bearings | St. Steel Backed PTFE |
| Rubber seal | Precision moulded nitrite rubber ring |
| Ring | (shore hardness 55 to 65) |
| Hardware | Stainless Steel |

Used inside

Inside portion of the valve shall be painted by coal tar epoxy paint.

  - DISMANTLING JOINT

A dismantling joint shall be provided in delivery pipe line of each pump. The dismantling joint shall be placed between pump and non-return valves and shall be fabricated from M.S. plates designed to withstand the 1.5 times of working pressure. However, plate thickness for barrels shall not be less than 10 mm. The design of the joint shall ensure that no forces are transmitted to the pump foundation and the flanges of dismantling joints are held rigid during normal working. For dismantling it should be possible to slide flanges at one end by at least 50 mm to enable dismantling and refitting. General arrangement drawing shall be got approved from the engineer-in-charge before actual fabrication of the joint.

  - LOCAL OPERATION SWITCH

Local operation switches near the valves should invariably be provided for operation of the valves.

TESTING

The valves shall be subjected to disc, seat and body test in accordance with IS / international standards at the manufacturer’s works vide table below. This test shall be carried out in presence of engineer or his representative before delivery test certificates shall be furnished in triplicate.

Electric Actuator

- Electric actuators shall consist of followings:

  - AC electric motor

  - Reduction gear unit

  - Torque switch

  - Limit switch

  - Continuous Local Indicator

  - Hand Wheel for manual operation

  - Hand auto lever with locking arrangement

- All local controls shall be protected by a lockable cover.

- Each actuator shall be adequately sized to suit the application and be continuously rated to suit the modulating control required. The gearbox shall be oil or grease filled and capable of installation in any position. All operating spindles, gears and headstocks shall be provided with adequate points for lubrication.

- The valve actuator shall be capable of producing not less than 1½ times the required valve torque and shall be suitable for at least 15 minutes continuous operation.

- The actuator starters shall be integrally housed with the actuator in robustly constructed and totally enclosed weatherproof housing. The motor starter shall be capable of starting the motor under the most severe conditions.

- The starter housing shall be fitted with contacts and terminals for power supply,remote control and remote positional indication, and shall also be fitted with internal heaters so as to provide protection against damage due to condensation. Heaters shall be suitable for single phase operation. The heaters shall be switched “ON” when the starters are “OFF” and shall be switched “OFF” when the starters are “ON”.

- Each starter shall be equipped as follows :

2 Nos. Three phase magnetically operated line contactors with no-volt release and electrical and mechanical interlock.

1 No Three phase thermal cut-out device.

1 No. Control circuit transformer fully protected by fuses on primary and Secondary circuit.

1 No. Set of “Open”, “Close” and “Stop” buttons.

1 No. Local- Off-Remote switches with padlocking facilities.

1 No. Set of torque and limit switches for “open” and “Close” positions.

3 No. Sets of auxiliary limit switches in each direction.

Valve position indicator and hand wheel for manual operation.

- Reduction gear unit:

Gearbox shall have a life of 1, 00,000 hours, be selected in accordance with AGMA recommendation for horsepower calculation and service factor application

  - E.O.T. CRANE

GENERAL

Suitable capacity EOT crane is to be installed in the Pump House. These cranes are meant for use for erection assembly and maintenance of pumps, motors and other related equipment in pump houses. The pump house building will be having RCC beams/steel beams over which gantry rails for longitudinal travel are to be fitted.

SCOPE OF WORK.

The scope of work of this specification shall include Design, Manufacture, test at works before dispatch, supply at site, erection load and overload testing, commissioning at site and setting to work with related equipment training and services as per requirements of this specifications and furnishing required drawing, literature etc. as a part lump sum turnkey contract for LIS.

The broad scope -

- Design, Manufacture, supply, erection, tests at work of E.O.T cranes conforming to latest editions IS-807, IS-3177 and to this specifications.

- Gantry Rails: - Gantry Rails for the full bay length along with continuous supporting sole plates, foundation plate anchorages, packing plates etc.

- Down shops Leads: - Down shop leads of copper bus bars complete with supporting and strain insulators, brackets and other fixtures. The DSL shall be of shrouded type.

- Working out and finalizing the arrangements of supplying necessary equipment for cranes to connect main on incoming supply cable to the down shop leads together with the main switch of adequate rating before the down ship leads. The cable up to the main switch fuse unit from L.T panel will be provided by the contractor. The main switch shall be located as per direction of Engineer – in – charge.

- One set of slings and shackles each at each pump houses required for use of crane for all purpose. The scope of this specification shall not be limited only to the one enumerated above but shall also include the following:

- Preparation and finalization of layout and fixing details of gantry rails and down shop leads and getting approval from Engineer.

- Necessary block out details for fixing the gantry rails and down shop leads will be prepared by the Contractor and got approved from Engineer. All the civil engineering works like grouting of foundation for gantry rails and down shop leads will be done by Tenderer only.

- Supplying and providing proper earthing of the crane structure, motor frames and metal cases of all electrical equipments.

- First filling of oil, grease etc.

The intent of this specification shall be to execute work on a Turnkey basis from the design till the crane is commissioned and put in to operation successfully at site as a part of the total lump sum contract as per the terms and conditions of this specifications. Crane shall be robust and suitable for humidity and dust.

APPLICABLE STADARDS:

Code of practice for design manufacture, erection	IS 807-1976 and IS 800

And testing of crane and hoist(Structural portion)	1962 , IS 1137 1967 And general design.

Code of practice for design of overhead travelling	IS 3177-1977

Cranes and gantry cranes other than steel work crane.

–do- of crane rail	IS 3443

–do – steel structural	IS 2062, IS 226

–do- Hooks	IS 3815, IS 482 C TYPE

-do- Ramshom	IS 3017 / IS 5749

–do- Gears	IS 1570

–do- Motors	IS 325

–do- wire ropes	IS 2266-1977 (2365/70)

–do- Cable and testing.	IS 3177 & IS 466

All other associated equipments / materials such as steel casting welding, conductors switch gears shall confirm to the relevant IS / BS/ Other international standard.

TYPE AND RATING:

The E.O.T cranes and associated equipments shall be designed and manufactured to comply with the particulars detailed below. The other details shall be go approved from the Engineer, before taking up the assigned work.

Sl.No.  Description	Particulars

Type of class of EOT	Medium duty for classification of IS :807 /1976 class II in door type, and with pendent control complete.

Capacity (S.W.L)	As per requirement of main & auxiliary hooks. Span i.e. Distance between c/c of		As per requirement gantry rail.

Size of gantry rails	As approved

No of longitudinal travel wheels	As required

Length of gantry rails	As per requirements

Operating speed:

- Long travel:	20M /min

- cross travel:	Max 10 M/min

- Hoist	2M /Min

- Aux hoist	5M /min

- Micro hoist speed	10% of Main hoist speed

- No of falls (wire rope)	8 falls

Head room above gantry rails.	Other details to be got approved from the

Engineer to suit the respective pump house.

SERVICE CONDITIONS.:

The crane shall be designed to operate under all service conditions- i.e. lifting lowering, holding, travelling and or cross travelling at the prescribed speeds with any load from self-weight up to maximum load for which crane is designed this has also to work in cement dust in air and 100% humidity conditions.

LOAD INDICATIONS:

The crane bottom block shall bear a permanent inscription on each side readily legible from the floor level stating safe on main and Aux hook.

FACTOR OF SAFETY:

It shall be guaranteed by the tenderer that safe mechanical stresses adopted in designing the equipment and the component under all specified conditions of operation and the component under all specified conditions of operation and the stresses adopted are conservative. Whenever necessary, the tenderer shall provide access to all technical calculations in respect of the crane. The crane shall be so designed and manufactured that, when it is working under worst conditions of loading in service, the stresses on any part shall not exceed the permissible stresses stipulated in the latest edition of relevant IS. The factor of safety for all parts of crane shall be as per relevant B.S or I.S. the relevant standards adopted for factor of safety for various parts of the crane shall be stated in the tender along with the

value of factor of safety adopted the contractor shall furnish the structural calculations showing clearly the calculated stresses, factor of safety adopted and the maximum permissible stresses in respect of end carriage assembly, bridge assembly and crab assembly.

CONSTRUCTION:

STRUCTURE:

The crane structure shall be designed for the worst conditions of loading, crane be taken to allow for the appropriate impact factor (inertia forces including shock) and the lateral thrust etc. in accordance with

I.S 807. All the structural parts of the crane shall be fabricated from tested weldable quality steel confirming to IS 2602, test certificates for which shall be furnished to the purchases by the contractor before taking up the fabrication work. The crane structure shall be so designed that the actual calculated stresses for the severest combination of loads shall not exceed the permissible stresses in accordance with the above mentioned para “Factor of safety”.

CRANE BRIDGE:

Cranes below 10 MT shall be of single girder type and above 10 MT shall be of double girder type. It shall be fabricated from tested weldable quality steel confirming IS 2602. The bridge shall be so designed that in addition to complying with the requirements of allowable working stress, vertical deflection caused by the safe working load with crane in the central position of the bridge, shall not exceed 1/900th of span.

The ends of the main girder shall extend over the full width of the carriage and the extensions shall have sufficient section to take maximum reaction from the girder. The crane shall be anti-vibration design the box girders shall be designed to limit the natural vibration damping time to less than fifteen seconds. Appropriate calculations showing the camping of vibration in the structure must be submitted to the department.

A platform of the checkered plating minimum 750mm in clear width and properly guarded with double tiered tubular hand railings of 1100mm height and toe guard of minimum height of 75mm shall be provided on driving girder of the crane throughout the span.

Track shall be provided on the top of the crane bridge girders for travel of the crab.

All parts of the crane shall be readily accessible for maintenance and provisions should be made in the design accordingly. For easy assembly / erection at site all parts of the crane structure shall be aligned and match-marked at works before dispatch.

CRAB:

The crab shall be fabricated from the rolled steel section fully welded together and shall carry the necessary hoisting and cross traversing equipment. Jacking points for crab should be clearly marked and noted on the crane necessary jacking pads shall be provided for this purpose. The ends of the traversing rails shall be fitted with end stops to prevent over traversing of the crab. Rubber buffers shall be provided for the crab. Wheel skid shall also be provided for cross travel motion.

END CARRIAGE:

The end carriage shall be fabricated from the rolled steel sections and shall be rigid box construction of one piece construction provided with suitable diaphragm plates. The wheel base shall be not less than one fifth of the span. The ends of the travelling rails shall be fitted with end stops and wheel skids, to prevent over running of the crane.

Rubber buffer shall be provided on the end carriage. The end carriage shall be fitted with suitable guards to prevent the crane from derailing. It shall be provided with suitable jack pads on the both the ends. The jacking points shall be clearly marked and noted on the crane. The end carriage shall be designed to enable the track wheels to be withdrawn readily. Suitably arrangements for locking of the wheels with the gantry rails, when the crane is not in use shall be provided on each of the end carriage at both ends. Mechanical jack of suitable capacity and lift shall be provided for the inspection/replacement of wheels of end carriage and crab.

Wheels and bearing housing assembly:

All the wheels of the crane and the crab shall be double flanged closed die-forged The hardness of the surface shall be approximately 350 BHN, gradually reducing inwards up to 280 BHN at the depth of 15 to 20 MN. The materials of the wheels shall be c-65 conforming to IS-1570.

All the wheels of the crane and crab shall be housed in “L” type bearing housing assemblies on either side of the wheels for easy removal and maintenance, the bearing provided shall be spherical roller bearings.

LONG TRAVEL MACHINERY:

THE longtravel motion machinery system shall consist of the enclosed oil lubricated horizontal type reduction gear box which is driven by an electric motor suitable on the platform. The output shaft of the gearbox shall extend on both sides coupled to the long travel shaft which drives two wheels of the

crane bridge. The entire transmission system on the output shaft of the long gearboxes shall be designed with use of geared fixable coupling.

Totally enclosed self-resetting two way lever type limit switches shall be provided to limit. over travelling of the bridge in both directions. Electro-hydraulic thruster operated brakes shall be provided on long travel motion which applied automatically, when the current to crane is off and brings the end carriage to the stop without any shock.

CROSS TRAVERSE MACHINERY:

THE cross-traverse wheels of the crab shall be driven by an electric motor through a totally enclosed oil immersed speed reduction gears having machine out teeth. The entire transmission system on the output shaft of the cross-traverse gears box shall be designed with use of geared flexible coupling.

An Electro-hydraulic thrasher operated brake which applies automatically when the supply is off shall be provided to bring the crab to rest without shock. Totally enclosed self-resetting two easy lever type limit switches shall be provided to limit over traversing of the crab in both direction, the cross-travel rail section and wheel width shall be the same as of long travel.

MAIN HOUSING EQUIPMENT:

The main housing equipment shall consist of fabricated mild steel rope drums or from seamless pipe confirming to the relevant IS or BIS and driven by an electric motor through to a totally enclosed oil immersed speed reduction gear.

The rope drum shall have grooves machined to suit the hosting rope. The drum will be of such size that there will not be more than one layer of rope of the drum when the rope is fully wound. Also length of the drum shall be that each lead of rope has a minimum of three full turns on the drum when the hook is in lowest position and spare groove for each rope lead when the hook is in the highest position. The coupling between the hoist gear box and rope drum shall be with flexible gear joint. The machine cut grooves shall be similar on both side of the drum so as to ensure equal distribution of the load on the two main beams of the crane bridge. Grooving shall be free from the surface effects liable to ensure the rope. Rope anchorage shall be easily accessible.

A pulley block with cast steel pullies with ball or roller bearings shall be provided with guards to prevent the rope leaving the sheaves when the hook is resting on the ground. The sheaves shall be machine

grooved to a depth of not less than 1.5 time the diameter of the rope. The grooves shall be finished smooth and shall be free from surface defects likely to injure the rope.

The main hook for the crane shall be Ramshorn type and shall be forged steel and treated for proof lead. The hook shall be carried in a trust ball bearing with freedom to swivel and shall conform in all respects to the British Standards(BS) No.3017 or 5749. Special precautions shall be taken to achieve an absolutely vertical movement of the hook. A locking device shall be fitted to prevent rotation of the hook whenever required it shall be possible to lock the hook in any position. The hook and block shall be arranged to lift or lower without twisting or horizontal shifting. The snatch block shall be fitted with guards to prevent the rope from leaving the pulleys. Certification giving actual chemical composition and physical properties for the main material shall be forwarded in original.

The hoisting rope shall be of best plough steel standard construction having the breaking strength in accordance with IS 2365 /70 or equivalent BS. The factor of safety under working conditions shall not be less than six (6). The diameter of outer wires of the rope and the diameter of sheaves shall be so chosen that the wire rope have sufficient fatigue resistance to withstand the effects of breaking and vibrations. The diameter of outer wire, the guard of wire and the distribution of wearing surface shall be so selected as to have sufficient abrasive resistance. The tenderer shall clearly state the methods adopted for selecting the diameter of outer wire as careful balancing of above properties is essential in selecting the same. The lay of the rope and the No. of strands shall be so selected that the rope shall have sufficient lateral stability.

The electro hydraulic thrasher operated brake shall be provided with adequate margin of safety to hold the load to prevent it from coming down when the current supply to the hosting motor is cut off accidentally or intentionally.

Mechanical Braking:

The mechanical load brake shall be provided in the hoist mechanism of main hook to hold the load in the event of failure of electrical brake. This brake shall be capable of preventing over speeding of the load in the following direction to facilitate accurate shooting. The design of mechanical load brake shall be such that down word slipping of the load is eliminated and accurate positioned of load is possible with 2-3 mm.

MICRO SPEED ARRANGEMENT FOR MAIN HOIST:

To achieve precision while lowering and hoisting the main hook at the 10% of the speed of main hoist, the hoisting machinery shall be equipped with a micro speed arrangement through electromagnetic clutch.

AUXILIARY HOSITING EQUIPMENT:

The auxiliary hoisting equipment shall be generally of the same type as the main hoisting equipment except for the provision of the mechanical brakes, and the macro speed arrangements. The auxiliary hooks shall conform to the relevant IS or BS. It shall be provided with an electro hydraulic thrasher operated brake which applies automatically when the power supply is cut off. The brake shall be suitable for continuous operation.

GRAVITY LIMIT SWITCH:

THE gravity limit switches shall be provided for Main and Aux. Hoisting Motion, these limit switches shall be provided in power, Circuit in addition to Rotary limit switches.

BRAKES:

All brakes shall be designed for continuous service conditions having a brake torque of not less than 150% of full load torque. The rubbing surface of the brake drum shall be accurately machined and shall be free from surface defects. The rubbing shoes of the brakes shall be self-aligning and lined with renewable asbestos of Ferrodo lining. The temperature of the rubbing surface should not exceed 200C under working conditions. The test report for this shall be submitted by the contractor. The brakes shall be provided with simple, easy and accessible means of adjustment of the lining. the terminals of the brake magnets shall be protected from accident contact and the winding shall be effectively protected from mechanical damages and weather exposure wherever necessary.

ELECTRO HYDRAULIC THRUSHTER BRAKE:

  - Brake shoes with large cooling surface shall be provided.

  - Electro Hydraulic thruster: class B3 phase continuously rated motor shall be provided to drive the centrifugal pump. No. of switching operating per hour for the motor shall be stated.

  - compression springs: -the brake shall be released by the electro-hydraulic thruster exerting thrust against the spring pressure. Dust excluding seals shall be provided.

LUBRICATION: -

Provision shall be made for lubricating all the bearings. Ball and roller bearings shall be suitably lubricated before assembly. The lubrication tubes from individual points will be brought to a single board for case of maintenance. However, the number of such groups not be more than five. A lubricating chart shall be provided indicating

Lubricant and recommended frequency of lubrication.

The lubricating nipples adopted and the tubes shall confirm in all respects to the relevant Indian standard or equivalent British standard.

The contractor shall apply sufficient quantity of lubricant for the first filling together with hand greasing gun.

EMERGENCY BRAKING: All the brakes shall irrespective of controller’s position be applied

immediately on pressing of an emergency stop push button to be provided.

GEARING AND GEAR BOXES:

ALL gearing for the crane shall be precision machine cut and shall have involute tooth with a pressure angle of 20. The gears and pinions shall be forged as per IS 1570 and they shall have minimum hardness of 250 BHN. They shall have a factor of safety not less than 6(six) under severe working conditions. Gear boxes shall be fabricated from the mild steel IS 226 or 2062 and they shall be totally enclosed dust proof, oil bath type and will have an un split oil sumps. The gear boxes shall be provided with inspection covers to enable to visual inspection of the working parts. Oil level gauges shall be provided wherever necessary. Facilities for oil filling, adequate breathing drainage shall be provided. The gear coupling shall be forged from EN-8 material and shall have minimum hardness of 250 BHN. Pendent switch:

For all the operations of the crane, a pendent push button station is to be provided with sufficient of length of cable. Suitable arrangements for operator friendly operations shall be made.

ELECTRIC MOTORS FOR CRANES:

ALL electric motors shall be T.E.F.C type except motor for micro hoisting slip ring induction motor suitable for the indoor crane duty. All motors provided shall be of the approved and same make. The motors shall comply with IS 325 or equivalent BS and shall be suitable for frequent acceleration and braking. All the motors shall be rated at 125% of the rated output at 150 starts per hour class of duty at ambient temperature, required under worst operating conditions and they shall have class B insulation and shall be half hour rated for main hoist motion and one hour rated for all other motions with temperature rise not exceeding 50 degree C. over ambient temperature of 45 degree C rating permitting overheads and their construction and characteristics shall be suitable for the crane service. Motor shall be so located that the brush gear and terminals shall be readily accessible for inspection and maintenance purpose.

All motors shall be suitable for voltage fluctuating between + or – 10% of rated value and for all motions minimum eight pole motors shall be provided. All motors shall have greased lubricated ball and roller bearing housing at non drive and drive ends respectively. Cartridge type bearing housing shall be

provided for main hoist and auxiliary hoist motion so that motor can be dismantled without disturbing bearing and for protection against dirt and dust entering in bearing.

For all other motors, the bearing shall be fitted in the housing, accurately bored and machined on end seals and sealed with dust cap.

CONTROLS:

Master control equipment, whereby the operator may control the function of the crane shall be place, and shall be so arranged as to provide maximum of convenience and view of the operation. Additionally, pendent control arrangement shall also be provided for operating from floor level. All motor controls shall be full magnetic reversing with definite time limit on frequency controlled acceleration devices and instantaneous overload and under voltage protection. They shall be designed so that it will be possible to limit the vertical movement of the hooks with full rated load and when starting from complete stand still to within 1.5 mm for the main hooks and to limit the movement of the bridge and trolley, with full rated load and when starting from complete stand-still to within 6 mm. All hoist motor controllers shall have at least five speed control points in each direction of operation and all other controllers shall have at least four points in each direction of operation. The contact of all protective relays shall be wired so that the operation of any relay will trip all motors, primary contractors thus making necessary to return all controls to the OFF position before any motor can be started again. Instantaneous relays shall be adjustable between 200 and 300 percent of the motor full load current changes in the speed in the lowering directions shall be under direct control of the operator and shall permit him to stop the motors, without time delay from any position of the master switches.

All switches, controller, levers and other operating mechanism shall be marked plainly and permanently.

When practicable, the controller handles should move in the direction of the resultant and movement. The position of the control shall be such that when operator is operating any control handles, he cannot operate any other control handles inadvertently. The control level shall be provided with steps and catches to ensure safety and facility of operation.

CONTACTORS AND RESISTERS:

The contactor and the resisters shall comply with the provisions of the relevant classes of IS 3177 / 1965 or latest version. They shall be of non-breakable, corrosion resisting type with a low temperature co-efficient and shall be air cooled. The resistance shall be cast iron grid type with appropriate rating. The resistance shall be provided in well ventilated sheet metal boxes. The contactors and resistors shall be adequately protected to prevent accidental contact with live parts. Resisters shall be so arranged that they are easily accessible for adjustment, examination and replacement, care being taken to see that it is not effected by vibrations.

ELECTRICAL PROTECTIVE GEAR:

An air brake contactor type main circuit breaker shall be provided in the control cabin connected by suitable cables to the air circuit breakers and fitted with magnetic type inverse time elements overload relays and no volt tripping device, in case the supply voltage drops below 60% of its normal value. The no volt tripping device shall be capable of being used for tripping the main circuit breaker in emergency from suitable position manually. The main circuit breaker shall be electrically interlocked with the controller in such a way as to prevent the current supply , being reinstated unless all controllers are in the OFF position.

All crane motors shall be provided with circuit breaker with instantaneous magnetic relays fitted in two phases for protecting the motors against short circuit and against overload by reliable type thermal relays, fitted in each phase with setting for adjustable between a range of 90% to 150% of the rated current.

Each crane motor shall have its own ammeter and one common voltmeter for all motors of a uniformly distributed scale and mounted on the control panel. Three separate indicating lamps shall be provided on the electrical panel to indicate the states (live or dead) of the three phases.

Complete wiring diagram of all electrical connections from the main switch to the respective appliances shall be fixed in the control cabin for ready reference of the operator. On this diagram, shall be given the rating of each of the motor the cable sizes and such other information as will facilitate inspection and maintenance. Similar diagram but showing the inside connection of each of the controllers and the switches. Suitable transformers, for low voltage supply with the switch fuses shall be provided. The main protective panel shall be at convenient position and shall include but not limited to the following items:

- Main isolating interlocked with panel door.

- Main air brake contractor type main circuit breaker.

- Overload relays of magnetic type for the main incoming supply and for each outgoing feeder of the motors.

- Indicating lamp for main contractor.

- Emergency push button.

- Separate circuit breakers for individual motors.

- Plug and socket connection to hand lamp.

- Transformer for low voltage supply.

- One voltmeter with selector switch and one ammeter with selector switch for the main incoming supply.

- Ammeter for each motor.

- Three indicating lamps showing the status of three phases of main incoming supply (live or dead)

- The electrical panel along with the equipment shall be of approved make.

Arrangement of the connections between the isolating switch and D.S.L and the cable with D.S.L shall be provided by the contractor. The isolating switch fuse unit and termination connections of cables at inlet and outlet ends shall be included. The arrangement shall include three indicating lamps for indicating the status D.S.L (live or dead).

For control and protective panels anti condensation heater, anti-vibration mounting and cubicle lighting (complete with switch) shall be provided.

LIMIT SWITCHES:

Total enclosed self-resetting two way rotary type limit switches which cuts off current and stops the motion when the hooks have risen to a pre-determined level shall be provided to prevent over winding and over lowering totally enclosed self-resetting two way lever type limit switches shall be provided to prevent over travelling and over revering in both direction.

COLLECTOR GEAR:

A schematic wiring diagram for the crane shall be provided. On this diagram, shall be given the rating of each of the motors, the cable sizes, types of contactors and resistance and such other information which will facilitate inspection and maintenance of the crane. The cable schedule giving the size of the cable, terminal numbers of various equipment, the designation of various electrical components shall be supplied by the contractor.

LIGHTING:

The crane shall be provided with a permanent 220 V A.C lighting system. A minimum of three nos. of 500 watts (Halogen) bridge light with indoor type reflectors shall be provided under each crane bridge girder (i.e. total 6 nos) for illuminating the working area. These lights shall be of the hinged self-setting type of easy removal. The contractor shall provide light near the meters and rope drums. He shall also provide a hand lamp with 15mtr. Cable and at least 2 nor. Three pin plug sockets along the platform at

suitable positions. Apart from bridge lights all light shall be of tungsten filament type and shall be provided with suitable indoor type reflectors with shock absorbing sockets.

EARTHING:

The crane and gantry structures, meter frames and metal cases of all electrical equipment shall be effectively connected to earth by the connector in accordance with Indian Electricity Rules. For effective earth connection, the earthing of gantry rails shall also be done by the contractor.

A set of tools, special tools, tackles and all other appliances necessary of complete assembly dismantling and maintenance of the crane together with N.S box locking arrangements holding them, shall be supplied, the spanners shall be single ended and made of fit each size of nut and bolt.

The list of the erection tools and tackles included in the supply shall be furnished.

PAINTING:

The crane shall be thoroughly cleaned and shall be free from scale rust and grease etc. and painted with one coat of best quality red oxide paint machinery housing and other mechanical parts shall be painted with finishing enamel of approved colours bright steel parts shall be treated with anti-corrosive compound.

After erection at site every part shall be cleaned and shall then received two coats of the best quality enamel machine paint of approval colour.

In case of the total erection being entrusted to the contractor, cleaning and painting of the crane after erection at site shall be included in his scope of work. The painting schedule and the painting scheme shall be got approved from the purchaser before starting the painting work.

DRAWING AND OTHER GUARANTEED DATA TO BE FURNISHED

The tenderer shall furnish along with tender the detailed technical particulars in respect of the crane to be supplied and a general a outline drawing showing the major important dimensions, clearances, hook approaches, maximum wheel load without impact, longitudinal and lateral thrust and wheel loading diagram etc.

Within six weeks from the date of the receipt of the order the contractor shall have to furnish in triplicate separate drawing for the following for the approval of the purchase.

General assembly drawing of the crane giving full and confirmed data regarding the various clearance, hook approaches and other important dimensions.

Layout for fixing of gantry rails and down shop loads.

The wheel load with impact along with calculation and indicating wheel loading diagram from transverse and lateral thrusts on the wheels.

LABELS AND LETTERING

All apparatus, meters, controls and all panels shall be clearly labelled indicating where necessary their purpose the “ON” and “OFF” position the label shall be clearly lettered one enamel ink or bright aluminum plates. In some cases, the label shall be cast on apparatus. All labels shall be printed in English; function labels shall be black letters on white backgrounds and danger label shall be white letter on red back ground.

GANTRY RAILS

The contractor shall supply gantry rails with continuous sole plats, anchor and necessary fixtures etc. for travel of the crane. The gantry rails shall be of appropriate size, flat bottom and shall be suitably clamped to the sole plate throughout the length and anchored suitably. The detailed drawing for this shall be given by the contractor for the approval of the Department. The contractor shall supply the requisite information regarding the maximum wheel loading in the unfavorable position.

CABLING AND WIRING

All the meters, controllers, current collector and resistance shall be factory wired. All connections among the apparatus shall be executed by means of armored cable and shall be suitably clamped in trough. The cables wherever likely to go damaged should be protected with sheet metal guard easily removable for maintenance and inspection. Control cables shall be manufactured from electrolytic copper and power cables shall be aluminum and shall be executed as per the minimum sections and type of insulation in accordance with IS 3177 or equivalent British Standards. The current rating of the cables shall be as per provisions of the appropriate clause of IS 3177 / 1965. The down shop leads shall be of hard drawn copper and the physical and electrical properties complying with appropriate Indian Standard or equivalent British Standard. The down shop leads shall be tightened in ends and supported with indoor insulator and tension adjusting device.

The power to the crab shall be supplied through flexible training cables. These shall be of copper and insulated and shall be supported in loops from the ball bearing type trolleys running along a track parallel to the cross traverse.

Provision shall be made for the protection of all live bare conductors against accidental contracts. The contractor for the crane shall include in his supply all the requisite length of down shop leads along with insulation and straining device.

The protection and control panel wiring shall be provided with ferrules with numbers and shall be terminated on the terminal block. The relays timers, contractors etc., shall be designed by giving type number which can be in the wiring diagram.

SOLENOID BRAKE:

A three-phase solenoid brake of air dash pot type for main hoist shall be fitted on the extension shaft of motor for emergency use. Totally enclosed self-resetting positively acting two-way rotary type limit switches shall be provided to prevent over winding and over lowering of the hooks.

Three Phase solenoid brake for main hoist/motion comprising-

- Air dash pot type solenoid—The brake shall be applied gently without giving jerks. Electro magnet-AC 3 phase electro magnet shall be totally enclosed with removable side covers for easy maintenance magnet laminations shall be high grade low magnetic steel laminations. Coils shall be wound on thoroughly insulated light bobbin. Dash pot provision for adjusting the speed of upwards and downward travel of the plunger shall be made.

COMPRESSION OF SPRINGS

Springs shall be made of steel and properly heat treated to give correct hardness. When the power to the crane is switched off, the compression springs shall provide working pressure to apply the brakes. When the magnet is energized, the solenoid shall exert force against a spring pressure releasing the brake.

PACKING:

The contractor shall provide for securely protecting and packing the crane parts as per his standard practice so as to avoid damage in transit under proper conditions and he shall be responsible for all loss or damage caused or occasioned by any defect in packing. The packing specifications shall comply with the requirement of insurance authority. All bright parts shall be thoroughly protected from rust during transit. The purchaser will take no responsibility for any damage done to the plant enroute to the “site of work” or place of delivery whichever may be specified.

TRANSPORT AND ERECTION:

Before dispatch all parts of the crane and the crane itself shall be completed, assembled, properly aligned and match marked with distinctive erection marks etched on them corresponding to these on the drawings so as to ensure correct assembly and alignment at site. The weight of the heaviest number of the structure of part of the crane that to be handled during erection shall be stated in the tender.

The contractor shall ensure minimum amount of assembly at site for early commissioning of the crane after delivery site welding of major members of crane will not be allowed. The crane is to erected in a surface type pump house on RCC beam. The contractor shall arrange for the required erection equipment such as mobile crane, derrick winches, wire ropes, shackles, pulley’s etc.

TESTS:

At manufacturer’s work:

X-ray testing of the welding joints of the girder—During the fabrication of bridge girder 10% “X-ray” testing of the welding on tension and compression zones of the box girder shall be carried out in presence of the representative of the department and test certificate in this regard shall be submitted to the Department.

Six copies of the test certificates for the chemical composition, lamination, test die perpetration test weldability of the steel to be used in bridge girders and other important structural items of cane shall be submitted before the fabrication work is taken up by the contractor.

All forging shall be subjected to ultrasonic test for internal cracks and forging defects six copies of the test certificate in this regard shall be submitted by the contractor.

HOOK: the hooks shall be tested as per the relevant BS or IS . The test certificates for the chemical compositions yield point, tensile strength elongation and bright hardness shall be submitted.

WIRE ROPES: Test certificates for the braking lead, tensile strength and the elongation of the wire ropes.Chemical analysis of the material of the track wheels.

All electrical and mechanical equipment shall be tested in accordance with the appropriate Indian standards and in accordance with the requirement of the specifications at either crane maker’s or equipment manufacturer’s works. Even when the test certificates/test reports are approved by the purchaser or by his representative, these tests shall not absolve the contractor of guaranteeing the performance at site.

The complete crane shall be assembled including wiring and other fittings and aligned at site and the following tests shall be conducted in presence of the representative of KNNL.

Deflection test: The deflection test shall be carried out with the crab in the central position. The measurement shall not be taken on the first application of the safe working load. The vertical deflection shall not be taken on the first application of the safe working load. The vertical deflection shall not exceed 1/900th of the span.

Motion test and Rated load: All the motion except long travel motion of the crane shall be tested with the hooks carrying the rated load to check up the compliance with the specified performance requirement such as speed etc. for the long travel motion the ideal running test for the wheels shall be carried out.

Over load Test: The crane shall be tested to lift and sustain a test load of 125% of the safe working load, keeping the load at the centre of the span. During this over load test each motion except long travel shall be maneuvered in both the directions and the crane shall show itself capable of dealing

safely with the over load. The contractor shall submit six copies of the complete test reports for above tests to the purchaser for approval.

Following operational tests shall be carried out:

- Satisfactory operations of each controller switch contractor, relay and other control devices including light switches.

- Correctness of all circuits and interlocks and sequence of operations.

- Satisfactory operation of each motion.

- Satisfactory operation of all protective devices.

- All the gear boxes shall be run for six hours nonstop and checked for noise vibration and oil leakage.

The contractor shall also furnish the test certificates ( in quadruplicate) in respect of the following:

INSULATION TEST:

After erection but before the crane is connected to the supply, the insulation of the electrical equipment shall be tested by a suitable instrument as per IS 3177 of equivalent IS 466-1960 and any defects revealed shall be made good by the contractor, without any extra cost.

TEST FOR OPERATIONS:

After connection to the supply, the contractor shall out the tests mentioned above and the correct operation of all limit switches under the most unfavorable conditions satisfactory operation of the L.T motion shall also be carried out.

All the above tests shall be witnessed by Engineer’s Representative.

  - TESTING TRIALS, COMMISSIONING AND OPERATION

TRIAL OPERATION

The plant in the pump house shall be on trial operation during which period all necessary adjustments shall be made while operating over the full load range enabling the plants to be made ready for performance and guarantee test.

The duration of trial operation of the complete equipment shall be fourteen (14) days out of which at least seventy two (72) hours shall be continuous operation at full load or any other duration on higher side as may be agreed to between this Engineer and contractor. The trial operation shall be considered successful if each item of the equipment can operate continuously at the specified operating characteristics for the period of trial operation.

Minor Interruptions not exceeding four (4) hours at a time caused during the continuous operation shall not affect the total duration of trial operation. However, if in the opinion of the Engineer, the interruptions are long, the trial operation shall be prolonged for the period equal to that of interruption.

A trial operation report comprising observations and recordings of various parameters to be measured in respect of above trial operations shall be prepared by the contractor. This report besides recording the details of the various observations during trial run shall also include the dates of start and finish of the trial operations and shall be signed by the representatives of both the parties. The report shall have sheets recording all the details of interruptions occurred adjustments made and any major repairs done during the trial operation. Based on the observations necessary modification / repair to the plant shall be carried out by the contractor to the full satisfaction of the Engineer to enable the latter to accord permission to carry out performance and guarantee tests on the plant. However minor defects which do not endanger the safe operation of the equipment, shall not be considered as reasons for withholding the aforesaid permission.

COMMISSIONING AND OPERATION

The commissioning and operation period generally will be 90 days and will follow the trial operation of individual set of pumping equipment unless otherwise specially agreed. During the commissioning and operation period, the contractor shall depute his personnel full time to operate, maintain and repair the equipment. Only water and electricity shall be provided by the Owner. During this period the Owner’s personnel who shall continuously work with the contractor’s personnel shall be adequately trained by the contractor’s personnel to take full responsibility of operating, maintaining, repairing etc. of the equipment and plant.

PERFORMANCE AND GUARANTEE TEST

- The final test as to the performance and guarantee shall be conducted at site by the contractor as per IS 9137. The contractors, commissioning and start up engineers shall make equipment ready for such test and assist the corporation in conducting the test free of cost such test will be commenced after the successful completion of operation of 75 days or 1000 hours. Whichever is more.

- These tests shall be binding on both the parties of the contract to determine compliance of the equipment with the performance guarantee. The acceptance of these tests will be subject to provision made.

- Unmeasurable parameters shall be taken into account in a reasonable manner by the engineer for the requirement of these tests. The test will be conducted on the completed installations without any special modifications for test purpose. No separate allowances or deviations from specified conditions in test procedures shall be allowed while evaluating the performance.

- Any special equipment tools and tackle, required for the successful completion of the performance and guarantee tests shall be provided by the contractor free of cost.

- The guarantee performance figures of the equipment shall be provided by the contractor during these performance and guarantee tests. Should the results of these tests show any decrease from the guarantee valves, the contractor shall modify the equipment as required to enable it to meet the guarantees in such case performance and guarantee test shall be repeated within one month from the date the Equipment is ready for the test and all cost of modifications including labour, materials and the cost of additional testing to prove that the equipment to meet the guaranty shall be borne by the contractor.

PROVIDING TOOL SETS AND SPARES

The contractor shall provide a set of recommended spares for 5 years operation & maintenance period of the plant. These spares shall be suitable for the equipment provided under this contract and from the original Manufacturers only.

## SPECIFICATIONS FOR ELECTRICAL SUBSTATION EQUIPMENTS

  - OUTDOOR SWITCH YARD EQUIPMENTS INTRODUCTION:

The proposed sub-station, to be constructed at the pump house for providing power supply to the pumps, will receive power supply from then earby sub-stations,where adequate power required for the pump house is available. The contractor shall construct the terminal bays required for drawing power at the pump house with necessary equipments and protective equipments at both the ends,The sub- station shall feed the pumps erected at the above places.The contractor shall assess the exact capacity of transformer and shall execute and construct the switch yard with all switchyard materials and protective equipments in complete.

SCOPE:

This part of the specification covers Design,Manufacture, Supply of material lsand transport to site,Erection,Testing and Commissioning of following equipment for sub-station, including all connected Civil Works.

SUB-STATION:

The specification shall also cover sub-station structural material, cables, lighting and all other associated equipment.The Substation shall comprise of the following:

- Circuit Breakers	:

- Isolators with Earth Switch	:

- Isolators without Earth switch	:

- CVTs	:

- CTs	:

- Lightning Arrestors	:

- EMVTs	:

- Bus bar connector& associated Equipments

- Special tools & plant	:

- Cables	:

- Groundingandearthing	:

- G.I.Structures.	:

- Marshalling boxes	:

- Required qty. of ACDBs & DCDBs, Bus conductors clamps, connectors etc.

SCOPE OF SUPPLY CONTRACT:

The scope of supply shall include all parts,accessories, supporting structure, Marshalling box, terminal connectors etc., which are necessary for assembly, erection,commissioning and operation of completes circuit breaker,Isolator,cts and pt sand lightning arresters even though these are not individually or specifically broughtout in the specifications. Corresponding parts of all the respective equipments and spares shall be of the same mater dimension workmanship and finish and shall be interchangeable without any modifications. Modifications, if required, to suit thesite conditions shall be carriedout without extra cost.

  - WORKS IN THE SWITCH YARD:

The works in switch yard is briefly stated as under -

    - Excavation for main and equipment structure foundations, plinths for Transformers, gate pillars, levelling, cable laying and earthing etc.,

    - RCC/CC foundations for structures, Transformer and circuit breaker plinths etc., Back filling for foundations. Levelling of sub-station site	with

borrowed gravel or excavated earth  including clearing of site.

    - Fire baffle wall, oil soak pit

    - Construction of chain link fencing around switchyard.

    - Construction	of	cable	duct	including	cable	ducts	crossing transformer track.

    - Formation of roads,

    - Spreading of HBG metal

This section covers the installation of Switchyard equipment, Main Bus Bars, cable trenches, power & control cables, Switchyard structures, Lighting, ground mat conductors, etc.

The scope of work of switchyard are

- Lightning protection down conductor, tap off and jumper connection to all the equipment in the switchyard are in Bidder’s scope

- Supply and Installation of bus arrangement	and	erection	of switchgear equipment with all interconnections

- Connections from transformers to bus.

- The contractor shall decide the exact Nos. of bays required for the pumping station depending on the No and capacity of the pumps selected.

- This electrical installation shall meet all requirements of Indian Electricity Rules.

The bidder also furnish the following for the approval of Employer -

- Power and Control Cable schedules.

- Earth mat design & Lightning Protection design.

- Estimated requirement of cable trays, conduits, earthing materials etc.

- Requirement of Hume pipes for crossing of roads, drain etc.

- Drawing for cable jointing and termination.

- Where assemblies are supplied in more than one section, bidder shall make all necessary mechanical and electrical connections between sections including the connection between buses.

STORAGE OF EQUIPMENT:

The bidder shall provide and construct adequate storage shed for proper storage of equipment. Sensitive equipment shall be stored indoors. All equipment during storage shall be protected against damage due to acts of nature and accidents. The storage instructions of the equipment manufactures/Purchaser’s Engineer shall be strictly adhered to. Storage is responsibility of the bidder only

TYPE OF CONSTRUCTION :

The sub-station structures shall be lattice type galvanised structures. The foundations of main structures are stub type and other structures are foundation bolt type.

PROCUREMENT OF STEEL, FABRICATION, GALVANISATION AND SUPPLY OF STEEL STRUCUTURES:

Procurement of steel such as MS angles, Plates, Channels and M.S. Rounds required for fabrication of structures is within the scope of contract. The structures shall be fabricated as per the structural drawings and galvanised. The Bidders are required to fabricate proto type structure and submit shop drawings for all the structures, stub settin templates. Mass fabrication of the structures shall be done after approval. The structural drawings & bill of material shall be issued by the Bidder. Galvanised bolts, nuts, pack and spring washers required for the assembly of the fabricated pieces to form into a composite structure of standard quality shall be supplied by the contractor. The ‘U’ bolts for Bus stringing and foundation bolts for main and/or auxiliary structures are also to be fabricated and galvanised by the contractor. The Galvanised nuts required for these bolts are also to be procured and supplied by the Contractor.

ERECTION OF STRUCTURES:

The structures shall be erected on the foundations, after allowing the required curing time for the foundations. The members shall not be strained or bent during the course of erection, Care

shall be taken to see that the jointing surfaces are clean and free from dirt or grit and fit properly. The structures shall be erected strictly in accordance with the approved drawings. After erection of structures the bolts shall be checked to ascertain that all nuts are fully tight. The contractor shall ensure that none of the bolts are left out. The structures must be truly vertical after erection and no straining will be permitted to bring them to vertical position. The tolerance allowed for verticality is 1 in 360 structure height.

STANDARDS:

The design, manufacture, installation, testing and performance of equipment and services provided under this specification shall comply with the latest edition of the following standards, Rules and Acts.

- IS: 1653	rigid steel conduits for electrical wiring.

- IS: 3480	Flexible steel conduits for electrical wiring.

- IS: 2667	Fitting for rigid steel conduits for electrical wiring.

- IS: 3837	Accessories for rigid steel conduits for electrical wiring.

- IS: 1239	Mild steel tubes.

- IS: 458	Specification for concrete pipes.

- IS: 5216	Guide for	safety	procedures and practices in

electrical works.

- IS: 280	M.S.  Wire for general engineering purpose.

- IS: 8309	Compression	type	tubular	terminal	ends	for	aluminum conductors of insulated cables.

Soldering and welded type terminal ends for conductors of Insulated cables.

- IS: 513	Cold rolled carbon steel sheet.

- IS: 2633	Methods	of	testing	hot	dipped galvanized articles.

COMPLIANCE WITH REGULATIONS :

The works shall be carried out in accordance with the Indian Electricity Act 1910, Indian Electricity Rules 1956 or any other revisions thereof which may be issued during the currency of the contract and the requirements of any other regulations and Acts in India to which the employer may be subjected to.

SUPPLEMENTAL ITEMS:

The contractor is bound to execute all the supplemental works that are found essential, incidental and inevitable during execution of main works at the estimated rates plus or minus over all tender percentage.

CLEARING UP THE SITE:

During construction the Contractor shall keep the work site and storage area used by him free from accumulation of waste materials or rubbish and before completing the works the contractor shall at his own cost, remove or dispose off in a manner satisfactory to the owner. All temporary structures, waste and debris shall be cleaned, all holes in the ground shall be filled in and the land restored to its original state as far as is practicable and the entire premises should be in a neat and tidy condition of cleanliness as the owner may direct. Any damage done to the permanent or temporary work of the Department by the Contractor or his sub- contractor shall be made good at contractor’s expenses.

GALVANIZING:

All members of structures and special structures ‘U’ bolts etc., shall be hot dip galvanized, Stubs and foundation bolts shall also be hot dip galvanized upto one third length of stubs and foundation bolts from top.

Galvanization shall be done by hot dip process in full compliance with IS:2629-1966 and IS:4759- 1968 where any materials is to be galvanized it should be free from greases and paint etc., during and after galvanization. After galvanizing the surface shall be free from sharp edges and metal nodules and there shall be no clogging of bolt holes due to stay of zinc in the holes after galvanizing Galvanization of the structures parts shall be to a thickness of 150 microns.

Tests on the galvanized samples shall be carried out regularly strictly in accordance with IS:2633-1972. The entire batch represented by the defective sample shall be rejected and re- galvanised to satisfy the test requirements.

In addition strict inspection of the galvanized materials shall be carried out by the contractor before dispatch and any visible or suspected defects shall be rectified forthwith.

The bidders shall submit with their bids full specification of the quantity of zinc to be used stating its percentage purity and the process of galvanization adopted by them along with the devices and facilities available with them for more authoritative and better control of quality of galvanizing. They shall also state the maximize percentage increase in the weight and steel with weight of the galvanized structures.

MARKING:

Each part of steel structure shall be clearly stamped with 20mm stamping die with identification number mark or symbol to facilitate erection corresponding to those shown in erection drawings. These marks shall be applied before painting/ galvanizing and shall be visible after painting.

BOLTS NUTS AND WASHERS:

Galvanised bolts and nuts and plain spring washers required for the assembly of the fabricated pieces to form into a composite structure of standard quality shall be supplied by the Contractor. The U-bolts for stringing and foundation bolts for main and auxiliary structures are however to be fabricated and supplied by the tenderer. The required MS rounds for U-bolts and foundation bolts will be under the fabrication item. The nuts required for these bolts shall be procured by the tenderer.

LEVELLING:

Sub-station switch yard should be levelled as per directions of Engineer with the surplus earth left over after back filling structure foundations. If surplus earth is not adequate for levelling, the levelling should be done by excavating earth in any portion of substation site whatever type of soil is met with and filling should be done with such earth for levelling switchyard. If this is not sufficient, the switchyard is to be levelled by supplying gravel from the approved borrowed areas. Clearing of the entire site by removing bushes, hedges, unwanted plant growth and other things are in the scope of levelling work.The work shall be carried out as per IS 301, 302 and 138.

COMPACTION: Compaction shall be achieved by the use of smooth wheeled rollers, pneumatic type rollers, sheep’s foot rollers, vibrating plates, frog rammers, power rammers and such other equipment as shall be specified. Compaction shall be carried out on each layer of thickness not more than 150mm thickness. Density tests shall be made on each compacted layer and the density attained shall not be less than 98% of maximum dry density (standard proctor for the type of material used). A record of the density tests conducted on each layer shall be recorded in a register maintained by field staff.

FOUNDATION EXCAVATION:

Earth excavation has to be done in all types of soils which can be excavated with pick axe & crow bars in all conditions such as dry, wet, slushy etc., and in hard rock requiring blasting including shoring, shuttering and dewatering wherever necessary covering initial lead and one extra lift.

FOUNDATION CONCRETE:

Laying foundation for main and auxiliary structures, transformer plinths including dewatering the pits before and during the process of laying concrete in the proportion of RCC 1:2:4 using 12 to 20mm HBG metal and CC 1:4:8 using 40mm HBG metal as per the drawings for structural foundations approved by the employer and curing for 14 days including cost of cement, reinforcement steel. Rate quoted shall be inclusive of stub setting, fixing and concreting foundation bolts and 90 lb rail poles for transformer plinths wherever necessary.

BACK FILLING:

Back filling of foundations with excavated soils including watering and consolidating in 150mm layers for normal soils. Providing sand cushion for foundations and flooring area including cost of sand, watering and consolidation complete for BC soils.

PLASTERING:

Plastering foundation plinths 12mm thick in 1:3 Cement Mortar and white washing (two coats) with cement paint. All projections of plinths and masonry above ground level shall also be provided with cement paint.

PROVIDING SAFETY EARTHING FOR EQUIPMENT.

The scope also includes Minor civil works like chipping/punching the foundations placing on the foundation/ structures,(or in the control room building in case the equipments are indoor type) aligning, plumbing and grouting, if required including supply of foundation bolts and other hardware, if necessary.

Codes & Standards

Electrical installation work shall comply with all currently applicable statutory Indian Electricity Rules, Fire Insurance Regulations and safety codes in the locality where the equipment will be installed. Nothing in this specification shall be construed to relieve the bidder of this responsibility.

Unless otherwise specified, installation work shall comply with the requirements of latest editions of applicable Indian Standards.

ERECTION, TESTING & COMMISSIONING:

In accordance with the specific installation instructions, as shown on the manufacturer’s drawings or as directed by the owner, the bidder shall unload, erect, install, wire, test and put into commercial use all the electrical equipment included in the contract. Equipment shall be installed in a neat, workman like manner so that it is leveled with plumb, square and properly aligned and oriented. Tolerances shall be as established in the manufacturer’s drawings or as stipulated by the Engineer.No equipment shall be permanently bolted down to foundation or structure until the alignment has been checked and found acceptable by the Engineer. All switchgear, shall be made absolutely vermin proof.

Induction motors if any shall be installed and commissioned as per IS code of practice  IS: 9000 and the manufacturer’s instructions. Care shall be taken during handling of insulating oil to prevent ingress of moisture or foreign matter.

Bending of compressed air piping should be done by a bending machine and through cold bending only. Bending shall be such that inner diameter of pipe is not reduced.

Cutting of the pipes wherever required shall be such as to avoid flaring of the ends. Hence only a proper pipe-cutting tool shall be used. Hacksaw shall not be used.

For cleaning the inside and outside of hollow insulators only leather cloth shall be used.

After installation of all power and control wiring, the bidder shallperform operating tests on all switchgear and to verify proper operation of switchgear and correctness of the interconnections between various items of the equipment.This shall be done by applying normal A.C or D.C voltage to the circuits and operating the equipment. Megger tests for insulation, polarity checks on the instrument transformers, operation tests on equipment, and the manufacturer’s installation tests shall be carried out by the bidder, who shall also make all necessary adjustments for proper functioning of the equipment.

The bidder shall touch up Equipment with finished coats of paint if the surface is soiled or marred while handling.

Petroleum jelly shall be applied for current carrying joint connections, clamps etc. to avoid corrosion.Silicon polish (water repellant) shall be applied on all insulation, stacks, bushingsetc. after installation and beforecommissioning toavoidtracking.

LIGHTNING PROTECTION IN SWITCHYARD:

Scope covers design of the direct stroke lightning protection system coveringdesign  of overhead shield wires to protect the entire switchyard including bus bar, equipment, buildings transformer yards, feeder yards, auxiliaries etc. from the direct stroke of lightning.

Standards:

The design of the direct stroke lightning protection system shall be based on a proven design method as per the applicable Standards/Specifications. The specifications/authority followed for the design shall be quoted in the bid and the relevant material relating to the design procedure followed shall accompany the bid.

The following Indian Standards or equivalent of any international standards shall be followed: -

Protection of buildings and Allied structures against lightning.IS:2309:1969

Code of Practice for EarthingIS:3043- 1987

Indian Electricity Rules.

Assumptions, if any, on which design or the direct stroke lightning protection (DSLP) offered is based shall be clearly stated in the bid.

Design requirements:

Direct stroke lightning protection (DSLP) shall be provided in the switchyard by overhead shield wire.

Lightning protection system down conductors shall not be connected to other conductors above ground level. Also no intermediate earthing connection shall be made to lightning arrester, transformer and voltage transformer earthing leads which shall be directly connected to pipe electrode.

The lightning protection system shall not be in direct contact with underground metallic service ducts and cables.

Tender Drawings:The bidder shall submit the following drawings with their bid: - Dimensional drawing of Earthing electrode and connections of thesame to the direct stroke lightning protection system.

G.S. Shield wire shall be strung on all main structures in Switchyard to Provide earth screen with 7/3.66 GI wire.

A 32 mm dia, 3000 mm long MS Earth Electrode shall be provided for each gantry column. Conductors of the lightning protection system shall not be connected with the conductors of the safety Earthing system above ground level.

Down conductors shall be cleated on the structures at 740 mm interval. Connection between each down conductor and rod electrodes shall be made via test joint located approximately 1400 mm above ground level. Lightning conductors shall not pass through or run inside G.I. conduits. All metallic structures within a vicinity of 2000 mm in air and 4000 mm below ground shall be bounded to the conductors of lightning protection system.

Lightning protection system installation shall be in strict accordance with the latest editions of Indian Electricity Rules, Indian Standards and Codes of Practice and Regulations existing in the locality where the system is installed.

Supply and installation of all clamps including but not limited to tension clamp suspension clamp, pad clamp for tower by Earthing, T-clamp, down conductor cleats, lugs, test joints etc., are in the

scope of this contract.

EARTHING SYSTEM :

Tests shall be carried out by the successful bidder to determine the as built resistance of the Earthing mat laid as per the design approved by the Owner. Field measurements of step and touch potentials shall also be carried out by the successful Bidder to show that the design

and installation of the Earthing mat are adequate. The results of the test/ measurements shall be furnished to the Owner. If the values of these	parameters are found to exceed the permissible values, the bidder shall take necessary remedial measures to bring the values of these quantities within the tolerable limits. Continuity of all conductors and efficiency of all bonds and joints shall be tested.The earth mat design shall be got approved f rom M/s KPTCL.

BUS BAR SYSTEM :

Design, manufacture, testing at manufacturer’s works, supply to site, site handling including storage, erection of bus post insulators, insulators, insulator hardware, clamps,connectors, conductor spacers, all accessories, jumper sleeves and all other required to make the bus bar system including cross connections, equipment interconnection bus complete in all respects STRINGING OF BUSBAR & GROUND WIRE:

The bus shall be formed with adequate size ACSR conductor.and shall be strung to required tension as per site Engineer’s direction and as per switchyard layout drawing.

The stringing of bus conductors covers installation of tension insulator strings, suspension insulator strings, post type insulator stacks and other accessories along with tensioning of conductor and clamps. The jumpering to various equipment and the ground wire stringing are also under the scope of this work.The G.I. Ground wire shall be strung as detailed in the layout drawing.

The insulator strings shall be assembled on the ground.These shall be cleaned, and examined before hoisting.All the parts including current carrying parts shall be clean without grease, paint and dirt.Insulators with cracks or chips or those having glazing defects exceeding 0.5 Sq.Cm shall not be used.

The sag of bus conductor shall not be more than 1%. Damaged and jointed conductors shall not be used. The conductor surface shall be clean and smooth without any projections, sharp points, cuts or abrasions, etc., and the conductor shall be continuous in span.

ELECTRICAL CLEARANCES:

The design of bus bar system for Switchyard : The main bus shall be suitable for switchyard equipment with specified BIL and shall ensure availability of the relevant minimum electrical

clearance under the condition of maximum swing of conductor due to wind and short circuit forces / or thermal expansion, in the horizontal and verticalplanesasapplicable. Allelevationsshall be reckoned with respect to the concrete plinth level.

The design shall be based on the following minimum clearances/ elevations as per IS/Standards.

DESIGN CRITERIA:

The Bidder shall furnish supporting calculations to prove adequacy of design parameters for: Cantilever strength of bus post insulators

Location of spacers to contain the short circuit forces. The bus design shall accommodate thermal expansion and contraction.

The forces transmitted to the equipment terminal shall not exceed the maximum allowable values indicated by the manufacturer.

CONSTRUCTION DETAILS: Switch yard :

The bus bar system shall be made up of ACSR conductor . Equipment inter connection and overhead cross connections shall be done with ACSR conductor. Whenever Bundle conductors are used it shall be provided with suitable spacers fixed at intervals to ensure that bundle does not collapse on the passage of rated short circuit currentthroughit.The design of conductor clamps used in the spacers shall be such thatconductors in the bundles do not suffer any damage due to tightening of the clamps.

The tapping from bus and the jumper connections between the switchgear equipment for the three phases shall be with ACSR conductor.

The minimum elevation of bay bus bars shall be available under the condition of maximum sag with the bus bar operating at a temperature of eighty five (85) degrees Celsius.

The maximum tension in each bus bar conductor shall not exceed the value corresponding to application of loads due to wind pressure and maximum ambient temperature conditions.

The sagging of bus bars shall be done so that sags in all phases are same. String hardware assemblies shall include suitable turn buckles sag adjustment devices to adjust the sag later, should it become necessary. Suspension insulator strings shall be provided to support the jumpers across the tension string assemblies on either sides of intermediate gantries and the jumpers connections from bus bars to the equipment in the bays. All renewable and similar parts shall be interchangeable.

All components and equipment as a whole shall be designed to withstand the extremesof electromagnetic, electro dynamic, mechanical and thermal stresses which may be encountered during their normal and abnormal operating conditions. The bus design shall accommodate thermal expansion and contraction. The forces transmitted to the equipment terminal shall not exceed the maximum allowable values indicated by the manufacturer.

BUSBAR ACCESSORIES:

The conductor accessories shall be free from inequalities, spills, splits, or other defects and shall be smooth, close grounded and have true forms and adequate dimensions.

The design and construction of conductor accessories shall be such that they can be easily fitted and are free from unsightly projections, sharp edges etc., Bolts nuts, washers check nuts etc, used in the parallel groove clamps, connectors etc. shall be made of stainless steel.

All parts of fittings shall be either inherently resistant to atmospheric corrosion or suitably protected against corrosion both during service and storage. All current carrying parts shall be so designed and manufactured so that minimize the contact resistance.Post insulator clamps/hardware:

Post insulator clamps required for supporting the connections between the switchyard equipment in the various bays shall be supplied by the Bidder.

The post insulator clamp shall permit expansion / contraction in the conductors constituting the connections such that post insulators are not subject to any bending moment on account of the loads resulting from the expansion/contraction of the connections.

The clamps shall be made of aluminum alloy and so designed and manufactured that visible corona never sets in under all type of operating conditions at site.

GENERAL TECHNICAL REQUIREMENTS: (Earth wire)

The details of the galvanized stranded steel earth wire are tabulated below:

- Stranding and wire diameter - 7/3.66mm galvanized of 94 Kg/Sq mm

- Number of Strands inner wire (Steel core)	1

Out Steel Layer - 6

- Total Sectional Area73.64 Sq.mm

- Overall Diameter	10.98 mm

- Approximate Weight	483

Kg/Km

| - Minimum ultimate tensile Strength - Director of lay of outer layer |  |  | 68.4 KN Right Hand |
| --- | --- | --- | --- |
| h) Calculated D.C. Resistance at WORKMANSHIP: | 20 C - | 2.4 ohms/Km |  |

All steel strands of other earth wire shall be smooth, uniform and free from all imperfections such as spills and splits, die marks, scratches, abrasions and kinds after drawing and also after stranding. The earth wire shall be free from grease, metal particles dirt etc.

The finished steel strands shall have minimum brittleness, as it will be subjected to appreciable vibrations while in use.

Steel strands shall be dip galvanized and shall have a minimum zinc coating of 274 gms/sq.m. The zinc coating shall be smooth, continuous of uniforms thickness, free from imperfections.

TECHNICAL SPECIFICATION FOR SUBSTATION HARDWARE, CLAMPS & CONNECTORS

The connectors used for connecting Aluminium busbars, tubes and ACSR conductors should be made of Aluminium Alloy in conformity with IS:617/1959 and latest ISS and shall have adequate strength for use in the outdoor conditions. The clamps and connectors shall be in accordance with the requirements in BS: 159/1957 and IS:5561/1970 or latest ISS.

The clamps and connectors shall be of adequate cross sectional area to be able to carry the full load current as well as the heavy rush of current during short circuits. The connectors shall be rated for 2500 Amps rating as per the requirement. The temperature rise shall not exceed that specified in Clause-6 of Is:5561/1970 when carrying rated normal current of the conductors/tubes connected to the clamps.The clamp shall comprise not more than 2 pieces other than Bolts and Nuts wherever the connection takes place with conductor of ACSR.

The clamps shall be so designed as to be able to withstand the force arising under service conditions due to expansion and contraction.

The clamps shall have current paths as short and direct as possible. Clevices in which moisture is likely to get accumulated shall be avoided.

The design will be such as to allow the pressure of clamping Bolts and evenly distributed over clamping surface, in order to avoid strain in the conductor and also to avoid hot spots. The contract pressure for which the joint is designed shall be indicated.

Where connections between copper and aluminium are involved suitable bimetallic strips shall be used so that electr5olytic action between the two metals prevented. Copper coating on Aluminium

will not be accepted.Bolts, Nuts and Washers used with the connectors shall be made of mild steel and shall be hot dip galvanized and made corrosion resistant as recommended in BS: 1706/1960.Clamps and connectors should be provided with double Bolts, Nuts and Spring Washers.The busbar clamps and equipment connectors should be so shaped as to facilitate formation of smooth curves for the jumper connections. Where the terminals pad or stud is in vertical plane and the jumper is to be taken horizontally or vice-versa, necessary ‘L’ clamps should be supplied along with the terminal connectors. The drawings for each type of clamps set should accompany the Tender.To facilitate easy identification at the time of use of the clamps and connectors, the diameter of the conductors being connected and the terminals of the equipment may be provided on all the clamps and connectors.

The finishing of the clamps shall be neat in appearance and should exhibit high workmanship. DESIGN FEATURES AND GENERAL SPECIFICATION FOR HARDWARE FITTINGS : TENSION HARDWARE FITTINGS:

The hardware fittings shall be made of heat treated malleable cast iron or drop forged steel and shall be hot dip galvanized.The clamps and fittings shall be tested in conformity with ISS:2486, Part-I and 11/1963 with latest amendments, if any. The hardware shall be suitable for use with ball and socket type insulators of 16mm pin diameter.The tension set hardware include complete set of tension materials without disc insulators ) with bolted type tension clamps and metal parts such as ‘U’ bolts, ball link, socket eye etc., complete in all respects and include all fittings necessary for bus bar stringing.The ‘Tension Clamp’ body shall be made of Grade-A malleable cast iron to IS:2108/1962 or Grade-B malleable iron to BS:310/1958. They should ensure long and continued service withstanding the vibration fatigue and free from blow holes and other casting defects such as cracks etc.,The tension clamps shall be bolted type and shall not permit slipping of or damage to or failure of the complete conductor at any part thereof at load less than 95% of the ultimate strength of the conductor.

The slipping strength and ultimate strength shall not be less than the specified values given below

Sl.

No.

Particulars	Suspension	Tension Sets (Kgs.)

Hardware Clamps for ACSR Conductors

- Sliping Strength	3,300

6,650 b)	Ultimate Strength 7,000

7,000

c) Minimum Failing Load	7,000	7,000

- Other	Hardware	Minimum Failing loads. 7,000 7,000

- Tension Clamp for 7/8” SWG	6,400

Bolts, Nuts and Washers used shall be made from mild steel and shall be hot dip galvanized and made corrosion resistant as recommended in BS:1706/1960.	The insulator stringing hardware including clamp body be hot dip galvanized. Electro galvanization is not acceptable. The design will be such as to allow the pressure of clamping bolts evenly distributed over clamping surface in order to avoid strain in the conductor and also to avoid hot spots.

The ‘U’ Bolts shall be fitted with hexagonal nut and a checknut and washers. After tightening, two or three threads must be left over.

All forging and casting shall be of good finish free from flaws and other defects. The edges of the outside fittings such as at the eye, clevis and holes shall be rounded. For use with ACSR conductors, Aluminium liners are to be provided for clamps and Aluminium saddle shall be provided at each ‘U’ Bolts point for tightening the ‘U’ bolts.

The edge of the clamps body shall be atleast one and half times the diameter of the bolts to ensure prevention from breakage while tightening.

The clamps shall be so designed, so as to withstand the force arising under service conditions due to expansion and contraction.

The design of the suspension clamps shall be such as to avoid all hard spots and links which are likely to injure the conductors. There shall be no sharp radii of curvature and ridges. Suspension clamps shall be so designed that the effects of vibration, both on the conductor and fittings itself are minimized. The clamps shall have ease of oscillation around a horizontal axis, light in weight, low effective power loss and small moment of inertia. The suspension clamp shall permit the conductor to slip before failure of the conductor occurs and shall have a sufficient

slipping strength to resist conductor tension under broken wire conditions. It shall have sufficient contract surface to minimize damages due to fault currents mentioned in the Appendix. The suspension clamps shall be provided with suitable socket or clevis eye for connecting it to the insulator string.

The body of the suspension clamp shall be made out of the high strength Aluminium Alloy and the hardware fittings with malleable cast iron.

The ‘U’ bolt type tension clamps shall be designed in such a way to bond the conductor through an arc of 60 to 120 deg and to grip the conductors with pressure applied by ‘U’ Bolts.

BOLTED TYPE TENSION CLAMPS FOR GROUND WIRE :

The tension clamp shall be made of hot dip galvanized malleable iron and shall be suitable for stringing 7/8” SWG ground wire for a working tension of 450 Kgs. The clamp shall be completed with eye link anchor shackles, bolts, nuts, washers and tinned flexible copper earth bonds. The clamp shall have provision for fixing the copper earth bonds. The slipping strength of the clamp should not be less than 95% of the breaking load of 6400 Kgs and the breaking strength shall not be less t5han the ultimate breaking strength (minimum breaking load) of the ground wire.

All tests as per ISS shall be conducted as per latest ISS

The successful contractor shall submit manufacturer drawings for each item in triplicate well in advance or commencement of the bus stringing and jempering works and got approved by Employer, All tests in accordance with latest issue of ISS/BSS shall be performed on all the hardware, clamps & connectors before supply by manufacturer.

  - SF6 GAS CIRCUIT BREAKERS TYPE AND RATING:

The circuit breaker shall be suitable for out door operation under the climatic conditions specified,without any protection from sun and rain.Circuit breakers should beof sulphur hexafluoride (SF6) type.

CIRCUITBREAKER PARAMETERS:

The basic technical parameters of the circuit breakers to be suppliedareindicatedbelow.

| 1. | (a)Numberof poles | 3 |
| --- | --- | --- |
| 2. | Class | Out DoorType |
| 3. | NominalSystemVoltage | dependingon the systemvoltage |
| 4. | Rated Voltage | dependingon the systemvoltage |
| 5 | Typeofoperation | spring/spring |

STANDARDS :

The circuit breakers and associated accessories shall conform to the latestissue of IEC:62271-100 standards and relevant Indian Standards wherever applicable.

GENERAL:

The circuit breaker shall be of modular construction with all components manufactured to assure the maximum inter- changeability of standard basic elements. All parts of the breaker unit shall be mechanically designed to withstand all electrical, mechanical and other stresses that may be experienced in the operation of the unit including those under short circuit conditions. Suitable lock nuts and locking plates shall be provided for bolts and nuts inside the mechanism housing to avoid loosening of the bolts & nuts due to vibrations. The breaker shall comprise of three identical single pole units, linked together electrically, complete in all respects with the associated accessories including fittings and wiring.

The design and construction of the equipment valves, couplings, connections shall be such that leakage of any SF6 gas shall be minimum.Similarly, valves, couplings and pipe work shall be so arranged that accidental loss of gas to the atmosphere shall also be minimum.

The circuit breakers shall be provided with two trip coils per pole having common electrical circuit.

Weather proof and corrosion proof rating plates showing all the details as per clause 13 of IS: 2516 (Part III/Sec2) of latest edition shall be provided on all circuit breakers and its operating devices.

The circuit breakers shall be reasonably quiet in operation.

All fittings and accessories which may not have been specifically mentioned, but which are necessary and essential for the efficient working, shall be deemed to be included in the contract.

DUTY REQUIREMENTS:

The circuit breakers shall be totally re-strike free under all duty conditions and shall be capable of performing their duties.

- The circuit breakers shall be so constructed that they would fail safe in the event of loss of SF6 gas pressure or loss of air pressure in the pneumatic operating mechanism below a certain level.

- The circuit breaker shall meet the duty requirements for any type of fault or fault location.

- The circuit breaker shall be capable of carrying, continuously under site conditions, the rated rms value of the current without deterioration at its rated frequency with the temperature rise of the various parts not exceeding the values specified in IEC.

- The circuit breaker shall be capable of rapid and smooth interruption of current, completely suppressing all undesirable phenomena under all the conditions such as

severe and persistent short circuit, interruption of steady and transient magnetizing current of transformers, small inductive currents, fault current under phase opposition condition etc.

- The circuit breaker shall be suitable for three phase and single phase auto re- closing duty of O-0.3 Sec -CO-3 min-CO where dead time is 300 m sec.

- The circuit breaker shall be of single break and the breaker shall satisfactorily withstand the high stresses imposed on them during fault clearing, load rejection and re- energisation of lines with trapped charges. The breaker contacts (Main & arcing) shall be of high erosion resistant and the erosion of contacts shall be minimum.

CONSTRUCTIONAL FEATURES :

The features and constructional details of circuit breakers shall be in accordance with requirements stated hereunder.The guaranteed technical particulars shall be furnished as per the format enclosed.

CONTACTS:

(a) All making and breaking contacts shall be sealed and free from atmospheric effects. The contacts shall be permanently under the pressure of SF6 gas. The gap between open contacts shall be such that it can withstand the rated dielectric stresses at zero gauge pressure of SF6 gas due to its leakage.

- Main contacts shall be the first to open and the last to close so that there will be little contact burning and wear.

- Arcing contacts shall be the first to close and the last to open and shall be easily accessible for inspection and replacement. If there are no separately mounted arcing contacts, the main contacts shall be accessible for inspection and replacement.

- Main contacts shall have ample area and contact pressure for carrying the rated current and the short time rated current of the breaker without excessive temperature rise that may cause pitting or welding.

- Tips of arcing and main contacts shall be silver plated or have a tungsten alloy tipping.

- Positive mechanical connections shall be providedbetween interrupting contacts, blast valve mechanism, if any, to ensure maximum operating reliability and retention timing.

INSULATING SUPPORTS AND HOUSING:

Porcelain used in the manufacture of insulating supports/housing shall be h o m o g e n o u s , free from cavities and other flaws or imperfections that might affect the mechanical or dielectric quality and shall be thoroughly vitrified, tough and impervious to moisture. Glazing of the porcelain shall be of uniform brown Colour, free from blisters, burns and similar other defects.Porcelain supports/ housings shall be designed to have ample insulation, mechanical strength and rigidity for the conditions under which these will be used.Allinsulatorhousings ofidentical ratings shallbe interchangeable. The puncture strength shall be greater than the dry flash over value.When operating at normal rated voltage, there shall be no electric discharge between the conductor and the porcelainparts,whichmaycause corrosion orinjury to conductors/insulators or supports by the formation of substances produced by chemical action.The insulating supports/ housings shall be free from radio disturbances when operating at rated voltage and shall also be free from external/internal corona. The insulating supports/ housing shall satisfactorily withstand the insulation level specified for circuit breakers.

SULPHUR HEXAFLOURIDE GAS (SF6 GAS) :

- SF6 gas shall comply with IEC: 376 and be suitable in all respects for use in the switchgear under the operating conditions.The necessary test certificates shall be furnished during inspection of breakers.

- The high pressure cylinders in which the SF6 gas is shipped and stored at site shall comply with requirements of the following standards and regulations:

  - IS:4379 -Identification of the contents of Industrial G a s Cylinders.

  - IS:7311	-

Seamless high carbon steel cylinders for permanent and high pressure liquefiable gases.

- Absorbent shall be provided in the interrupter unit of each phase to absorb any traces of moisture. These shall be permanent facilities.

- The precise procedure to be adopted by maintenance personnel for handling equipment.

SUPPORT STRUCTURE:

The contractor shall supply the SF6 breaker along with support structures of self-supporting type and foundation bolts required. The clearance between the live parts to ground shall be as per electricity

rules. with support structure plinth height of 300 mm. Support structure and foundation bolts shall be supplied along with each breaker.

OPERATING MECHANISM: GENERAL:

- Circuit breaker mechanism shall be spring/spring for opening and closing of the breaker contacts and shall be electrically gang operating type. The mechanism shall be strong, positive, quick in action and shall be removable without disturbing the other parts of the circuit breaker. The mechanism shall operate simultaneously without requiring any critical adjustment.

- The operating mechanism shall be suitable for high speed re- closing over a wide range of parameters. It shall be anti- pumping and trip free. In case of failure of a pole to close properly, all the three poles should trip.

- A mechanical indicator along with operation counter shall be provided in addition to facilities for remote electrical indication to show open and close position of breaker. It shall be located in a position where it will be visible to a man standing on the ground with the mechanism housing closed and easily assessable from the ground for the O&M personnel to operate and maintain locally.

- The control circuit shall be designed to operate on 110V +/- 10% DC. Closing coil and trip coil shall operate correctly at all values of voltage between 85% to 110% and 70% to 110% of the rated voltage respectively.The necessary wiring shall be made in the cubicle and terminated at the terminal block to extend the wiring to the control room.

- Working parts of the mechanism shall be of corrosion resisting material.Bearings which require grease shall be equipped with pressure type grease fittings. Bearing pins, bolts, nuts and other parts shall be adequately locked by split pins, lock nuts, plates wherever required to prevent loosening or changing adjustment with repeated operation of the breaker.

- Operating mechanism shall normally be operated by remote electrical control.Electrical tripping shall be performed by shunt trip coils. Shunt trip coils shall operate correctly at all values of voltage between 70% to 110% up to breaking capacity of the breaker. Provisions shall be made for local electrical control.`Local/remote' selector switch and close and trip push buttons shall be provided in the breaker control cabinet on a hinged panel with position locked with bolt and nuts to provide access to the rear of panel for maintenance purpose. The relay trip should act independent of

the position of local/remote selector switch.

- A push button shall be provided to trip all 3 phases electrically from local. In the event of failure of auxiliary supply, manual emergency trip lever shall also be provided on each phase to trip them individually.

- Operating mechanism of each phase shall be housed in the individual operating mechanism housing along with all pressure switches, gauges, indication and other equipment while all the necessary controls are housed in free handling marshalling box, which is common for all three phases. The operating mechanism housing and marshalling box shall be of outdoor type and weatherproof. These boxes shall be fabricated out of not less than

12 SWG thick mild steel cold rolled sheet of tested quality complying with the latest edition/amendment of IS 513/1973.The operating mechanism housing and marshalling box shall have hinged door, which could be easily closed without applying excessive pressure on the doors. The door hinges shall operate at ease and strong enough to withstand the self weight of the door and to keep the door properly aligned. The complete box shall be fabricated in such a way that when closed it shall be perfectly water tight, dust proof and vermin proof and conform to IP55 as per IS: 2147. All Marshalling boxes shall be provided with necessary fixtures for fixing the cable entry and exit pipes with check nuts on all the sides of the marshalling box.Thermostatically controlled space heaters, a light point with a door switch shall be provided and MCBs shall be used for protection of supply to space heaters.The mounting height of the marshalling box shall be easily assessable for a person standing on the ground for operation and maintenance.

- Provisions shall be made on breakers for attaching an operation analyser to perform speed tests after installation at site to record contact travel against time and measure opening time.

- The circuit breaker shall be provided with pole position discrepancy detector.

- The contractor shall furnish along with Test Certificates, curves

supported by test data indicating opening time under close-open operation with combined variation of trip coil voltage and operating pressure.

- In case of spring/spring mechanism, the closing and tripping operations shall be by spring charging. When the closing signal energizes the Closing coil, the trigger shall release and the charged closing spring shall close the Breaker and also recharge the

opening spring. When opening signal is given, the energy accumulated in the opening spring shall be released and cause the main contacts of the breaker to separate.

- The spring operating mechanism shall have adequate energy stored in the operating springs to close/open and latch the Circuit Breaker against the rated making current and also to provide required energy for both closing and tripping mechanism.

- The spring charging motor shall not take more than 10 seconds for fully charging the closing springs and provision shall be made for automatic charging of the closing springs as soon as they are discharged in a closing operation. For this, the mechanism shall be such that the charging of the springs by the motor does not interfere with the operation of the Breaker.

- The motor shall be adequately rated to carry out a minimum of 5 close and open operations continuously. Also provision shall be made to protect the motor against over loads.

- Mechanical inter locks shall be provided in the operating mechanism to prevent discharging of the closing springs when the Breaker is already in the closed position. Provision shall also be made to prevent a closing operation to be carried out with the spring partially charged.

- Facility shall be provided for manual charging of the closing springs and it shall be possible to operate the same standing on the ground. affected by possible irritants of the skin and respiratory system.

ADDITIONAL REQUIREMENTS FOR SF6 GAS CIRCUIT BREAKERS

Circuit breakers shall be of pressure type and utilise puffer cylinder for interrupting circuit currents. Adequate service pressure of SF6 gas shall be provided. Protective measures to prevent operation of the breaker in the event of drop in SF6 gas pressure shall be provided.

Design and construction of the circuit breaker shall be such that there is minimum possibility of gas leakage and ingress of moisture. There should not be any condensation of SF6 gas on internal insulating surfaces of the circuit breaker.

The design of the breaker shall be such that, upon loss of pressure, the gap between open contacts shall be suitable to withstand at least the rated voltage at zero gauge pressure of the gas.

In the interrupter assembly there shall be an absorbing product box to eliminate SF6 decomposition products and moisture. Materials such as activated alumina or molecular sieve shall be provided at appropriate location as moisture absorbent.

Potential free contacts shall be wired to terminal block for low gas pressure alarm and lockout, which can be used at remote panels

If each pole forms an enclosure filled with SF6 independent of the two other poles, the pressure of each pole shall be monitored and regulated by individual pressure switches.

Facilities shall be provided to reduce the gas pressure within the circuit breaker to a value not exceeding 8 milli bars within 4 hours or less. Each circuit breaker shall be capable of withstanding this degree of vacuum without distortion or failure of any part.

Material used in the construction of circuit breakers shall be fully compatible with SF6.

The pole units shall be filled with SF6 gas at atmospheric pressure of 0.5-1 kg/sq. cm before dispatch and sufficient SF6 gas shall be supplied to fill all the circuit breakers installed to the required pressure plus an additional 20% of the quantity to compensate for losses.

RATING PLATE:

Weather proof and corrosion proof rating plates showing year of manufacture and other values as per IS: 2516/IEC-62271 - 100 shall be provided on all circuit breakers and its operating devices.

TERMINAL CONNECTORS AND EARTHING TERMINALS:

Breakers shall be supplied withTerminal connectors suitable for ACSR Conductors. The terminal connectors shall be either bi- metallic or aluminium as the case may be and shall be suitable for both vertical and horizontal take off. The terminal pads of the breaker shall be such that it is possible to connect the terminal connectors on the opposite sides of the terminal pad depending upon the site requirement. Suitable terminals for earthing connectors for earthing connections shall also be provided for the structures, operating cubicles and marshalling boxes. The actual sizes of grounding conductors is 50 x 6 mm steel flat.

TERMINAL BLOCKS :

Terminal blocks shall be 1100 V grade and of current capacity 10

Amps with insulated barriers, stud type terminals suitable for 4 wire up to 2.5 sq. mm, spring washers, nut and lock nuts and identification strips.All wiring terminations shall be with suitable tinned copper crimped lugs.All wiring shall be carried out with flameproof insulated wires made up of tinned or annealed copper conductor.

AUXILIARY SWITCHES:

They shall be capable of breaking at least 2 Amps at 220V DC with circuit time constant of not less than 20 milli seconds. If installed on the frame of breakers, it shall be suitably protected against accidental arcing from the main circuit. The insulating materials of the switches

and terminals shall be of ceramic or other non-tracking and non-hygroscopic materials. All the contacts (10 NO & 10 NC) of Aux. Switch shall be wired up to the terminal blocks.

Special contacts for use with trip coils and single shot re-closing operation, which permit relative adjustment with respect to the travel of the circuit breaker shall also be provided wherever required. Required number of auxiliary switches shall be provided.

INTERLOCKS

Necessary interlocks to prevent the closing of the breaker (manual and remote) under low gas pressure and devices for initiating alarm shall be provided. Provision shall also be made to wire up to the terminal block.

FITTINGS AND ACCESSORIES:

The contractor shall furnish the following fittings and accessories as an integral part of the equipment:

  - Operating Mechanism Housing

    - Pad locks and duplicate keys

    - Local/remote change over switch

    - Operation counter

    - Terminal board with minimum 6 spare terminals

    - MCB/MCCB to cut off control power supply, wherever required.

    - Two earthing terminals

    - Auxiliary relays required for satisfactory operation

    - Breaker local control switch, 3 pin 16 A socket outlet

    - Terminal connectors

    - Earthing pads

    - Foundation bolts

    - Galvanised steel structures/Steel frames for mounting of the breakers.

    - Necessary cables from respective Control cubicles to Marshalling box/Central control cubicle of the Breaker.

Apart from the above, one set of SF6 Gas regulator along with hose for Gas filling/evacuating shall be supplied.

TESTS AND CONDITIONS FOR DISPATCH :

Each circuit breaker shall comply with the type test and the routine tests prescribed in IEC-62271 -

100. The routine acceptance tests shall be carried out on each breaker before dispatch.

Report of all type tests as stipulated in IS/IEC and the line charging current and transformer charging current, interrupting tests shall be furnished along with the bid, if a l r eady carried out, otherwise the type tests shall be carried out

No equipment shall be dispatched without prior approval of the test certificate and dispatch instructions are conveyed by the Engineer

Routine acceptance tests shall be carried out on each breaker in the presence of Engineer’s representative. Also the Engineer’s representative shall have access to the contractor's works for the purpose of inspecting the manufacture of the equipment and Test certificates in six sets shall be furnished for approval.

SITE TESTS ON CONTROL AND AUXILIARY CIRCUITS :

The following site tests shall be carried out at the time of commissioning of the breakers:

- Voltage tests on control and auxiliary circuits

- Measurement of resistance in the main circuit.

- Mechanical operating tests.

- Speed curves shall be obtained with the help of a suitable operation analyser to determine breaker contact movement duringopening,closing,auto-reclosing and trip free operation under normal as well as limiting operating conditions (control voltage, gas pressures etc.). The tests shall show the speed of contacts at various stages of operation, travel of contacts, opening time, closing time, shortest time between separation and meeting of contacts at break-make operation etc.

- Tests to measure the difference in the instance of closing/opening of contacts between poles.

TESTS ON SF6 GAS :

The test certificates as obtained from the SF6 gas supplier shall be furnished during inspection of the circuit breakers.

TRANSPORT, STORAGE, ERECTION & MAINTENANCE :

The manufacturer should provide instructions for the storage, erection and maintenance of circuit breakers. Special precautions should be taken for its protection during shipment.

Advice should be provided for unpacking and lifting to prevent damage. If necessary, the conditions under which the packed circuit breaker be stored should be stated. When circuit breaker is dismantled for transport, all parts should be clearly marked. Drawing showing assembly of these parts should be attached.

Instructions for mounting of circuit breaker, operating mechanism and auxiliary devices should include details of location and foundations. Instruction should be given for connection of leads providing adequate clearance distances. The manufacturer should give details regarding the maintenance measures to be observed

The information should include the number of short circuit operations and/ or operations in normal service after which the circuit breaker is to be overhauled.

The instructions should at least include:

  - Inspection, adjustment and renewal of contacts, advice  for resistance measurement of main circuit, permissible contact burning and information about tolerances on the opening and closing time.

  - Sampling, testing, drying and refilling of liquid or gas, recommendations for quality and freedom from contamination, and indication of the required quantity of oil (or other liquid).

  - Maintenance and adjustment of operating mechanism, checking of coils, relays, interlocking devices, adjustable electric devices, heating and drying devices, bearings (which parts) connections (which place) resistors and capacitors (allowed/variation of the values).

  - Checking of spring operations/ strength inspection and replacement of gaskets.

  - Specification for quality of oil and grease required for lubrication and greasing.

  - Recommendations for cleaning.

  - Part no. of various  components for ordering spares and replacements if any.

DRAWINGS :

The contractor shall furnish the following drawings for approval -

    - General outline drawings showing dimensional front side elevation and plan of the circuit breaker and its local control panel. The detailed dimensional drawings of mechanism housing, marshalling box and support structure.

    - Sectional view drawings.

    - Assembly and sub-assembly drawings of the breakers, arcing chambers, contacts, operating mechanism etc.

    - Detailed dimensional drawings and assembly of the auxiliaries.

    - Piping diagram.

    - Descriptive literature for circuit breaker and write-up for the control sequence.

    - Foundation plans including weights of various components

and impact loading.

    - Wiring	diagrams	showing	the	local	and	remote	control scheme of the breaker, including alarms, indicating devices, instruments, space heaters etc.

    - Terminal connectors for circuit breakers.

    - Net and shipping weight.

    - Complete Bill of Materials per breaker.

Detailed drawings or design data for the purpose of checking the adequacy of the contractor's designs by calculations will not ordinarily be required but the Engineer reserves the right to call for these in certain cases, at his discretion. Any manufacturing works performed prior to the approval of drawings will be at the contractor's risk.

When revised drawings are submitted for approval, the changes from the previous versions/submissions shall be clearly indicated on the drawings, with every revision made during the period of the contract shown by number, date and subject in a revision block and a notation shall be in the drawing margin. The drawings shall be clear and legible in all respects.

The Engineer shall have the right to request the contractor to make any changes in the design which may be necessary in the opinion of the Engineer to make equipment conform to the provision and intent of these specifications, without additional cost to the Engineer. Approval by the Engineer of the contractor's drawings shall not be considered to relieve the contractor of any part of the contractor's obligation to meet all the requirements of these specifications or of the responsibility for the correctness of the contractor's drawings.

The responsibility of getting the drawings duly approved by the Engineer as per milestone activity stipulated in rests with the contractor.

In addition, details such as dimensions, tolerances, materials detailed specification and drawings as may be necessary for erection, maintenance, repairs, identification of parts for ordering replacement parts shall be supplied by the contractor as and when required by the Engineer.

INSTRUCTION/OPERATION AND MAINTENANCE MANUALS:

Ten copies of operation and maintenance manuals of circuit breaker shall be supplied with in one month prior to the dispatch of equipment. The manuals shall be bound volumes and shall contain all the drawings and information required for erection, operation and maintenance of the equipment. The manuals shall include the following particulars amongst other things specified.

- Marked erection prints identifying the components of the equipment with the assembly drawings.

- Detailed dimensions, assembly and description of the equipment and accessories.

- The contractor shall submit to the Engineer detailed progress report of the manufacture and supply of the equipment, every month during the contract period.

- All applicable part and spare parts list shall be furnished in the erection manuals with part numbers.

  - TRANSFORMERS

The pump house shall be provided with adequate capacity of Power and Auxiliary transformers for satisfactory and safe operation of the pumping system. One spare Main and auxiliary transformers shall be provided. Calculations for fixing the rating of the transformers shall be provided along with the bid.

The SLD of the system is enclosed, which should be taken as a guideline. The bidders have to submit the SLD of the system for which they have quoted.

The General Technical specifications mentioned below is a general one common to all the transformers. For auxiliary transformers, some of the clauses will not be applicable. The bidder has to submit detailed technical specifications for each category of the transformer for the Engineer’s approval.

TECHNICAL SPECIFICATIONS FOR MAIN AND AUXULIARY TRANSFORMERS

Sl.No.	Particulars

- Capacity (MVA)	As per load requirement

- Type	Outdoor three phase

- System frequency	50 Hz

- Voltage rating	To suit power supply & Motors

- Percentage impedance at normal tap %	To be furnished.

- Type of cooling	ON AN

- Winding connection

HV	Delta

LV	Star

- Vector Group	DY n 11

- On load taps

Plus Minus

- Type of insulation HV

LV

- Insulation level in KV HSV

PFV BIL

5% HV

15% on LV

Taps to be provided on HV

Fully insulated Fully insulated As per IS

- Temperature rise	As per IS

SCOPE:

The Scope of this specification is the design, manufacture, testing, supply delivering at sites including unloading and commissioning of POWER TRANSFORMERS required for installation in the pump house.

PERFORMANCE REQUIREMENTS

  - Transformers shall operate without injurious heating at the rated MVA/ KVA at any voltage within ± 10 percent of the rated voltage of that particular tap in accordance with IS:6600.

  - Transformers shall be capable of delivering the rated current at a voltage equal to105 percent of the rated voltage without exceeding the limiting temperature rise.

  - Transformers shall be capable of operation continuously, in accordance with the applicable standard loading guide at their rated MVA/KVA and at any of the specified voltage ratios. Under these conditions, no limitations by terminal bushings,on-load tap changers or other auxiliary equipment shall apply.

  - The neutral terminal of windings with star connection shall be designed for the highest over current that can flow through this winding.

  - The transformers shall be designed with particular attention to the suppression of harmonic voltage, especially the third and fifth, so as to eliminate wave form distortion and any possibility of high frequency disturbances reaching a magnitude as to cause interference with communication circuits.

STANDARDS:

The applicable standards for Power Transformers including various accessories and fittings are specified here blow:

Colours for paints and enamels	IS 5 Ready mixed paint, brushing, zinc chrome plaster	IS 104 Ready mixed paint, brushing, priming, plaster	IS 109

Insulating-Oil	IS 335

Testing of steel sheets and strips for Magnetic circuits	IS 649 Solid press board for electrical purposes	IS 1576

Code of practice for maintenance of mineral insulating

oil in equipment

IS 1866

Code of practice for installation and maintenance of	IS 1886 Transformers

Power transformers	IS 2026 Part I to IV

Impulse voltage testing	IS 2070

High voltage testing	IS 2071

Porcelain bushings	IS 2099

Determination of water content in oil	IS 2362

Painting of Transformer	IS 2932

Porcelain Transformer bushings	IS 3347

Gas operated relays	IS 3637

Application guide for gas operated relay	IS 3638 Fittings and accessories for Power Transformers	IS 3639 Clamping arrangement for porcelain transformer bushing IS 4275 Electric Power Connectors	IS 5561

Testing of specific resistance of electrical insulating Liquid

IS 6262

Method oflest for power factor and Dielectric constant	IS 6262 of electrical Insulating liquid

Guide for loading of oil immersed Transformer	IS 6600 Determination of electric strength of Insulating Oils	IS 6792 OH impregnated, paper insulated Condenser bushing	IS 12676

SERVICE CONDITIONS:

As per IS 2026 (Part - I) - 1977, Clauses 3.1, 3.1.1 and 3.2.1.

General Design of Apparatus

The Transformers and accessories shall be designed and manufactured in accordance with IS 2026 and Section – A (General) of CBIP Technical Report No.1 in regard to design, standardization, galvanizing, labels, bolts and nuts, cleaning and painting, oil and prevention of acidity.

ELECTRICAL CHARACTERISTICS AND PERFORMANCE;

All transformers, unless otherwise specified shall be oil immersed and core type and shall be suitable for outdoor installation.

CONTINUOUS MAXIMUM RATING AND OVER LOAD;

Transformers provided with ON AN cooling shall in regard to rating, temperature and overloads comply with Clause 4.0 of IS 2026, Part-I with latest amendment thereof.

VOLTAGE RATIO

The voltage between phases on the higher and lower voltage windings of each transformer measure at no load and corresponding to the normal ratio of transformation shall be those stated in the ordering schedule and shall be capable of giving rated volts from the secondary when rated primary voltage is applied at the normal tap and at the rated frequency.

ELECTRICAL CONNECTIONS;

Transformers shall be connected in accordance with the IS Vector symbol specified.

The primary shall be connected in Delta and the secondary is Star following the Vector Group DY-II.

DUTY UNDER FAULT CONDITIONS;

Except where modified below, it is to be assumed that the amount of generating plant simultaneously connected in and that normal voltage will be maintained on one side of and transformer when there is a short circuit between phase or to earth on the other side. Any transformer may be directly connected to an underground or overhead transmission line and switched in to and out of service together with its associated transmission line.

REQUIREMENTS WITH REGARD TO AVAILABLITY TO WITHSTAND SHORT CIRCUIT;

As per IS 2026 (Part-I) Clause 8 & Sub-Clause thereof;

DEMONSTRATION OF ABILITY TO WITHSTAND SHORT CIRCUIT;

As per IS 2026 (Part-I) 1997, Clause 9 & Sub-Clause thereof;

LOSSES MEASUREMENT;

As per Clause 16.4 and 16.5 of IS 2026(Part-I) 1997.

TOLERANCE;

As per Clause 11 of IS 2926 (Part-I) 1997.

GUARANTEED LOSS;

The bidder should clearly indicate the guaranteed value in respect of under mentioned losses at normal tap.

- No load loss at rated voltage and rated frequency.

- Total losses including auxiliary losses at rated output, rated voltage and rated frequencies.

- The guaranteed values of the losses will be compared with that of tested values and in the event of tested values exceed former, the firm will be liable for penalty as per contract data.

In the event of measured losses exceeding the guaranteed loss penalty will be based as upto 10% excess losses, the transformer manufactured will be rejected.

Guaranteed losses mentioned in the bid will be datum and proportionate loading will be done for the difference.

No load loss and load loss are reckoned at Rs.2, 90,000 /- and	Rs.1, 18,500/- respectively per KW. The bidders shall note that the values assigned for capitalization of the losses are based on present worth.

Fraction of KW of loss will be rounded to nearest number and penalty of loading will be done accordingly.

REGULATION AND IMPEDANCE:

The impedance voltage at principal tap and rated KVA shall be stated in the bid and tolerance shall be in accordance with IS: 2026.

FLUX DENSITY:

The maximum flux density in any part of the core yokes, at normal voltage and frequency of each transformer shall be such that the flux density under over voltage condition shall not exceed 1.9 Tesla (19,000 Lines per Sq. Cm.)

SUPPRESSION AND HARMONICS:

All the transformers shall be designed with particular attention to the suppression of harmonic voltage, especially the third and fifth, so as to eliminate wave from distortion and from any possibility of high frequency disturbances, inductive effective or of circulating currents between the neutral points at different transforming stations reaching such is magnitude as to clause interference with communication circuits.

CORES:

CONSTRUCTION:

The cores shall be constructed from high grade cold rolled non-again grain oriented silicon steel laminations.

MAGNETIC CIRCUIT:

The design of the magnetic circuit shall be such to avoid static discharges, development of short-circuit paths within itself or to the earthed clamping structure and the production of flux components at right angle to the plane of the laminations which may cause local heating.

Extreme care shall be exercised in the selection, treatment and handling of core steel to ensure that as far as is practicable, the laminations are flat and the first assembled core is free from distortion.

The oxide/silicate coating given on the core steel is adequate.

Oil ducts shall be provided where necessary to ensure adequate cooling. The winding structure and major insulation shall not obstruct the free flow of oil through such ducts. Where the magnetic circuit is divided into pockets by cooling ducts parallel to the planes of the. laminations or by insulating material above 0.25mm luck, tinned copper strip bridging pieces shall be inserted to maintain electrical continuity between pockets.

The frame work and clamping arrangements shall be earthed in accordance will Clause

The insulation structure for the core to bolts and core to clamp plates shall be such as to withstand a voltage of 10 KV AC for one minute.

For consideration of over fluxing the transformer shall be suitable for continuous operation for values of over fluxing factor up to 1.1, this factor being v/vm x m/f. The manufacturer shall state the over fluxing capability and corresponding withstand durations for the transformers for factors 1.1, 1.25 and 1.4.

MECHANICAL CONSTRUCTION OF CORES:

All parts of the cores shall be of robust design capable of withstanding any shocks to which they may be subjected during lifting, transport, installation and service.

All steel sections used for supporting the core shall be thoroughly sand blasted or shot blasted after cutting, drilling and welding. Any non-magnetic or high resistance ally be of established quality.

Adequate-lifting lugs shall be provided to enable the core windings to be lifted.

Adequate provision shall be made to prevent movement of the core and winding relative to the tank during transport and installation or while, in service.

The supporting frame work of cores shall be so designed upto avoid the presence of pockets which would prevent complete emptying of the tank through, the drain valve, or cause tapping of air during filling.

WINDINGS:

All star connected windings for system of 66 KV and above shall have graded insulation as defined in Is: 2026. All windings for system voltages lower than 66 KV shall be fully insulated. All neutral points shall be insulated for the voltage specified in IS: 2026.

Power transformers shall be designed to withstand the impulse and power frequency test voltages as specified in IS: 2962.

The landings shall be designed to reduce to a minimum the out-of-balance forces in the transformer at all voltage rates.

The insulation of transformer windings and connections shall be free from insulating composition liable to soften, ooze out, shrink or collapse and be non catalytic and chemically inactive in transformer oil during service.

Windings shall be made using Class A paper insulated copper conductors. The conductors shall be electrolyte grade copper free from scales and burrs. The stacks of windings shall receive adequate shrinkage treatment before final assembly. Adjustable devices shall be provided for taking up any possible shrinkage of coils in service.

The coil clamping arrangement and the finished dimensions of any oil ducts shall be such as will not impede the free circulation of oil through the ducts.

No strip conductor wound on edge shall have a width exceeding six times its thickness.

The conductors shall be transposed at sufficient intervals in order to minimize eddy currents and equalize the distribution of currents and temperatures along the windings.

Further, windings shall be so designed that all coil assemblies of identical voltage ratings shall be interchangeable and that field repairs to the windings can be made readily without any special equipment. The coils shall be supported between adjacent sections by insulating spacers and barriers. All threaded connections shall be provided with looking facilities. All leads from the winding to the terminal board and bushings shall-be rigidly supported to prevent injury from vibration. Guides shall be used wherever practicable.

The windings shall be clamped securely in place so that they will not be displaced or deformed during the circuits.

The maximum current density in any winding shall not exceed 2.3A/Sq.mm.

BRACING OF WINDINGS:

The windings and connections .of all transformers shall be braced to withstand shocks which may occur during transport, or due to switching short circuit and other transient conditions during service.

INTERNAL EARTHING ARRANGEMENT:

All metal parts of the transformer with the exception of the individual core laminations, core bolts and associated individual clamping plates shall be maintained at some fixed potential.

EARTHING OF CORE CLAMPING STRUCTURE

The top main core clamping structure shall be connected to the tank body by a copper sump. The bottom clamping structure shall be earthed by one or more of the following methods.

- By connected through vertical tie-rods to the top structure.

- By direct metal-to-metal contact with the tank base maintained by the weight of the core and windings.

- By the connection to the top structure on the same side of the core as the main earth connection of the tank.

EARTHING OF MAGNETIC CIRCUIT:

The magnetic circuit shall be earthed to the clamping structures at one point only through a link placed in an accessible position beneath an inspection opening in the tank cover; the connection to the link shall be on the same side of the core as the main earth connection.

Magnetic circuits having an insulated sectional construction shall be provided with a separate link for each individual section. Where oil ducts or insulation barriers parallel to the plane of the laminations divide the magnetic circuit into two or more electrically separate parts the ducts or barriers shall be bridged in accordance with Clause 2.02(d) and the magnetic circuit shall not be regarded as being of sectional construction.

SIZE OF EARTHING CONNECTION:

Where coil clamping rings are of metal at earth potential each ring shall be connected to the adjacent core clamping structure on the same side of transformer as the main earth connections.

SIZE OF EARTHING CONNECTION:

All earthing connections with the exception of those from the individual coil clamping rings shall have a cross sectional are of not less than 0.2 Sq. Cm.

TANKS:

CONSTRUCTIONS:

The transformer tank and cover shall be fabricated from good commercial grade low carbon steel suitable for welding and adequate thickness. The tanks of all transformers shall be complete with all accessories an shall be designed so as to allow the complete transformer in the tank filled with oil, to be lifted by crane or jacks, transported by road, rail without over straining any joints and without causing subsequent leakage of oil.

The main tank body excluding tap changing compartments, radiators and coolers shall be capable of withstanding vacuum as per standards.

The base of each tank shall be so designed that it shall be possible to move the complete transformer unit by skidding in any direction without injury when using plates or rails. Normally a detachable under base will be used, but in case transport facilities permit, a fixed under case can be used.

Where the base of a channel construction, it shall be designed to prevent retention of water. Tank stiffeners shall be designed to prevent retention of water.

Where possible the transformer tank and its-accessories shall be designed without pockets wherein gas may collect pockets cannot be avoided, pipes shall be provided to vent the gas into the main expansion

pipe. The vent pipe shall have a minimum inside diameter of 15mm except for short branch pipes which may be 6 mm minimum inside diameter.

All joints other than those which may have to be broken shall be welded when required they shall be double welded. All bolted joints to the tank shall be fitted with suitable oil tight gaskets which shall give a satisfactory service under the operating conditions and guaranteed temperature rise conditions. Special attention shall be given to the methods of making hot oil tight joints between the tank and the cover as also between the cover and the bushing and all other outlets to ensure that the joints can be remade satisfactorily at side and with case with the help of semi-skilled labour.

However the minimum thickness of the plates used for Transformer Tanks shall not be less than 8 mm. for the sides and not less than 10mm, for the bottom plate and top cover.

LIFTING AND HAULAGE FACILITIES:

Each tank shall be provided with:

Lifting lugs suitable for lifting the transformer complete with oil.

A minimum of four jacking lugs, in accessible positions to enable the transformer complete withoil, to be raised or lowered using hydraulic or screw jacks. The minimum height of the lugs above the base shall be about 500 mm. Suitable haulage holes shall be provided

In addition the Transformers shall be provided with bollards on the Transformer Tank sides at the top for lifting the Transformer by a crane.

TANK COVER:

Each tank cover shall be of adequate strength, and shall not distort when lifted. Inspection openings shall be provided as necessary to give easy access to bushing or changing ratio or testing the earth purpose for which it is provided and at least two openings one at each end of the tank, shall be provided. The tank cover and inspection covers shall be provided with suitable lifting arrangements. Unless otherwise approved inspection covers shall not weight more than 25 Kg. Each.

The lank cover shall be fitted with pockets for thermometer and for the bulbs of oil and winding temperature indicators. Protection shall be provided where necessary, for each capillary tube.

The pocket shall be located in the position of maximum oil temperature at C.M.R. and it shall be possible remove the instrument bulbs, without lowering the oil in the tank.

AXLES AND WHEELS:

All wheels should be detachable and shall be made cast iron or steel or required.

Wherever specified, flanged wheels shall be provided suitable for use on gauge track as specified in the detailed specification and shall be so placed that pinch bar can be used to move the transformer.

The direction of motion shall be specified in case of unidirectional movement. If wheels are required to swivel, they shall be arranged to that they can be turned through an angle of 90 degrees when the tank is hacked up clear of the rails or floor. Means shall be provided for locking the swivel movements in positions parallel to and at right angles to the longitudinal axis of the tank. The wheels shall be suitable for movement on a rail track, the gauge of which shall be 1676 mm standard board gauge track.

CONSERVATOR VESSELS, OIL GAUGES AND BREATHERS:

A conservator complete with sump and drain valve shall be provided in such a position and not to obstruct the electrical connections to the transformer having a capacity between highest and lowest visible levels to meet the requirement of expansion of the total cold oil volume in the transformer and cooling equipment from the minimum ambient temperature to 90°C. The minimum indicated oil level shall be with the feed pipe from the man tank covered with not less than 15 mm. Depth of oil and the indicated rang of oil level shall be from minimum to maximum.

If the sum is formed by extending the feed pipe inside the conservator vessel, this extension shall be for at least 25 mm. The conservator shall be designed so that it can be completely drained by means of the drain valve provided, when mounted as in service.

One end of the conservator shall be bolted in to position so that it can be removed for cleaning purposes.

Normally one oil gauge magnetic/prismatic/plain type shall be provided. The oil level at 30 C shall be marked on the gauge.

Taps or valves shall not be fitted to oil gauge.

The oil connection from the transformer tank to the conservator vessel shall be arranged at the using angle of 3 to 9 degree to the horizontal up to the Buchholz Relay and shall consist of -

- For transformers up to and including 1000 KVA 25 mm, inside diameter pipes as per IS 3639.

- For transformer from 1001 to 10,000 KVA 50 mm, inside diameter pipes as per IS 3639.

- For transformers of over 10,000 KVA 80mm inside diameter pipes as per IS 3639.

A valve shall be provided at the conservator to cut off the oil supply to the transformer after providing a straight run of pipe for at least a length of five times the internal diameter of the pipe on the tank side of the gas and oil actuated relay and at least three times the internal diameter of the pipe on the conservator side of the gas and oil actuated relay.

Each conservator vessel shall be fitted with breather in which silicagel is the dehydrating agent and designed so that:

The passage of air is through the silicagel.

The external atmosphere is not continuously in contact with the silicagel.

The moisture absorption indicated by a change in color of the tinted crystals can be easily observed from distance.

All breathers shall be mounted at approximately 1,400 mm above ground level.

However (he conservator main tank shall be provided with a magnetic oil gauge and the partitioned conservator tank for the oil in the OLTC chamber shall be provided with a plain gas oil tube gauge.

FILTER AND DRAIN PLUGS, SAMPLING DEVICES AND  AIR RELEASE PLUGS

Each transformer shall be fitted with the following:

The filter and drain valves are specified.

A drain valve as specified below Shall be fitted to each conservator. For diameter upto 650 mm :	Size of the valve 15 mm.

For diameter above 650 mm :	Size of the valves 25 mm.

A robust oil sampling device shall be provided at the top and bottom of the main tank. The sampling device shall not be fitted on the filter valves specified under (a) above. However top, middle and bottom oil sampling valve shall me mounted at the tank base through suitable internally located pipe headers. One 15 mm air release plug.

All other valves opening at atmosphere shall fitted with blank flanges.

COOLER AND RADIATOR CONNECTIONS:

Valves and valve mountings shall be provided as specified under ‘Cooling Plant’ Cl. 7.0 Section - A of CBIP Manual.

All valves shall be of gun metal or cast steel or may have cast iron bodies with gun-metal fittings. They shall be of full way type with internal screw and shall be opened by turning counter clock wise when facing the hand wheel.

Means shall be provided for padlocking the bottom valves in the open and closed positions. This required for the valves where opening device like hand wheel, keys etc. are the integral part.

Every valve shall be provided with flanges having mechanical faces.

The drilling of valve flanges shall comply with the/requirements of IS 3939.

PRESSURE RELIEF DEVICE:

The pressure relief device shall -be provided of sufficient sizes of rapid release of any pressure that may be generated within the tank and which might result in damage to the equipment. The device shall operate at a static pressure of less than the hydraulic test pressure for transformer tank; Means shall be provided to prevent the ingress of rain.

Unless otherwise approved .the relief device shall be mounted on the main tank, and if on the cover shall be fitted with skirt projecting 25 mm, insider the tank and of such a design to prevent gas accumulation.

If a diaphragm is put at the base of pipe, an oil gauge is required on the standpipe for indicating fracture of diaphragm.

One of the following methods shall be used for relieving or equalizing the pressure in the pressure relief device.

An equalizer pipe connecting the pressure relief device to the conservator, or

The fixing of a silicagel breather to the pressure relief device the breather being mounted in a suitable position for access at ground level.

EARTHING TERMINAL:

Two earthing terminals capable of carrying for 4 seconds the full lower voltage, short circuit current of the transformer. Provision shall be made at positions close to each of the bottom two corners of the tank for bolting the earthing terminals to the tank structure to suit local conditions.

RATING AND DIAGRAM AND PROPERTY PLATES:

The following plates shall be fixed to the transformer tank at an average height of about 1750 mm, above ground level: A rating plate bearing the data specified in the appropriate clauses of IS 2026.

A diagram plate showing the internal connection and also the voltage vector relationship of the several windings in accordance with IS: 2026 and in addition a plan view of the transformer giving the correct physical relationship of the terminals. When links are provided in accordance with Clause 2.3 for changing the transformer ratio, then approved means shall be provided for clearly indicating ratio for which the transformer is connected. No load voltage shall be indicated for each tap.

Where specified a plate showing the location and function of all valves and air release cocks or plugs. This plate shall also warm operators to refer to the maintenance instructions before applying the vacuum treatment for drying.

The above plates shall be of material capable to withstanding continuous outdoor service.

JOINTS AND GASKETS:

All gaskets used for making oil tight joints shall be of proven material such as granulated cock bonded with synthetic rubber or synthetic rubber gaskets.

COOLING PLAN:

The transformer shall be supplied with the requisite number of radiators and coolers.

Radiators and cooler shall be so designed as to avoid pockets in which moisture may collected and shall withstand the pressure rests.

Unless the pipe work is shielded by adequate earthed metal the clearance between all pipe work and live parts shall lie more than the clearance for lives parts to earth.

Radiators connected directly to the tank shall be detachable and shall be provided with machined or ground flanged inlet and outlet branches. 19mm, drain plug shall be provide at the bottom and 29mm air release plug shall be provided at the top of each radiator for draining and filling.

Valves shall be provided in the tank at each point of connection to the tank.

Where separate radiator banks are provided, the conservator vessels specified in Clause 6.5, Section - A of CBIP Manual can be mounted thereon. .

All coolers shall be suitable for mounting on a flat concrete base. The oil circuit of all coolers shall be provided with the following:

A valve at each point of connection to the transformer tank.

Removable blanking plates to permit the blanking off the main oil connection of each cooler. A drain valve 25mm, lowest point of each bank of cooler.

A thermometer pocket fitted with a captive screwed cap on the inlet and outlet oil ranches of each separately mounted cooler bank.

A filter valve as specified in Clause 6.6, Section-A of CBIP Manual at the top and bottom of each cooler bank of cooler.

Air release plugs 15 mm.

VOLTAGE CONTROL (ON-LOAD TYPE):

The transformers shall be fitted with an on-load tap changer mechanism. [OLTC is not required for auxiliary transformer]

When specified, each transformer shall be provided with voltage control equipment of the tap changing type for varying its effective transformation ratio whilst the transformers are on load and without producing phase displacement.

Equipment for local and remote electrical and local manual operation shall be provided and shall comply with the following conditions. Local remote switch may be housed in remote control panel or in tap changer driving unit.It shall not be possible to operate the electric drive when the manual operating at the same time.Operating from the local or remote control switch shall cause one tap movement only until the control switch is returned to the off position between successive operations.

All eletrical control switches and the local operating gear shall be clearly labeled ina suitable manner to indicate the direction of tap changing.

The local control switches shall be mounted in the marshalling box, or driving gear housing.

The equipment shall be so arranged as to ensure that when a tap change has been commenced it shall be completed independently of the operation of the control relays or switches. If a failure of the auxiliary supply during a tap change or any other contingency such as tap changer getting stuck would result in that movement not being completed adequate means shall be provided to safeguard the transformer and its auxiliary equipment.

Suitable apparatus shall be provided for each transformer to give indications as follows:

To give an indication mechanically at the transformer and electrically at the remote control point if specified, of the number of tapping in use on the transformer.

To give an indication at the remote control point that a tap change is in progress, by means of an illuminated lamp.

For remote control, the switches, tap position indicator, etc. shall all be supplied as loose apparatus unless a remote control panel is specified.

All relays and operating devices shall operate correctly, at any voltage between the limits specified in the relevant Indian Standard.

Any enclosed compartment not oil filled and shall be adequately ventilated, metal clad thermostatically controlled heaters shall be provided in the driving mechanism chamber and in the marshalling box, all contractors, rely coils or Other parts shall be suitably protected against corrosion or deterioration due to condensation fungi etc.

The tap changer contacts which are not used for making or breaking current like separate selector switch contacts can be located inside main transformer tank where tap changer Construction permits such an arrangement. On load tap changers having separate compartment for selector contracts, the oil in such compartment shall be maintained under conservator head by means of pipe connection from the highest point of the chamber to the conservator. Such connection shall be controlled by suitable valve and shall be arranged so that any gas leaving the chamber will pass into the gas and oil actuated relay. A separate Buchholz relay/diverter switch may be provided for this compartment.

It shall not be possible for the oil in these compartments of the tap change equipment, which contain contacts used for making or breaking current, on mix with the oil in the compartments containing contacts not used for making or breaking current.

Each compartment in which the oil is not maintained under conservator head shall be provided with a suitable direct reading oil gauge.

The alternating supply for electrical operation of the control and indicating gear shall be standard 415 volts, three phase, 3 wire 50 Hz, along with 240 volts, single phase, 2 wire, 50 Ha, subject to a variation of + 10 to -30% so that the equipment offered can withstand variation in A.C.

Limit switches shall be provided to prevent over running of the mechanism and shall be directly connected in the circuit of the operating motor. In addition a mechanical stoop or oilier approved device shall be provided to prevent over running of the mechanism under any condition.

Limit switches may be connected in the control circuit of the operating motor provided that a mechanical deducting mechanism incorporated.

Thermal devices or other means like motor circuit breakers with shunt trip coil shall be provided to protect the motor and control circuits. All relays, switches, fuses, etc., shall be provided in the marshalling box or driving gear housing are shall be clearly marked together with any voltage within 10 percent of nominal valve.

The overload protection relay shall be of robust adjustable triple pole construction. It should provide accurate and reliable protection against overload, single phasing, overheating and short circuit.Contractors/Relays shall be of robust and compact construction and shall comply with Indian Standard IS: 2959.

The Contractors shall be suitable for operation at 110 volts A.C. - 15 percent to +10 percent 50 Hz. Main and auxiliary contacts of contractors shall be suitably rated. For sufficient long life these contacts shall be for double break type and shall make contacts practically bounce free.

The control supply transformer shall be single phase having ratio 415/55-0-55. Its insulation shall be suitable impregnated to render it non-hydroscopic.

All the control selector switches shall be robust and compact construction and shall comply with Indian Standard IS: 4064 and 4047.

Remote lap position indicator mounted on remote control cabinet shall show accurately same tap position as indicated by local tap position indicator on on-load tap changer. The remote indication can be by means of an analogue indicator, or digital indicator or by means of lamp indications. The remote indicator mounted on control cabinet shall not be affected by normal auxiliary voltages supply variation.Necessary indicating lamps provided shall be of low watt consumption of LED type.Space heater of adequate capacity and robust construction shall be provided inside each control cabinet to prevent moisture condensation. Space heaters shall be complete with miniature circuit breaker or “ON- OFF” switch.

All the wiring shall be carried out for motor circuit with 1100 volts grade PVC insulated standard copper conductors of size 2.5 sq. m. and for control circuit with 440 volts grade PVC insulated copper

conductor of size 1.5 Sq. m. suitable for tropical atmosphere. All wiring shall be in accordance with relevant IS or BS, Engraved core identification ferrules, marked to correspond with the wiring diagram shall be fitted at both ends of each wire. Ferrules shall fit tightly on the wires and shall not fall of when the wire is removed. All wiring shall be terminated on terminal blocks through suitable lugs. Insulated sleeves shall be provided at all the wire terminations. All wiring-shall be neatly bunched and cleared without affecting access to equipment mounted within the cabinet.

Terminal board rows should be spaced adequately apart to permit convenient access to wires and terminations.

Terminal boards hall be so placed with respect to the cable gland plate (at a minimum distances of 200mm) as to permit satisfactory arrangement of multi core cable tails without undue stress or bends opening of door should not disturb or stress the wire termination.

The tap changer shall be located in the HV windings. The tap change variation shall be in the range of

+5 to 15% of HV in steps of1.25% i.e.: 16 equal steps (number of position 17).

Parallel operation of transformer with on-load tap changer:

Besides the local and remote electrical control specified on-load tap changers, when specified, should be suitable for remote electrical parallel control also.

In addition to the methods of control as in clause 9, section ‘A’ of CBIP Manual, the following additional

provision shall be made.

Suitable selector switch be provided, so that one transformer of the group can at a time be selected as

“Master”. “Follower” or “Independent”.

HV Bushings:

The design of the bushing shall be such that stresses due to expansion and contraction in any part of the hushing shall not lead to deterioration.

Cement if used in the construction of the bushing shall not cause fracture by expansion or loosening by contraction. Cement thickness shall be as small and even as practicable.

All exposed ferrous metal parts shall be hot dip galvanized wherever possible. No arching horns shall be provided on the bushings.

Any stress shield shall be considered as an integral part of the bushing assembly.

52 KV and above voltage class bushings shall be Oil impregnated paper (OIL) type condenser bushings. The bushings below 52 KV volts class shall be porcelain, oil communicating or condenser type if specified.

Each bushing shall have marked upon it the manufacturer’s identification mark.

The duration and rated short time current of the bushing for various voltage ratings shall be as specified.Limits of temperature rise shall be in accordance with IS: 2099.

Permissible variation in the value of capacitance and maximum value of capacitance of value dielectric dissipation factor tan delta) of bushing andthe test tap on transformer bushings shall be as per IS: 2099 and IEC- 137.

Bushing made of solid insulation and those having a filling which does not flow under separate conditions shall be suitable for mounting at any angle of inclination unless otherwise specified, those having a liquid filling shall be suitable for mounting at any angle of inclination to the vertical, not exceeding 330°C.

The cantilever strength of the bushing shall be in accordance with IEC - 137 and IS: 2099 unless otherwise specified.

The profile of the porcelain and spacing of the petticoats shall suit the duty specified. When specified petticoats of desired profile and petticoat spacing shall be offered.

The electrical characteristics of the bushings shall be in accordance with IS: 2099.

The dimensional parameters of the bushings upload and including 36 KV voltage class shall be in accordance with IS: 3347.

Rated current voltage, basic insulation level: The rated voltage, current and basic insulation level; of the bushings shall be in accordance with IS: 2099.Interchangeability: All the bushing above 52KV voltage rating shall have dimensions as mentioned in Clause 4.3, section-P if CBIP manual, to enable interchangeability with different makes of bushings manufactured in conformity with this specification.

The standardized dimensions shall be kept in view by the transformer manufacturers as well, while designing the transformers, so that the transformer can accept any bushing of the parameters and dimensions specified herein.

Other ratings of bushings, not covered in the specifications, shall be supplied, if required.

The basic insulation level, rated voltage and current and creep age distances for various voltage class bushings shall be as per IS

The minimum value of creep age distance specified is 25mm/KV of the rated voltage. The bushing shall be provided with oil level indicators.

The oil level indicator shall be so designed and dimensioned that oil level shall be clearly visible from ground level.The neutral bushings stud shall be suitable for connecting 506mm G.I. flat.

TEMPERATURE CONTROLLER:

The transformer shall be provided with a 150mm dial type thermometer for top oil temperature indicator, fitted with maximum reading pointer, resetting, device and two sets of electrical contacts. The contacts

shall be with mercury switches, electrically independent ungrounded. The accuracy class shall be +- 1.0%.

The temperature indicator shall be fitted in a tank mounted, weatherproof. Marshalling box.tripping contacts of winding temperature indicators shall be adjustable to close between 60 C and 120°C and both shall reopen when the temperature has fallen by about5°C.

All contacts shall be adjustable on a scale and shall be accessible for removal of the cover.It shall be possible to check the operation of the contacts and associated equipment.

Connections shall be brought from the device to terminals placed inside the marshalling box.

GAS AND OIL ACTUATED RELAYS: BUCHHOLTZ RELAY.

Each transformer shall be fitted with pas and oil actuated relay equipment to 1S:3637 having contacts which close following oil surge or low oil level conditions.

Each gas and oil actuated relay shall be provided with a pet cock to take a flexible pipe connection for checking the operation of the relay.

Where specified to allow gas to be collected at ground level, a pipe approximately 5mm inside diameter shall be connected to the gas release cock of the gas and oil actuated relay and brought down to a point approximately 1.25 mm above ground level, where it shall PC terminated by a cock.

A machined surface shall be provided on the top of each relay to facilitate the setting of the relays and to check the mounting angle in the pipe and the cross level of the relay.The design of the relay mounting arrangements, the associated pipe work and the cooling plant shall be such that maloperation of the relays shall not take place under normal service conditions.The pipe work skill be so arranged that all gas arising from the transformer should pass into the gas and oil-actuated relay. The oil circuit through the relay shall not form a delivery path a parallel with any circulating oil pipe, not shall it be tied into or connected through the pressure relief vent. Sharp bends in the pipe work shall be avoided.When a transformer is provided with two conservators the gas and oil actuated relays shall be arranged as follows:

If the two conservators are connected to the transformer by a common oil pipe one relay shall be installed in the common pipe.

If the two conservators are piped separately to the transformer two relays be installed, one in each pipe connection.

Adequate clearance between oil pipe work and live metal shall be provided. TEMPERATURE RISE:

As per clause 3.1 of IS: 2026 (Part- II) - 1977 INSULATION LEVELS:

As per IS: 2026 (Part - III) 1977, clauses 3.0, 5.0 and sub clauses thereof.

As per IS: 2026 (Part - IV) - 1977. However the transformer shall be designed for variable flux voltage as per clause 3.2 of the said IS.

INSULATING LIQUIDS:

Mineral insulting oil to be used shall comply with IS: 335-1972 (latest edition). Loose oil to be supplied shall be in sealed oil drums with 10% extra quantity over and above that required for the first filling.

MARSHALLING BOX:

A sheet steel vermin proof, well - ventilated and weather proof marshaling box of suitable construction shall be provided for the transformer ancillary apparatus. The box shall have domed or sloping roofs and interior and exterior painting shall be in accordance with clause 1.6.

The marshalling box, wherever provided shall accommodate the following equipments alternatively weather proof instruments can be mounted outdoor:Temperature indicators.

Control and protection equipment for the local electrical control of tap changer, if the same cannot be accommodated in the motor driving gear housing.Control and protection equipment for the cooling plant, andTerminal boards and gland plates for incoming and outgoing cables.

All the above equipment except (d) shall be mounted on the panels and back of panel wiring shall be used for interconnection.

The temperature indicators shall be so mounted that the dials are not more than 1600mm from ground level and the door(s) of adequate size.

To prevent internal condensation an approved type of metal clad heater shall be provided controlled by a suitable switch. Ventilation louvers shall be provided. Counselor 158 Executive Engineer

All incoming cables shall enter the kiosk from the bottom and the gland plate shall be not less than 450mm from the base of box. The gland plate and associated compartment shall be sealed in suitable manner to prevent the ingress of moisture from the cable trench.

Undrilled gland plate shall be provided for accommodating glands for incoming and outgoing cables.

TRANSFORMER PROTECTION:

DIFFERENTIAL PROTECTION:

This shall consist of electronic static high impedance biased type differential type.The percentage bias settings shall be adjustable in steps of 10% over a range of 20 to 80%. The percentage bias shall however be low near rated current sufficient to allow for OLTC tap variation and CT errors but shall be increased automatically for severe through faults to ensure stability even under CT saturation errors.The relay shall be very fast in operation with an operating time of not more than 20/30 milliseconds for 4 or 5 times its value under all fault conditions and even in the presence of harmonics

and CT saturation.The relays shall be inherently stable for external through fault conditions alternatively the relay may be provided with an unrestrained high set element with a pick up setting equal to 4 or 5 times the rated current to ensure automatically through fault stability. However to have a quicker operation for severe internal faults an unrestricted highest elements shall be provided.The relay shall offer a very low burden to the CT, each relay shall be provided with two sets of changeover contacts for tripping. It should be possible to connect all such contacts of all single-phase relays in tandem to obtain 6 sets close/open contacts for connection to multiple trip coils.The relay shall be accompanied by inter auxiliary current transformers to match the group of the power transformers.Alternatively a 3 phase biased differential relay for-the protection of 2 winding transformer having all the features detailed above and in addition built in intermediate current transformers for matching current and phase angle and current magnitude compensation by selector switches and easy integral test facilities to check functions of internal circuits of relays by test push buttons in the panel can be offered.

BACK-UP PROTECTION:

Electronic type back-up protection shall be provided to the transformer.The protection on the HV side shall consist of three numbers of non-directional 1DMT over current relays and one earth fault relay. Relays to have3-second characteristics and to be mounted horizontally in common case. All over current and earth fault relays shall be provided with high set instantaneous elements. These instantaneous elements shall wherever applicable be directionalised.

RESTRICTED EARTH FAULT PROTECTION:

An instantaneous single pole circulating current or high impendence voltage type relay with a suitable setting shall be provided. A stabilizing resistor shall be provided inthe relay circuit. These relays shall be provided on LV side of the transformer.

COMPONENTS OF THE TRANSFORMER

The transformer shall generally comprise of the following components/parts.

- HV line bushings.

- LV line bushings.

- LV neutral bushing.

- Bi-Metallic terminal connectors for HV.

- Bi-Metallic terminal connectors for LV. Cable for XLPE cable connections.

- Terminal connector for neutral suitable for connection to G.I. flats.

- Monogram plate.

- Main conservator with compartment of OLTC as per design with sump, drain valve lifts. Separate conservator for OLTC optional as per design.

- Oil filling hole with bolted cover for main conservator.

- 150mm dial magnetic oil level gauge with low-level alarm contact.

- 150mm dial winding temperature indicator with alarm trip contacts and maximum reading pointer.

- 150 mm dial oil temperature indicator with alarm and trip contacts and maximum reading pointer.

- Surge protection relay with one set of contact and one isolating valve on conservator side for OLTC.

- Pressure relief device with one set of contact

- Buchholtz relay with alarm and trip contacts two-wheel type isolating valves (50mm size) with directions for mounting marked on Buchholtz relay.

- De-hydrating silicagel with oil seal and glass inspection window.

- Prismatic oil gauge.

- Thermometer pocket.

- Air release plugs on main tank and bushing turrets.

- Inspection cover lifting lug.

- Inspection covers on main tank and side manholes for OLTC conservator.

- WTI CT test link box with access window for transformer of above 5 MVA capacities.

- Bath for oil temperature indicator with probe for capillary tubing.

- Bath for winding temperature indicator with probe for capillary tubing.

Marshalling box with PVC copper cable wiring 660/1100 grade (tank mounted weather proof) along with required control cables for connection to Buchholtz relay, temperature indicator etc.

On-load tap changer with operation counter and single phase-preventer if OLTC is of 3-phase 440V design.

Radiator with top and bottom shut off valve, lifting lug, air release and drain plug.

Combined rating and diagram plate and valve schedule line diagram. The rating plate shall be minimum l mm thick anodized cadmium steel plate

Lifting Bollards.

Jacking pads 500mm above the base with adequate pad area.Haulage eyes

Earthing pads suit to receive plate withM12 tapped holes to suit 4 bolted connections.

Earth connection between tank and cover.

Drain valve with locking arrangement and blanking plate.

Top filter valve (size 50mm) with blanking plate with 3Smm adopter with locking arrangement. Bottom filter valve (size 50mm) with blanking plate with 38mm adopter with locking arrangements. Middle sampling valve (size 15mm) with plugs.

Bottom sampling valve (size l5mm) with plug.

Piping arrangement from top and middle valve to the level of the bottom filter valve.Under base skid type.

Bi-directional rollers to suit 1676 mm track with locking arrangements. Top stay bracket for supporting the conservator.

Remote OLTC control panel with 2312 height and 610 mm depth with single phase prevented protection for driving mechanism motor and AC voltmeter of adequate rating.

GI/Copper bar (2 No of flats) of adequate rating from neutral bushing mounted on insulators to a convenient point near plate for neutral earth connection with terminal connection.

TENDER DRAWINGS AND LITERATURES:

Duplicate copies of following drawings and literatures shall be submitted along with tender. GA drawing showing dimensional details

Front and rear views of transformer with instrument and device position marked. Photographs of similar transformer supplied by the manufacturer.

Illustrative descriptive literature, general technical data.

CONTRACT DRAWINGS:

Agency shall submit drawings in quadruplicate for the approval of the employer prior to manufacturer in A3 A4 size only. After the drawings arc approved six copies of drawings shall be supplied for immediate use.

The agency shall forward the drawings and literature as follows:

One set of reproducible originals and 6 sets of blue print copies of all approved drawings along with 6 sets of literature, commissioning and maintenance manuals to the employer.

Four sets of blue print copies of all approved drawings along with four sets of literature and manual in respect of each of the stations.

Foundation drawings indicating the details of foundation plan cross section suitable for Normal Dry Soil taking actual SBC

Bushing assembly, plan, elevation, sectional view and details of joints, seals etc., Radiator assembly: Sectional View of radiator.

Interconnection diagram between Marshalling box and OLTC, Power Transformer and other associated equipments.

Dimensional drawings showing cooling passage in transformer core and windings.

Individual internal wiring diagram of all devices and elementary wiring diagram or relays for internal wiring.

Construction details of the switches, terminal blocks and test blocks etc.,

Diagram and rating plates as per details in the specification, temperature rise oil and wind high voltage test figures etc.

Assembly of OLTC gear mechanism: Full details of the main parts, limits and fits wearing parts, timing gear adjustments etc.

Dimensional drawings showing cooling passage in transformer core and windings.

It may be noted non-supply or part supply of drawings literature and manuals will be deemed as incomplete supply of Transformer

TESTS AT FACTORY:

The following tests shall be carried out in addition to any other customary tests and seven copies of test certificates shall be supplied before shipment of the equipment.

- Vacuum test with stand strength of tank.

- Tests for oil tightness.

- Materials tests on core, conductor and insulating materials,

- Leakage tests for radiators.

- All double weld shall be tested with nitrogen at not less than 7 Kg/ Sq. Cm. To ensure that no weld would sweat.

- Routine tests shall be carried out as per IS: 2026.

- Temperatures rise test shall be carried out.

TYPE TESTS:

The tenderer shall submit with his tender, type test reports of type test in conformity of IS: 2026. Type test reports in conformity with clause 17.3 of CBIP manual shall be furnished. .

After the completion of the manufacture, the routine tests shall be conducted on each unit and type test on one unit. These would be in conformity with IS: 2026 Clause 16.12. The zero-sequence test shall be conducted on each unit. This would in conformity with IS: 2026 Clause 16.13.

INSPECTION:

The inspection may be carried out by the employer at any stage of manufacture. The supplier shall arrange free access to the employer’s representative at a reasonable time when the work is in progress. Inspection and acceptance of any equipment under this specification by the employer shall not relieve the supplier of his obligation of furnishing equipment in accordance with the specification and shall not prevent subsequent rejection if the equipment is found to be defective.

The supplier shall keep the employer informed in advance about the manufacturing program so that arrangement can be made for inspection.

The employer reserves the right to insist for witnessing the acceptance/routine testing of the bought out item. No material shall be dispatched from its point of manufacture unless the material has been satisfactorily inspected and tested.

  - CURRENT TRANSFORMERS:

TYPE AND RATING :

The Current transformers shall be electro magnetic type suitable for outdoor use, single phase, 50 Hz, oil immersed, self cooled and suitable for operation under climatic conditions specified in Section- II without any protection from sun and rain.

STANDARDS:

The Current transformers shall comply with the latest issue of IS2705(part I,II,III and IV) or IEC-85 except where specified otherwise. Equipment meeting any other authoritative standard, which ensures an equal or better quality than the standard mentioned above, is also acceptable.

GENERAL

TECHNICAL: The technical parameters like ratio, No. of cores, burden etc., shall be as follows. The CTs shall be 0.2 class and shall have three cores suitable for following functions: protection, metering.	[ 2 for protection and one for metering]. The contractor shall select the suitable ratio, burden etc., Thecalculations for which shall be submitted during engineering stage for the approval of the purchaser.

The Current transformers shall be of single phase, oil immersed and self-cooled, dead tank type suitable for the services indicated, complete in all respects, conforming to the modern practice of design and manufacture.

The primary and secondary windings shall be Electrolytic grade Copper/ Aluminium with low hysterisis loss and high permeability core to ensure high accuracy at both normal and over currents or voltages. The current transformers shall be sealed to eliminate breathing and prevent air and moisture from entering the tank. These shall be provided with oil level gauge and a pressure-relieving

device capable of releasing abnormal internal pressure. The temperature rise shall be as specified in the latest IS: 2705.

Secondary terminals of current transformers shall be brought out in a weatherproof terminal box. Glands and lugs for terminating Engineer ’s external cable connections shall be provided.

Terminal and polarity marks shall be indelibly marked on each current transformer on the associated terminals and these marks shall be in accordance with relevant standards.

The current transformers shall be provided with the following accessories.

- Rigid	type	Terminal	connectors	suitable	for	single	ACSR	Drake conductor.

- Two earthing terminals on tanks on opposite sides.

- Oillevel gauge.

- Filling and draining plugs.

- Power factor testing terminal

- Facility for lifting bushings and tank.

- The quantity of insulating oil required for first filling. Di-electric dissipation factor of the oil shall not exceed 0.005. Insulating oil shall comply with applicable standards.

- Rating and diagram plate as per relevant standards.

- Pressure relieving device.

- Galvanised steel support structures along with foundation bolts.

Current transformers shall be given tropicalised treatment for satisfactory operation in hot and humid condition.

Current transformers shall be suitably braced to withstand stresses induced due to seismic forces of zone – II as per relevant IS.

The temperature rise shall not exceed the figures given in applicable standards for operation under ambient temperature conditions.

The tanks/bases and all exposed ferrous parts shall be hot dip galvanised and painted conforming to applicable standards.

In the case of multi-core CTs, it shall be possible to adjust the tap settings on any core independent of the setting on the other cores, for which purpose these tapings will have to be provided on the secondary windings.

No turns compensation shall be used in case of ‘PS’ class current transformers. Turns compensation, if any, should be clearly bought out in the technical data.

In case of multi ratio current transformers, the minimum specified requirements in respect of VA, accuracy, knee point voltage and maximum secondary resistance specified shall be met at all taps.

Magnetising characteristics (extending well beyond knee point voltage) and secondary impedance values shall be furnished for all protection cores.

INSULATORS/BUSHINGS :

Insulators / bushings shall conform to applicable standards and shall be made of homogeneous vitreous porcelain, the glazing of which shall be of uniform brown or dark brown in colour.

Oil filled insulators/bushings shall be hermetically sealed to prevent ingress of	moisture.Metallic bellows shall be used for cushioning and to allow for expansion.

TESTS & CONDITIONS FOR DISPATCH:

The following routine tests shall be carried out on all the current transformers in the presence of the Engineer ’s representative as per the relevant latest IS and 6 sets of test certificates shall be furnished for approval before dispatch. No equipment shall be dispatched before the approval of test certificates and dispatch instructions conveyed by the Engineer .

  - Verification of terminal markings and polarity.

  - Power frequency voltage with stand test on primary windings.

  - Power frequency voltage with stand test on secondary windings.

  - Over voltage inter turn test.

  - Determination of errors according to the requirements of the appropriate accuracy class.

  - Partial discharge test.

The following Type tests shall be carried out on one of the current transformers. If the contractor has already carried out type test on similar equipment, a copy of the same shall be furnished for Engineer’s reference. If type test is not carried out, the same shall be conducted free of cost and test certificates furnished for Engineer ’s approval.

- High voltage power frequency test on primary windings.

- High voltage power frequency test on secondary windings.

- Determination of errors according to the requirements of the appropriate accuracy class.

- Short time current test.

- Temperature rise test.

- Impulse voltage test.

A copy of the type test certificate for the following type tests carried out on one of the bushings shall be furnished for Engineer ’s reference.

- Power frequency visible discharge test.

- One minute power frequency withstand test.

- Full wave impulse voltage withstand test.

- Under oil flash over or puncture withstand test.

EARTHING TERMINAL :

Two numbers of 12 mm diameter brass bolts and nuts with spring washers for each box shall be provided by the side of the body of the marshalling box for fixing copper /GI 25X3 mm flat. The earthing terminal shall be identified by means of the sign marked, in a legible and indelible manner on or adjacent to the terminal. The terminals shall be provided  inside the marshalling box for connection of earthing leads. Earthing terminal shall have provision for terminating the earthing leads from neutral connection at the inside of the box.Suitable size cubicle heater and illuminating lamp with independent control switch shall be provided inside each marshalling box. The illuminating lamp shall be automatically switched on when the door is opened.The auxiliary supply voltage available at the marshalling box is 240+/-10% V, AC.

The general arrangement and other drawings pertaining to the marshalling boxes shall be submitted. The Bill of materials shall be indicated in the general arrangement drawing of marshalling box.

TESTS AND TEST CERTIFICATE :

The marshalling boxes shall withstand the insulation test of 2 kV AC(RMS) between terminals and earth or between adjacent terminals for one minute.All tests shall be conducted on the CT marshalling boxes in accordance with relevant IS in presence of the Engineer or his representative. Reports of the tests conducted on similar type of marshalling boxes shall be submitted along with the bid.

PAINTING :

The marshalling boxes shall be painted first with two coats of red oxide primer paint both inside and outside so as to with stand highly humid atmosphere. The inside surface of all boxes shall be painted with another coat of fresh Grey paint as per IS : 5: 1961, No.630, over the two coats of red oxide primer. The out side surface of the boxes shall be painted with light Grey paint as per IS 5: 1961,No.631, over two coats of red oxide primer. All the painting surfaces shall be thoroughly cleaned before applying primer paints.

TERMINAL CONNECTORS:

Suitable terminal connectors for ACSR conductor shall be supplied for the CTs. Terminals shall be so mounted as to enable easy connection.The terminal connector shall be suitable for horizontal/vertical take off Any extra quantity of terminal connectors required shall be supplied at the quoted unit rates

ELECTRO-MAGNETIC VOLTAGE TRANSFORMERS:

This section covers the design, manufacture, quality surveillance, assembly, testing at manufacturer’s works, supply and delivery of0.2 class Outdoor-Electro magnetic type voltage transformer

TYPE AND RATING:

The Voltage transformers shall be of the Outdoor type, single phase, 50 Hz, oil immersed, self cooled and suitable for operation under climatic conditions as specified in this tender document.

TECHNICAL PARAMETERS:

The technical parameters like ratio, No.of cores, burden etc., shall be as follows;

The PTs shall be 0.2 class and shall have three cores suitable for following functions: protection, metering.[2 for protection and one for metering]. The contractor shall select the suitable ratio, burden etc., The calculations for which shall be submitted during Engineering stage for the approval of the purchaser.

STANDARDS:

The EMVTs shall comply with the latest issue of IS - 3156 (Part I, II, III and IV) or IEC 186 and

186 A, except where specified otherwise. Voltage transformers meeting any other authoritative standard, which ensures an equal or better quality than the standard mentioned above, is also acceptable.

GENERAL:

- The EMVTs shall be of single phase, oil immersed and self cooled, suitable for the services indicated, complete in all respects, conforming to the modern practice of design and manufacture.

- The core shall be of high grade, non-ageing, electrical grade silicon laminated steel of low hysteresis loss and high permeability to ensure high accuracy at both normal and over voltages.

- The EMVTs shall be sealed to eliminate breathing and prevent air and moisture from entering the tank. These shall be provided with oil level gauge and a pressure relieving device

capable of releasing abnormal internal pressure. The temperature rise shall be as specified in the latest IS 3156.

- The primaries of all the EMVTs will be connected across phase and neutral of the system with the neutral solidly earthed. EMVT shall be designed to operate well below knee point.

- Secondary terminals of EMVTs shall be brought out in a weather proof terminal box. Glands and lugs for terminating purchaser’s external cable connections shall be provided.

- Terminal and polarity marks shall be indelibly marked on each EMVT on the associated terminals and these marks shall be in accordance with relevant standards.

- The secondary terminal box for the EMVT shall also include necessary HRC fuses for protecting the secondary circuit. Further, for the purpose of fuse supervision on remote panel both terminals of the fuse shall be brought out to the terminal block.

The Voltage transformers shall be provided with the following.

  - Two earthing terminals on tanks on opposite sides for connecting the purchaser’s earthing conductors.

  - Oil level gauge.

  - Filling and draining plugs.

  - Power factor testing terminal

  - Facility for lifting bushings and tank.

  - Rating and diagram plate as per relevant standards.

  - Pressure relieving device.

- Voltage transformers shall be given tropicalised treatment for satisfactory operation in hot and humid condition.

- Voltage transformers shall be suitably braced to withstand stresses induced due to seismic forces of zone – II of relevant IS.

- The temperature rise of Voltage transformers shall not exceed the figures given in applicable standards for operation under ambient temperature conditions.

- The tanks/bases and all exposed ferrous parts of the Voltage transformers shall be hot dip galvanized and painted confirming to applicable standards.

- The end of the primary winding of EMVT intended to be earthed shall be brought out through a bushing and earthing connection shall be made out side. This is required to facilitate meggering of the primary winding for which the earth connection has to be removed. A

caution plate on the cover shall be fixed to warn that VT is not to be energised unless earth connection is put.

INSULATORS/BUSHINGS:

Insulators / bushings shall conform to applicable standards and shall be made of homogeneous vitreous porcelain, the glazing of which shall be of uniform brown or dark brown in colour. Oil filled insulators/bushings shall be hermetically sealed to prevent ingress of moisture. A cushion of Nitrogen gas or Metallic bellows shall be used for cushioning and to allow for expansion.

TESTS AT MANUFACTURER’S WORKS:

The following routine tests shall be carried out on the electro magnetic voltage transformers in the presence of the purchaser’s representative as per the latest edition of IS: 3156 ( Part I to IV).

  - Verification of terminal markings and polarity.

  - Visual inspection and dimensional checks.

  - Power frequency voltage with stand test on primary windings.

  - Power frequency voltage with stand test on secondary windings.

  - Determination of errors according to the requirements of the appropriate accuracy class

  - Partial discharge test.

  - Tan delta measurement.

Note: Apart from the above, if any other tests are required to be carried as per IS:3156, the same shall be carried out.

The following Type tests shall be carried out on one of the Voltage transformers. If the bidder has already carried out type test on similar equipment, a copy of the same shall be furnished for Purchaser’s reference.

- High voltage power frequency withstand test on primary windings.

- High voltage power frequency withstand test on secondary windings.

- Determination of errors according to the requirements of the appropriate accuracy class.

- Impulse voltage with stand test on Voltage transformers for service in electrically exposed installation.

- Temperature rise test.

- All the routine tests shall be carried out after conducting di electric tests.

The Routine test certificates shall be furnished in 6 sets for purchaser’s approval and conveying dispatch instructions. No equipment shall be dispatched before the approval of test certificates and dispatch instructions conveyed by the purchaser.

A copy of the type test certificate for the following type tests carried out on one of the bushings as per the relevant IS, shall be furnished for purchaser’s reference.

  - Visual examination.

  - One minute power frequency dry withstand test. c)  Oil tightness test.

- Partial discharge test.

- Test for capacitance and power factor measurement.

TERMINAL CONNECTORS:

The terminal connectors suitable for connecting PT Primary terminals to ACSR conductors selected for interconnection of the equipments shall also be supplied. The terminal Connectors shall be suitable for horizontal/ vertical take off.

  - CAPACITOR VOLTAGE TRANSFORMERS:

TYPE AND RATING :

The Capacitor Voltage transformers shall be of the Outdoor type, single phase, 50 Hz, oil immersed, self cooled and suitable for operation under climatic conditions specified in Section-II without any protection from sun and rain.

The CVTs shall comply with latest issue of IS 9348, IS 3156 (Part IV) & IEC-186.Voltage transformers meeting any other authoritative standard, which ensures an equal or better quality than the standard mentioned above, is also acceptable.

The CVTs shall be of single phase, oil immersed and self-cooled, suitable for the services indicated, complete in all respects, conforming to the modern practice of design and manufacture.

The individual capacitor units built up inside the shell shall be so inter connected such that resulting inductance shall be minimum. The resultant combination of the capacitance and inductance shall not resonate within the frequency range of 50 to 550 KHz and shall be far beyond this range. The variation in capacitance due to temperature variation shall be within the limits as specified in IS3156, Part IV. The loss angle (Tan delta) shall be minimum in the carrier frequency range for 8800 pf capacitance values. The insertion loss shall be less than 0.5 db in the carrier frequency range with the capacitance duly compensated by means of tuning filters.

The complete assembled individual units shall be provided at both ends with cast alluminium alloy metal caps. Porcelain in contact with metal caps shall be hermetically sealed with recessed gaskets so as to prevent ingress of moisture.

The CVT shall be completely filled with insulation oil conforming to IS 335 and the oil shall not require renewal, replacement etc., at any stage during its life span while in service.

The maximum voltage stress in the dielectric of the capacitor element shall be limited to such a value that under surge conditions any puncture or flash over that occurs shall take place only on the outer surface of the insulator shell.

There shall be provision for separately earthing the low voltage side of the coupling condenser stack and the body of the CVT.

The secondary EMVT shall form an integral part of the CVT and shall consists of a high voltage transformer, the primary of which shall be connected to a suitable tap within the coupling capacitors. The primary and secondary windings shall be provided if necessary by design with damping resistors, and compensating inductance coils duly ensuring that the EMVT shall not be subjected to Ferro resonance. The secondary winding shall have 1 core which will be used for line indication/ synchronizing. The secondary terminals shall be brought out to a terminal secondary Marshalling box through HRC Fuse base and fuse cartridges. The secondary terminals shall be brass and of the front projecting stud type with check nuts and washers. Earth connections shall be through tinned copper links. There shall be separate glands for HF cable, and VT supply cables for secondary winding.

The CVT should be thermally and di-electrically safe when the secondary terminals are loaded with the grounded terminal burden.

The Capacitor Voltage transformers shall be provided with the following accessories.

- Terminal connectors suitable for ACSR Drake conductor.

- Two	earthing	terminals	on	tanks	on	opposite	sides	for connecting the

Engineer’s earthing conductors.

- Oil level gauge.

- Filling and draining plugs.

- Power factor testing terminal

- Facility for lifting bushings and tank.

The quantity of insulating oil required for first filling. Di electric dissipation factor of the oil shall not exceed 0.005. Insulating oil shall comply with applicable standards.Rating and

diagram plate as per relevant standards. Pressure relieving device.Hot dip galvanized steel Support Structures.

CVTs shall be given tropicalised treatment for satisfactory operation in hot and humid condition.CVTs shall be suitably braced to withstand stresses induced due to seismic forces of zone – II of relevant IS. The temperature rise of CVTs shall not exceed the figures given in applicable standards for operation under ambient temperature conditions.The tanks/bases and all exposed ferrous parts of the CVTs shall be hot dip galvanized and painted confirming to applicable standards.

INSULATORS/BUSHINGS :

Insulators / bushings shall conform to applicable standards and shall be made of homogeneous vitreous porcelain, the glazing of which shall be of uniform brown or dark brown in colour.

Oil filled insulators/bushings shall be hermetically sealed to prevent ingress of moisture. A cushion of Nitrogen gas or Metallic bellows shall be used for cushioning and to allow for oil expansion.

TESTS AND CONDITIONS FOR DISPATCH :

Following routine tests shall be carried out on the Capacitor voltage transformers in the presence of the Engineer ’s representative as per the latest edition of IS 3156( Part I to IV)

- Verification of terminal markings and polarity.

- Power	frequency	voltage with	stand	test	on	primary windings.

- Power frequency voltage with stand test on secondary windings.

- Determination of errors according to the requirements of the appropriate accuracy class.

- Partial discharge test.

Note: Apart from the above, if any other tests are required to be carried as per IS:3156, the same shall be carried out.

A copy of the type test certificate for the following type tests carried out on one of the Capacitor Voltage Transformers shall be furnished for Engineer ’s reference.

- High voltage power frequency withstand test on primary windings.

- High voltage power frequency withstand test on secondary windings.

- Determination of errors according to the requirements of the appropriate accuracy class.

- Impulse voltage with stand test on Voltage transformers for service in electrically exposed installation.

- Temperature rise test.

- All the routine tests shall be carried out after conducting di electric tests.

A copy of the type test certificate for the following type tests carried out on one of the bushings/hallow porcelain insulator as per the relevant IS, shall be furnished for Engineer ’s reference.

- Visual examination.

- One minute power frequency dry withstand test. c)   Oil tightness test.

- Partial discharge test.

- Test for capacitance and power factor measurement.

The Routine test certificates shall be furnished in 6 sets for Engineer’s approval and conveying dispatch instructions. No equipment shall be dispatched before the approval of test certificates and dispatch instructions conveyed by the Engineer.

TERMINAL BLOCKS :

The materials used for the Secondary terminal blocks shall possess excellent mechanical and electrical properties. The terminal blocks shall be rigid and shall withstand handling while making repeated terminations. The terminal blocks shall be of stud type (Bolt and nut type). Each unit shall be complete with copper terminal studs, nuts and washers together with label carriers, with blank label strips and suitable cable lugs. The terminal block shall be mounted on galvanized rolled steel strip of sufficient length and size which acts as a support bar for fixing on hylem sheet of 10 mm thick brass studs. Each terminal block shall be suitably numbered.

The terminal studs, nuts, washers and links shall be made of best quality copper and shall be suitable for copper conductor of size 16 sq. mm.

All terminal blocks shall be designed for voltage rating of 750/1100 volts and continuous current rating of 25 A, AC or DC.

The terminals shall be of good mechanical construction providing adequate electrical contact for the appropriate size of the copper cable used. Terminal connectors shall be such that the conductors may be connected by screw or other equivalent means to maintain the necessary contact pressure permanently.

Terminals shall not run or be displaced when the connecting screws are tightened and the conductor shall not become displaced out impairing the normal performance of the unit. No contact

pressure shall be transmitted through insulating material and the gripping of the conductor shall take place between metal faces.

EARTHING TERMINAL :

Two numbers of 12 mm diameter brass bolts and nuts with spring washers for each box shall be provided by the side of the body of the marshalling box for fixing copper /GI 25X 3 mm flat. The earthing terminal shall be identified by means of the sign marked, in a legible and indelible manner on or adjacent to the terminal. The terminals shall	be	provided	inside the marshalling box for connection of earthing leads. Earthing terminal shall have provision for terminating the earthing leads from neutral connection at the inside of the box.

  - LIGHTNING ARRESTERS:

CONSTRUCTION FEATURES:

Lightning arresters shall be gapless metal oxide hermetically sealed type, of self supporting construction and base mounted suitable for mounting on steel structures.They shall have adequate thermal discharge capacity for various types of surges.The lightning arresters shall be capable of withstanding the internal pressures developed during discharges without operation of the pressure relief devices or should safely vent the internal pressures associated with arrester failure without shattering.

Insulator housing shall be of porcelain having adequate mechanical strength and rigidity. Arrester housing shall withstand short circuit, wind, seismic and other forces during operation.

Arresters shall incorporate anti-contamination features to prevent arrester failure consequent to uneven voltage gradient across the stack in the event of contamination of the porcelain. The arrester shall be protected against the ingress of moisture.

Surge counter should be furnished with the insulating bases for connection. No radio interference shall be caused by the arresters operating at the normal rated voltages.

FITTINGS AND ACCESSSORIES:

Arresters shall be complete with insulating base and discharge counter and provision for bolting to the supporting structure (pedestal).

Self contained discharge counter, suitably enclosed for outdoor use and requiring no external auxiliary supply shall be provided for each arrester. The discharge counter shall have a glass window. Suitably sized links of copper to facilitate bypassing of discharge counter shall be provided.The terminal connectors shall have provision for connection of these links.

The conductor provided between lightning arrester earth terminal to the discharge counter terminal shall be insulated for a minimum of 4 kV and this insulated conductor of 1.5 m length shall be

supplied along with the arrester.It shall not require sealing ends or plumbed joints at either ends for terminations.

A leakage current detector as an integral part of the discharge counter shall be supplied. The value of leakage current beyond which the operation is abnormal shall be clearly marked in red colour on the detector.

Grading rings shall be provided on each arrester unit for proper stress distribution as dictated by the voltage class of the arrester.

Arresters shall be supplied with clamps/connectors on line terminal suitable for ACSR Drake conductor with earth terminal and the discharge counter terminals along with Galvanized steel support structure with bolts, nuts etc., including foundation requirements.

Supporting Structure

Supporting structure for the lightning arrestor shall be of galvanised steel and shall be included in the Contractor’s Scope of Supply. Contractor shall furnish detailed dimensioned drawings indicating weights and all fixing details.

  - ISOLATOR:

CONSTRUCTION FEATURES:

The Isolator shall be three pole, horizontally mounted, center pole rotating, motor operated. The isolator shall be complete with mechanisms and mounting poles. All switch bases, operating mechanisms, rods, and other steel parts shall be hot dip galvanised.

Isolator and earth switch shall be equipped with all necessary linkages, clamps, couplings, operating pipes and handle supporting brackets, guide blades, auxiliary switches, earth copper flexible braids and other miscellaneous items required to make complete installation. All operating rods and levers shall be cut to length and all machining operations and threading shall be completed in the factory. Earth switches shall be operable only in position and should have protection interlocks.

The isolator and the earth switches shall be mechanically designed to safely withstand the effects of temperature, wind load, tensile forces and movement of connections, as well as short circuit forces. The isolator blades shall be of high conductivity EC grade of 99.9% purity and all conducting parts shall be of high conductivity Electrolytic grade copper or aluminium alloy. Bolts, screws and pins shall be provided with lock washers, keys or equivalent locking facilities. All bearings shall be such that no lubrication or maintenance is required.During the course of normal operation, it is likely that the isolator may be left in the open / closed position for long periods	of	time.	They

shall be designedto operate satisfactorily even after being kept in one position for longer period.

All bearings shall be double ball bearings for smooth operation.The isolator shall be capable of breaking the magnetizing current of associated power transformer.

The temperature rise of any part of the isolator and the associated equipment	shall

not exceedthe maximum permissible	temperature	rise values	as stipulated in the relevant standards.

CONTACTS:

The main blades of all switches shall have adequate strength and current carrying capacity conforming to the maximum rating. The switch blade shall be so assembled that no part of the blade can move relative to the other. The current path shall not be through any springs or movable part connection. The contact shall be designed to be adjustable, self aligning high pressure providing, self-cleaning action with turn and twist mechanism. All contact surfaces shall be silver faced copper.

EARTH SWITCH :

Earth switch shall be provided wherever necessary and shall form an integral part of each pole of the isolator. The earth switches shall be three pole and shall be manually group operated, mechanically interlocked with the connected isolator so that it is possible to close and open the earth switch only when the connected isolator is in the open position. A flexible tinned copper earthing braid of suitable size shall be provided from each earthing blade and shall be suitably attached to the earthing connector for common wire connection. The earth switch shall be designed to withstand electrodynamics stress due to currents upto 50 KA (peak) as per IEC recommendations.

INSULATORS:

The insulators shall be porcelain Solid core type. The porcelain used for manufacture of insulators shall be homogeneous, free from flaws or imperfections that might affect the mechanical or dielectric quality. They shall be thoroughly vitrified, tough and impervious to moisture., The glazing of the porcelain shall be of uniform brown colour, free from blisters, burns and other defects.

The insulators shall have creepage distance to suit normally polluted atmosphere. The porcelain and metal parts shall be assembled in such a manner that any thermal expansion differences between the metal and the porcelain parts throughout the range of temperature variation shall not loosen the parts or create undue internal stresses which may affect the electrical or mechanical strength and rigidity. Each cap and base shall be of high-grade cast steel or malleable steel casting and they shall be machine faced smoothly and galvanized.

OPERATING SYSTEM :

All isolators shall be of motor operated type. The switch operating mechanism shall be so designed that it will not cause excessive deflection to the member to which it is attached. All switches shall be self-locking in the open and closed positions independent of the control shaft restraint. Each mechanism shall be provided with an indicator showing direction of rotation for opening / closing. The gears shall be of Aluminum bronze and lubricated for life.

The operating mechanism shall provide a quick, simple and effective operation with double tandem type arrangement. Time of operation shall not exceed 12 seconds. One man shall be able to operate the isolator/ earthing switch without undue effort.

The operating mechanism shall be provided with sufficient adjustment to allow for final alignment of the isolator blades for simultaneous operation.

The manual operating handle shall be mounted inside a box. Guide bearings shall be provided if necessary at a height of 750 mm above ground level. All bearings shall be weather protected by

means of covers and grease retainers. Bearing pressure shall be kept low to ensure long life and ease of operation.

The operating mechanism design shall be such that during the operation of the isolator, once the moving blades reach the sparking distance, springs shall take over to give a quick, snap actionclosing so that the isolator closing is independent of manual efforts.

The operating mechanism shall be mounted such that the operating handle is about 1000 mm above ground level.

INTERLOCK:

A mechanized key interlock shall be incorporated for interlocking with associated circuit breaker. The key shall be released only when the isolator is fully closed or fully opened.

FITTINGS AND ACCESSORIES:

Position Indicator: A mechanical position indicating device shall be provided for each isolator/earthing switch provision for remote position indicator shall also be provided.

Terminal pads & connectors: Each isolator shall be provided with suitable terminal pads and terminal connector suitable for ACSR conductor selected for interconnection in the bay.

Earthing pads: Each pole of the isolator shall be provided

with two earthing pads of non corrosive materials at opposite end, brazed to the base. Flexible tinned copper braid of suitable size shall be provided for connecting operating handles of isolators and earthing switches to the earthing system.

Auxiliary switches: Each isolator switch shall be provided with a mechanically driven auxiliary switch with all necessary contacts for control, indication and interlocking purposes and with (8 NO,8NC) spare contacts. All contacts shall be rated for 10 amps. continuous rating of 110 ± 10% Volts D.C.

Name plate: A weather proof and corrosion proof name plate shall  be provided on isolator,marked  with information as per relevant standards .

Supporting structures: Supporting structures for isolator and earthing switch to be supplied shall be of galvanised steel.The vertical clearance from live conductor to the ground shall be maintained at least 5500 mm. Necessary foundation bolts shall be supplied along with the structures.

PAINTING :

The operating housing mechanism, control cubicles shall be painted both inside and outside with two coats of red oxide paint and one coat of French grey paint in the inside and one coat of light grey paint on the outside surface as per relevant standards.

  - CAPACITOR CUBICLES:

Applicable Standards

The capacitor banks and panel shall conform to the latest applicable standards specified below.

- Metal enclosed switchgear : IS:3427/BSEN:60298/IEC:60298

- Current transformers : IS:2705/BS:7626

- Arrangement for switchgear busbars, : IS:5578/IS:11353

- main connections and auxiliary wiring

- Busbar support insulators : IS:2544/BS:3297/IEC:60273

- Degree of protection : IS:13947 – Part (I)/IEC:60947-1

- High voltage fuses : IS:9385/BS:2692/IEC:60282

- Specification for copper rods: IS:613

- Code of practice for phosphating : IS:6005/BS:3189

- Load break switches : IS:9920, IEC:129, 265, 298

- Shunt capacitors for power systems : IS:2834

- Series reactor : IS:5553

- Internal fuses and internal overpressure : IS:12672

- Porcelain post insulators : IS:2544

Each motor shall be provided with the bank of capacitors to improve the power factor of motors to 0.95. However, care shall be taken that KVAR of capacitor shall not exceed magnetizing KVAR of the motor, in that case the corrected power factor may be less than 0.95, the capacitors shall be provided in separate expanded metal housing with top completely covered with MS sheets. The capacitors shall be mounted on rigid framed structure. The bushings required for supporting interconnection of capacitors and HRC fuses shall be as per IS 2834 but shall also meet the requirement as per BSS 1950 of 1965 wherever these are applicable.

Each capacitors cubicle will comprise of following.

- Bank of capacitors of suitable KVAR rating for each motor to improve the P.F. of motor to 0.95.

- HRC fuses suitable for operating voltage

- Earthing terminals

- Switching device to isolate individual bank of capacitors.

Design Features

- The panel shall be indoor, metal clad with separate metal enclosed compartments for

  - 11 kV capacitor banks

  - Load break switch with fuse

  - busbars

  - core balance current transformers and

  - power cable terminations.

- Separate removable gland plates shall be provided for power and control cables. The gland plate for the power cables shall be of non-magnetic material.

- All sheet steel work shall be thoroughly cleaned of rust, scale, oil, grease, dirt and swarf by pickling, emulsion cleaning etc. The sheet steel shall be phosphated and then painted with two coats of zinc rich primer paint. After application of the primer, two coats of finishing synthetic enamel paint oven baked/stoved, shall be applied.

- The cable compartment shall house all power cable connections along with associated cable terminations. Zero sequence current transformers provided for earth fault protection shall be located inside the cable compartment.

- Each cubicle shall be fitted with a label in the front and rear of the cubicle. Each capacitor bank, switch, fuse and other devices shall be provided with separate labels, indicating designation rating and duty.

- The capacitor bank shall be complete with accessories and shall be metal enclosed, indoor floor mounting and free standing type.

- The capacitor bank may comprise of suitable number of single phase units in series parallel combination. However, the series parallel combination of capacitor units shall be such as not to exceed the permissible overvoltage across the healthy capacitor units in case of failure of one or more units.

- The assembly of the banks shall be such that it provides sufficient ventilation for each unit. Necessary louvers may be provided in the cubicle to ensure proper ventilation.

- Each capacitor unit/bank shall be fitted with directly connected continuously rated, low loss discharge device to discharge the capacitors and reduce the voltage to less than 50 volts within five minutes.

- The capacitor banks shall be suitable for continuous operation at 110% of rated rms voltage.

- The capacitor bank shall be suitable for continuous operation at 150% of rated rms current.

- Bushings shall be of porcelain and shall be joined to case by soldering/welding or other method which ensures an adequate and permanent seal.

- Each unit active parts shall be non-inflammable dielectric immersed in suitable impregnant, self- cooled, and hermetically sealed. The impregnant shall be non-PCB (Poly chlorinated Biphenyl) oil.

- Each capacitor unit shall be individually protected by an HRC fuse suitably rated for load current and interrupting capacity, so that a faulty capacitor unit shall be disconnected by the fuse without causing

the bank to be disconnected. Thus, the fuse shall disconnect only the faulty unit and shall leave the rest of the units undisturbed. An operated fuse shall give visual indication so that it may be detected during periodic inspection. The fuse breaking time shall coordinate with the pressure built up within the unit to avoid explosion.

- Mounting of the individual fuse may be internal or external to the capacitor case.

- The switching and protective devices and the connections shall have a capacity corresponding to 1.5 times the rated current of the capacitor bank.

Main Busbars

- Busbars shall be fully insulated by encapsulation in epoxy resin, with moulded capsprotecting all joints.

- Busbars shall be supported on insulators capable of withstanding dynamic stresses due to short circuit.

- Busbars shall be of copper conductor of hard drawn (HD) and high conductivity.Disconnection Switches

- Disconnect switches shall be load break, type. Push button with indicating lamps shall be provided for the opening of the load break switch.

Earthing

- An earthing bus shall be provided at the bottom and extended throughout the length of the cubicle. It shall be bolted/welded to the frame work.

- All non-current carrying metal work of the cubicle shall be effectively bonded to the earth bus. Hinged doors shall be earthed through flexible earthing braid.

Panel Accessories and Wiring

- Panel shall be supplied completely wired internally upto equipment and terminalblocks and ready for the external cable connections at the terminal blocks.

- All auxiliary wiring shall be carried out with 650 volts grade, single core, strandedcopper conductor with PVC insulation. The sizes of wire shall be not less than 1.5mm2.

- Terminal blocks shall be of stud type, 650 volts grade 10 amps, rated complete withinsulated barriers. Terminal blocks for CTs shall be provided with test links andisolating facilities.

- All spare contacts and terminals of cubicle mounted equipment and devices shall bewired to terminal blocks.

- Push buttons shall be provided wherever specified. They shall be provided withinscription plates engraved with their functions.

- Indicating lamps shall be panel mounting type with series resistors. The wattage oflamps shall be 5 to 10 watts.

- Each panel shall be provided with 240 volts, 1 phase, 50 Hz, 5 amps, 3 pin receptacle with switch located in a convenient position.

- An interior illuminating lamp together with operating door switch and protective fuse shall be provided.

Cable Termination

- Necessary number of cable glands shall be supplied for terminating auxiliary power and control cables.Glands shall be of heavy duty brass castings, machine finished and complete with check nut, washers, neoprene compression ring etc.

- Cable lugs for all power and control cable connections shall be supplied. The lugs shall be tinned copper/aluminium depending on cable conductor and of solderless crimping type

- All necessary materials required for terminating the power cables such as tapes,fillers, binding wires, armour clamps, brass glands etc. shall be supplied.

The tenderer should ensure that power factor of the system does not fall below 0.95 lag during off load and/or monsoon period.

The Tenderer should make necessary arrangements for connecting the required capacity KVAR capacitors bank in the circuit with load break switches, fuse units etc., during off load and/or monsoon period.

The capacitors shall be provided with earth terminals. The earth fault relay is included under HT Panel. The one no of CBCT to detect the earth fault required for each fault relay shall be provided.

EMERGENCY STOP SWITCHES:

Emergency stop switches near the capacitors should be provided for switching off the unit in case of emergency.

Number of capacitor cubicles may have separate A.C.B / Vacuum contact breaker, which connect them in line circuit.

Note:	These capacitors can be put ‘ON’ especially when there will be low power factor of the system,

in rainy season or when the motor will be idle.

Capacitors shall be protected against over current by means of suitable Breakers with adjustable over current relays, which are adjusted to interrupt the circuit. When the current exceeds the permissible limits specified in 5.3 of IS 2834-1964.

Suitable discharge device may be provided across the second axis of the current transformers used for over current protection to afford necessary protection against transient over voltage during switching. Suitable discharge device shall be provided to discharge the capacitors.

The protection against internal fault of a capacitor bank should be provided by suitable means to isolate automatically a faulty unit.

L.T. CAPACITOR CUBICLE:

These capacitors will be suitable for operation on 440 V three phase AC and to improve power factor of Butterfly Valve actuator motor, Booster pump motors to 0.95 and other L.T. Auxiliary loads e.g. lighting,Air-conditioning, Ventilation, Sump Pump, Vacuum Pumps etc.

These capacitors should be provided with HRC switch fuse unit for each bank.These will be mounted near L.T. Panel.Every capacitor should have discharging resistance to reduce the voltage to 50 V within 60 seconds when capacitor is taken out of circuit.Capacitor winding shall be free from oxidation and protected from humidity.Capacitors should have minimum dielectric loss, self heating property and should not short between the phases throughout its life. It should have negligible temperature rise for better performance with longer life.

TESTING:

The Capacitor will be tested in manufacturer’s works as per IS 2834-1964 in presence of the Engineer or his representative.

  - SWITCH GEAR PANEL

Main panel shall be of sheet steel dust and vermin proof indoor floor mounting type panel with Bus Bars suitable for the motor voltage completely assembled, wired, tested and painted with rustproof paint confirming to relevant IS. The panel shall comprise of following incoming breakers. The degree of protection should be IP-42 as per IS.

INCOMING BREAKER SHALL CONSIST OF FOLLOWING:

- Vacuum circuit breaker, draw out type suitable for the required, voltage three phase, 50 Hz. AC with motor charged spring closing mechanism and facility for remoter operation. Surge suppression arrangement iv VCB is essential.

- Three nos. double core current transformers of ratio rated cap/1.1A. one core for metering class 1 accuracy 30 VA burden and the other core for protection Class 5 P-10 15 VA burden.

- Three numbers single core current transformers of rated CAP/1 amps / Class-p 5 accuracy with suitable knee point voltage to be used for differential protection of transformers. The requirement of knee point voltage shall be subject to prior approval.

- Three numbers single phase potential transformers to be star/Star connected with ratio rated voltage/ 1.7321 (110 V/1. 7321) Class-I accuracy and rated burden 150 V.A.

- Trip neutral, close, circuit breaker control switch.

- Indication lamps, red/ green / amber for circuit breaker ‘ON / OFF / auto trip indication rated for 110

volts DC.

- White indication lamp for trip circuit healthy indication suitable for 110 volts DC.

- 96 sq. mm ammeter of suitable scale with 3 way and ON/OFF selector switch.

- 96 sq. mm voltmeter of suitable scale with 3 way and ON/OFF selector switch.

- High speed tripping relay.

- Static type pole inverse definite minimum time lag (IDMTL) relay with two element one for over current protection having setting range 50 to 200% on IDMTL unit and other element for earth fault protection with setting range 20 to 80% on IDMTL unit with common instantaneous setting range of 500 to 2000%.

- Cable termination arrangement with cable end box suitable for terminating XLPE cable coming from transformer.

- DC fail relay.

- Auxiliary relays, AC and DC fuses etc., as required.

- Remote / Local selector switch with locking arrangement.

- (MWH) Mega Watt Hour meter suitable for 3 phase, 3 wire unbalanced load.

- (RKVAH) Reactive Kilo Volt Ampere Hours suitable for 3 phase, 3 wire Maddened load.

- Power factor meter showing the power factor of system (0.50 Lag to 0.50 Lead).

- Time delay relay.

- Single pole instantaneous under voltage relay.

- Frequency indicator having range of 45 Hz to 60 Hz.

- Counter showing no. of trappings made by breaker.

- Phase sequence indicators.

OUTGOING FEEDERS FOR MOTORS:

Each feeder to have the following:

- Breaker- draw out type suitable for installation with suitable rupturing capacity.

- 3 nos. double core current transformers of suitable rating on primary side and 1/1 amp. On secondary side, one core for metering Class-1 accuracy 20 V.A burden, one core for protection Class-5 P 10 accuracy with 15 VA burden.

- 3 Nos. single phase PT with ratio (system voltage/1, 7321) / ((110 V/1, 7321) Class-I accuracy and 150 VA burden.

- Motor protection relays of numerical type shall be provided

- Under voltage relay with time lag arrangement.

- Trip, neutral, close, circuit breaker control switch.

- Indicating lamps Red / green / Amber for circuit breaker On / Off / Auto Trip indication rated 110 volts DC.

- Indicating lamp for trip circuit healthy indication suitable for 110 Volts D.C.

- Indication for valve actuator motor operation for following position-

- Valve fully open

- Valve partially open

- Valve fully closed.

Indication and annunciation for following.

- Low water level in sump

- High water level in sump

- Capacitor earth fault.

- 96 sq.mm Ammeter shall be with suitable scale with 3 way ON/OFF selector switch.

- High speed tripping relay.

- Protection relays with flange for following.

- Comprehensive motor protection relay (relay subject to approval by Dept.) having following protection.

- Thermal overload

- Instantaneous earth fault

- Instantaneous unbalance

- Stalling protection

In addition to above following relays for fault shall be provided –

- Earth fault relays for capacitor earth fault.

- High/Low water level in sump with sensing element.

- Disconnecting links for disconnection of cable of capacitors.

- Cable termination arrangement with cable end box suitable for terminating cables as per cable Schedule (for motor and for capacitor)

- Remote/ local, selector switch with locking arrangement.

- Remote switch gear panel/local selector switch with locking arrangement for valve motors.

- Auxiliary relays, terminals, AC and DC fuses etc., as required.

- Time delay relay.

- Forced water lubrication pump start/stop switches with indication lamps.

- Hour meter one for each motor panel and square panel operating on 230/110 V AC/D.C. supply.

- Butter fly valve operation switches OPEN/CLOSE with indication lamps indicting valve positions of fully open/ Fully close / Partly open / Operating.

Outgoing feeder for connection Aux. Transformer comprising of following.

- Air circuit breaker / Vacuum circuit breaker draw out type / Load break switch with shunt tripping arrangement suitable for installation with a minimum rupturing capacity.

- Three sets of single core C.Ts of suitable rating on primary side and I AMP on secondary side for metering Class-I accuracy and 20 VA burden.

- Three sets of single core C.Ts. of suitable rating on primary side and I AMP on secondary side for protection Class-5, P-10 accuracy and 15 V.A burden.

- Trip, neutral, close, circuit breaker control switch.

- Indication lamps Red / Green / Amber for circuit breaker On / Off / Auto trip indication rate for 110 volts DC.

- One indication lamp for trip circuit healthy indication suitable for 110 volts DC. Indication for following:

- Buchholtz relay operated

- Over current earth relay operated.

- 96 sq. mm Ammeter having suitable scale with 3 way and ON/OFF selector switch.

- High speed tripping relay for IDMT and buchholtz.

- Static type triple pole IDMT relay with two elements one for over current protection having setting range 50 to 200% in IDMTL unit and one element for earth fault protection with setting range 20 to 80% on IDMTL unit with common instantaneous setting ranges of 500 to 2000%.

- Cable termination arrangement with cable end box suitable for terminating cable as mentioned in cable scheduled.

- Auxiliary relays, terminals, AC and DC fuses etc., as required.

- Remote/ Local control switch.

ANNUNCIATION:

1 No. buzzer suitable for operation on 110 volts DC. 1 No. Bellsuitable for operation on 230 volts AC

Note: The bell and Buzzer will operate in parallel with corresponding Annunciation of Remote Control panel.

SWITCHGEAR PANELS WHEN LV MOTORS [400 V] ARE USED –

For pumping stations where 400 V motors are to be used, the switchgear panels shall consist of the following –

- Incomer feeder with ACB / MCCB as required in the designs.

- Outgoing feeders for the motors with thyristor based soft starters.

- Outgoing feeders for Capacitor banks.

- Outgoing feeders for the various station loads

The description of panels and other components shall be generally as per the HT panels and is subject to approval of the Engineer.

AIR CIRCUIT BREAKERS / VACCUM CIRCUIT BREAKERS:

Each Breaker shall have following accessories:

- Operation counter to register number of Breakers operations.

- Mechanical operating device for manual closing and tripping of breaker.

- Device for manual charging of closing spring.

- Mechanically operated Red 'Trip' shrouded push button.

There should be locking facility in SERVICE, TEST and ISOLATED position. In TEST position, the Breaker / ACB will be tested without energizing the power circuit. It should not be possible to plug in a closed Breaker or to draw out a Breaker / ACB in closed position. It should not be possible to operate Breaker / ACB unless it is fully plugged IN, TEST or fully isolated position. Through the Breakers are to be suitable for electrical operation, provision of manual charging, closing and tripping shall be made. All Breaker / ACB of identical current ratings shall be interchangeable. Charging motor and closing coil shall operate between 85 to 110 percent of 110 volts DC supply and trip coil between 70 to 110 percent of 110 volts DC supply. Suitable thermal protection shall be provided for charging motor.

BUS BARS AND SUPPORTS:

Bus Bars shall be of Electrolytic Aluminum/copper and of ample size. It shall be adequately supported on non-hygroscopes, non-combustible, fibber glass reinforced, plastic insulator. The Bus Bars up to incoming of Breakers and also up to the outgoing terminals, including all joints, shall be fully insulated

with heart shrinkable PVC sleeves. They shall be uniform and continues throughout the length of Switch Board. The Bus Bars shall be extendable on both sides.

CONTROL WIRING:

All control wiring shall be of adequate capacity and all outgoing circuits shall be wired upto terminal blocks for external connections. Wires shall be properly colour coded and ferruled to distinguish different circuits. They shall be neatly routed through PVC channels of adequate size. All control wiring shall be carried out with 1.1 KV, grade, 2.5 sq. mm. PVC insulated wires.

PANELS:

The panel shall be indoor, free standing type, fully compartmentalized and properly ventilated. It shall be totally enclosed, dust and vermin proof. It shall be possible to extend the assembly on either side. It shall be made out of at least 10 SWG sheet steel suitably reinforced to provide flat level surface, resistant to vibration and rigid during transportation and installation. Door and removable covers may be of 14 SWG sheet, Breaker compartment shall have front hinged door with lock and key.

Fixed main disconnect contact in panel housing shall be provided with automatic safety shutters, to cover the high voltage circuit. means shall be provided to operate shutters by a handle or knob, on the front of the panel.Shutter operating mechanism shall be inter locked with withdrawal truck, to prevent incorrect operation.All panel surfaces to be painted shall be first chemically treated to remove all rust, scale and then two coats of zinc primer shall be applied. The color of all panels shall be light gray to shade no. 631 of IS-5 with semi-glossy for the exterior and brilliant white synthetic enamel, for interior.

TESTS

The switch gear assembly and all other components, like circuit breakers, bus bars, C.T, P.T. shall be tested for all type and routine test, as per latest edition of relevant Indian standard/ international standards. In case, type test reports on similar equipment are available, engineer may waive these test. All routine tests as per relevant standard shall be conducted on the assembly on the various component. All the above testing shall be carried out for routine and functional test at manufactures works in presence of engineer or his representative.

CONTORL FROM BOTH SWITCHGEAR PANEL AND REMOTE CONTROL PANEL

It is necessary that pump operation with all other allied equipments should be possible both from HT panel as well as remote control panel. Necessary control switch and annunciation indications for operation of pump sets and allied equipment should invariably be provided on both the panels.

REMOTE CONTROL PANEL:

The panel shall be indoor, free standing type and properly ventilated. It shall be totally enclosed, dust and vermin proof. It shall be possible to extend the assembly on either side. It shall be made from at least 10 SWG sheet steel suitably reinforced to provide flat level surface, resistant to vibration and rigid during transportation and installation.The Remote control panel shall be located at a suitable place and the layout plan of all the panels shall be got approved by the Engineer.It shall be possible to operate the incoming breakers located at the switch yard and perform all the operations for starting of the pumping units.Remote control panels shall be tested for routine and type functional tests at Manufacturer’s works, in the presence of Engineer

FCMA Neutral Soft Start Panel

- Flux Compensated Magnetic Amplifier (FCMA) neutral soft start panel shall be indoor, metal clad with separate metal enclosed compartments for

  - control, metering and current transformers for differential protection

  - shorting switch

  - busbars

  - power cable terminations

  - push buttons with indicating lamps.

- FCMA shall achieve smooth starting by torque control for gradual acceleration of the drive system thus preventing jerks and extending the life of equipment.

- Starting current shall be limited to 3.0 times the full load current of the motor.

- Separate removable gland plates shall be provided for power and control cables. The gland plate for the power cables shall be of non-magnetic material.

- All sheet steel work shall be thoroughly cleaned of rust, scale, oil, grease, dirt and swarf by pickling, emulsion cleaning etc. The sheet steel shall be phosphated and then painted with two coats of zinc rich primer plant. After application of the primer, two coats of finishing synthetic enamel paint oven baked/stoved, shall be applied.

- The cable compartment shall house all power cable connections along with associated cable terminations.

- Each cubicle shall be fitted with a label in the front and rear of the cubicle, indicating the panel designation, rating and duty. Each relay, instrument, switch, fuse and other devices shall be

provided with separate labels.

- Caution name plate with inscription “Caution - Live Terminals” shall be provided at all points where the terminals are likely to remain live and isolation is possible only at remote end, e.g. incoming terminals of main disconnecting switch.

- Starting of motor shall be from either FCMA panel located near to motor or shall be from 6.6 kV motor module or from PLC. Necessary wiring diagram shall be provided considering starting interlock, trip circuit, starting and running mode signal.

- Suitable breaker shall be used for shorting the reactors.

Main Busbars

- Busbars shall be fully insulated by encapsulation in epoxy resin, with moulded caps protecting all joints.

- Busbars shall be supported on insulators capable of withstanding dynamic stresses due to short circuit.

- Busbars shall be of copper conductor of hand drawn (HD) and high conductivity. Busbars shall be fully insulated by encapsulation in epoxy resin with moulded caps protecting all joints.

Earthing

  - An earthing bus shall be provided at the bottom and extended throughout the length of the panel. It shall be bolted/welded to the frame work.

  - All noncurrent carrying metal work of the panel shall be effectively bonded to the earth bus. Hinged doors shall be earthed through flexible earthing braid.

TEMPERATURE SCANNER

1 No. of temperature scanner to be provided i.e. one for each HT motor and one stand byTemperature scanner panel shall be made of sheet steel, floor mounted consisting of temperature scanner as detailed below. The panel shall be duly wired painted and complete in all respect.10 points microprocessor based Temperature scanner to monitor motor winding and bearing temperature as well as the temperature of thrust bearing of pumps. The scanner shall be suitable for working with 3 wire system potential transformer (PT) 100 RTDs for a range of 00 C to 2000 C with indicating accuracy of 0.25% full scale +10 C and resolution of 0.10 C. The scanner shall be suitable for operation at for the availablepower supply and shall have one common relay for alarm. The unit shall be complete with

necessary cabling lugs etc. for interconnection between the terminal blocks and scanner terminals within the panel.

The instruction shall be suitable for programming data for each channel with the help of key board. Scanning speed shall be variable from one second onwards. The channel NO. and data shall be indicated on the seven segment Light Emission Diode (LED) display. The individual LEDs shall indicate the status of high or low alarm and control relay status and sensor. A lock shall be provided so that the program cannot be tempered with. Control relay shall be given for each channel which will operate depending on the control levels as per the program.

TESTING

The switch gear panel shall be tested for routine and type functional tests at manufacturer’s works in

presence of the engineer or his representative. Type test certificates shall be furnished.

- L.T. DISTRIBUTION PANEL: STANDARDS

| No. | Standard | Description |
| --- | --- | --- |
| 1. | IS 3247 | Switch gear general requirement |
| 2. | IS 2516 | Circuit breaker |
| 3. | IS 8623 | Factory built assemblies of Sw, Gr & Cont. Gr. (for voltages <650 V) |
| 4. | IS 2147 | Degree of protection of enclosure of LV switchgear and control gear. |
| 5. | IS 1248 | Electrical Indicating Instruments |
| 6. | IS 722 | Integrating AC electric meters |
| 7. | IS 2705 | Current Transformers |
| 8. | IS 3156 | Voltage Transformers |
| 9. | IS 10118 | Installation and maintenance of switch gear |
| 10. | IS 3231 | Electric Relays |
| 11. | IS 8686 | Specification for static relays |
| 12. | IS 5082 | LT aluminum and alloy bars, tubes, and rods for Electrical purpose. |
| 1. | IS 9431 | Indoor post insulators organic material |
| 2. | IS 5621 | Insulators |
| 3. | IS 11353 | Guide for uniform system of marking terminals |
| 4. | IS 2544 | Porcelain post insulators |
| 5. | IS375 | Marking and arrangement for switch gear bus bar main connectors and auxiliary wiring |

TECHNICAL PARAMETERS

1.	TPN bus bar details	:

High Conductivity A1 grade E91E for TPN bare bus bar, size shall be suitable for current rating as per requirement

- Min. Clearance	:	Phase to phase – 25 m and Phase to earth 20 m

- Earth Bus	:	50 x 6 GI strip

- Power freq. Withstand	:	2.5 KV RMSI 50 Hz for one minute

- Short Time	:	50 KA (rms) for 1 second

- Max. temp, of bus bar	:	70° C

7.	CT details	:

Cast resin bar primary type, 1 A CT, CT ratio burden and class as per SLD

MCCB details	:

Rating shall be as per requirement with static release, U/V and current limiting feature

9.	Selector switch details	:

AS for Ammeter with R, Y, B, OFF position VS for Voltmeter with RY, YB, BR, OFF positions

Moving iron type, 90° scale, for AM & VM. AM dial range to

10. Indicating Meter details	:

suit CT primary current VM dial range to suit PT primary voltage

Size 96 mm2 for outgoing feeder Accuracy Class 1.10 for other details refer drawings

11. Integrating Meter details	:

Train gear type, calibrated for required CT, PT ratio Accuracy Class 1.0 for other details refer drawings.

- Push button details	:	Momentary type, 2 NO & 2 NC contracts of 10A at 240V AC.

- Indicating lamp details	:	7 watts filament type with series resistance

select rating.

Control fuse details	:	HRC cartridge type with base and carrier. Contractor to

- Miscellaneous details	:

Control wiring shall be with standard copper conductor, PVC

insulated, 650 V grade wires of’2.5 mm2 for CT circuits and

1.5 mm2 for other circuits.

Control terminals shall be of 10A, 1100 V grade clip on type with din rail mounting.

CT terminal shall be provided with shorting link and earthing facility.

BRIEF DESCRIPTION OF PANELS

One sheet steel totally enclosed dust and vermin proof L.T. panel board suitable for indoor floor mounting with requisite capacity aluminum bus bar and neutral of half the rating for operation on 433 V. 3 phase, 50 Hz. A.C. System completely assembled, wired, tested and painted with rust proof paint for controlling L.T. supply to different auxiliaries of pump house. Each panel shall consist of following items well installed and connected to suitable size of bus bars provided in the panel.

INCOMING FEEDER OF SUITABLE CAPACITY COMPRISING OF:

- Triple pole 415 volts suitably rated draw out type manually operated L.T air circuit breaker, provided with suitable thermal relay ranges along with shunt trip magnetic release and auxiliary contacts etc., each comprising of following items will be installed and connected to suitable size of bus bars provided in the panel.

- Circuit breaker control switch.

- Indication lamps, red/green/amber for “ON/OFF” and auto trip position indications

respectively.

- Current transformer having a ratio cap/1 A 15 VA Class-1 accuracy for metering.

- 3 current transformers having a ratio cap/1 A 10 VA Class-5 5P10 accuracy for protection.

- One 96 Sq.mm volt meter scale 0 to 600 volts

- 1 volt meter selector switch 3 way and “ON/OFF”

- One 96 sq.mm ammeter scale 0 to rated cap.

- One ammeter selector switch 3 way and “ON/OFF”

- One kWH meter suitable for 3 phase unbalanced load

- P.F. meter suitable for three phase unbalance load

- Suitable 415 volts, MCCB/MCB/T.P. switch fuse units with neutral link (one no. for EOT crane, one no. for work shop, two no. of DC charger, two no. of AC and one spare).

- Suitably rated 415 volts, MCCB/MCB/T.P. switch fuse units with neutral link (for butterfly valve and one no. spare)

- Suitably rated 415 volts, MCCB/MCB/T.P. switch fuse units with neutral link for lighting etc.,

- DOL type push button operated reversible starters for indivisible butterfly valve control through actuator with 2 No. (normally open) +2 NC (normally closed) auxiliary contacts.

Motor shall be connected on this panel duly wired through the suitable rated rating switch fuse unit mentioned as above.

- DOL type starters for exhaust fan with suitable rated switch fuse unit.

- Switch for local\ remote control operation should also be provided.

- All outgoing feeders shall be non-draw out type.

- Auxiliary relays, contacts terminals etc. as required.

- One static type triple pole inverse definite minimum time lag relay with two

elements, one for over current protection having setting range 50 to 200% on IDMTL unit and other one element for earth fault protection with setting range 20 to 80% IDMTL unit with common instantaneous setting range of 500 to 2000%

- One cable termination gland for adequate capacity cable.

PAINTING

- Pretreatment of all sheet steelwork, including de-greasing, rust/scale removal, phosphating and oven drying shall be carried out as per applicable standard.

- The phosphate coating shall be sealed by the application of two coats of ready mixed, stowing type zinc chromate primer. The first coat may be ‘flash dried’, while the second coat shall be stoved.

- After application of the primer, two coats of finishing synthetic, enamel paint shall be applied, each coat followed by stoving. The second finishing coat shall be applied after completion of tests. The colour of the finishing paint shall be shade 631 as per IS 5.

- The final finished thickness of paint film on steel shall be 100 microns.

- A small quantity of finishing paint shall be supplied for minor touching up required at site after the installation of the Panel.

TESTING

The L.T. panel switch board shall be tested for routine type and functional tests at manufacture’s works,

in the presence of the engineer or his representative.

| No. | Standard | Description |
| --- | --- | --- |
| 1) | IS 8320 | General requirements and methods of tests for lead acid storage batteries |
| 2) | IS 1651 | Stationary cells and batteries, lead acid type with tubular positive plates |

BATTERIES, BATTERY CHARGERS AND DC DISTRIBUTION PANEL STANDARDS

BATTERIES

The batteries to be supplied are to be rated against the estimated load currents as to be calculated by the Bidders as per IEEE & Battery manufacturers guideline. The supplier shall verify adequacies of capacities offered for the specified load currents and the necessary Battery Ampere Hour calculations shall be furnished by the tenderers along with the bid. The voltage rating of the battery shall be 110 V or 220 V and shall be subject to the approval of the Engineer.

CONSTRUCTIONAL FEATURES

- The batteries shall be flooded type conforming to the IS standards with latest amendments..

- Offered battery capacity shall be deleted for site conditions specified.

- The plant positive plates shall be cast solid in pure lead in one piece and shall have adequate mechanical strength. It shall be electrochemically formed and shall be capable of operating under normal operating conditions without buckling or cracking.

- The containers shall be made of hard rubber, glass, lead lined wood, plastics, or fiber reinforced plastics (FRP).

- The vent plug shall be of the anti splash type, preferably with more than one hole, and shall allow the gases to escape freely but shall effectively prevent acid particles or spray from coming out On removal, it shall permit drawing of the electrolyte samples, servicing and checking.

- Inter-cell and inter-tier connectors shall be of lead plated copper.

- Terminal posts shall be designed to accommodate external bolted connections conveniently and positively. Each terminal post shall have two bolt holes of the same diameter. The bottom hole shall be used to terminate the inter cell connection. All the metal parts of the terminals shall be of lead or lead coated type. Bolts, heads and nuts, except seal nuts, shall be hexagonal and shall be lead covered. The junction between terminal posts and cover, and between cover and container shall be properly sealed to prevent any seepage of electrolyte.

The electrolyte shall be battery grade sulphuric acid conforming to relevant standards. Required quantity of electrolyte for first filling with 10% extra shall be supplied in non-returnable containers.

ACCESSORIES

The battery sets shall be complete with accessories. Following minimum accessories shall be provided.

  - Battery racks

  - Porcelain insulators, rubber pads

  - Set of inter cell, inter-tier and interbank connectors as required for the complete installation.

  - Electrolyte for first filling +10% extra.

  - Accessories for testing and maintenance

One-	DC v6ltmeter with suitable leads for measuring cell voltage

One	Hydrometer for measuring specific gravity of electrolyte

One	thermometer

Three	Acid resisting funnels

Two	-	Acid resisting jugs adequate capacity.

Two	Rubber aprons

Two	Rubber gloves

Two	Cell lifting straps

One set Terminals and cable boxes with glands for connecting cable as required. 10% spare connectors, vent

plugs, nuts and bolts, set.

BATTERY RACKS

Battery racks shall be constructed from good quality teakwood and painted with two coats of approved acid resist ant paint. The racks shall be rigid, free-standing type and free from warp and twist.

VENTILATION

The battery shall operate satisfactorily over the entire range of temperature indicated.

MARKINGS

Each cell shall be marked with following in a permanent manner -

- Cell number

- Type of positive plate

- AH capacity at 10 hour rate

- Type of container

- Manufacturer’s name

- Month & year of manufacture.

BATTERY CHARGER

Battery charger suitable for the above battery shall be supplied. The charger shall be capable of delivering the float charging current, boost charging current and the load current and the rating shall be subject to the approval of the Engineer.

The charger shall be float-cum boost type. The charger in float mode shall supply float-charging current of battery. In boost mode the charger shall charge the fully discharged battery in 8 hours.

The charger shall be static type composed of silicon controlled rectifiers (SCRs) anddiodes connected in three phase full wave half controlled bridge circuit. The rectifier transformers for float and boost chargers shall be indoor dry type,

The charger shall have individually adjustable float I boost modes, over load and over voltage surge suppresser. On the power input side 3 Ph, 415 V, 63 A MCCB shall be provided. The battery shall be connected through a MCCB/MCB rated for battery short circuit current. The DC output voltage during float charging shall be stabilized within + 1% of the set DC bus voltage for the input AC voltage variation of + 10%l frequency variation of + 5% and DC load variation from 0-100%. The ripple content shall be within 3% of DC nominal output voltage.

Suitable dropper diodes shall be provided to ensure the correct voltage across the load during the charging process.

The setting of the output DC bus voltage shall be adjustable between + 10% of nominal rated voltage. The load-limiting feature of the float charger should be designed for short time over load to take care of testing of lamps.

All printed circuit boards shall be plug-in type, interlocked to prevent insertion in a wrong slot. Each card shall have LED indication on its front plate to indicate normal condition.

The boost charge voltage and current settings shall be adjustable between 70% to 100% of maximum boost charge voltage and between 30 to 100% of maximum boost charging current.

All components shall be clearly marked and all wiring colour-coded and tagged.

All power and control wiring shall be done with 1.1 kV grade stranded copper conductor and shall be adequately sized. Minimum size of control wiring shall be 1.5 mm2& power wiring 4 mm2. Ground terminals with isolating links shall be provided.

Following minimum protections shall be provided for the charger –

  - Charger goes into current limit mode if battery and or charger current exceed the set value.

  - Charger trips if Input u/v or DC o/v condition is sensed

  - Instantaneous DC current high is sensed. Following alarms/indications and meters shall be provided -

- 3 Ph, AC input supply ‘ON’

- DC ‘ON’ condition

- Charger ‘ON’

- Battery on load

- Battery under voltage

- Charger failure

- Battery CB open

- Any other necessary parameter for monitoring

- 72 X 72 mm, AC voltmeter and ammeter with selector switches.

- 72 X 72mm, DC voltmeter and ammeter with shunt

- An under-voltage relay shall be provided to isolate battery from load when the cell voltage drops below 50% of healthy cell voltage

DC DISTRIBUTION BOARD (DCDB)

Sheet steel cubicle for DC distribution board shall comprise of:

- Two incoming double pole miniature circuit breakers(MCB) of suitable rating.

- One change over switch for connection either to load bus or charge bus.

- One load bus, one charge bus and one common negative bus.

- Two MCBs/ breakers/ contactors suitable for connection with batteries to charge bus and load bus.

- Suitable outgoing feeders with MCB or switch fuse unit.

- Two 96 sq.mm 0-150 volt D.C. volt meter for indication of voltage from each charger.

- One hand reset over voltage relay, tripping the MCBs / beaker of charger connected	to load bus, in case voltage exceeds floating voltage.

- One under voltage relay with time relay in drop for alarm operating at 100 volts and transferring battery from charge bus to load bus

- Arrangements for mid-point earthing of battery with switch, a milli ammeter and high resistance.

- One earth fault relay (for alarm only) along with 0.5 sec. Time delay relay and setting range of 1 mA to 7 mA in steps of 1 mA

- One 96 sq.mm DC suitable rated for output load with shunt.

- Two indicating lamps for indication whether the load bus and charge bus are charged.

- A feeder with relay AC / DC contactor etc., for emergency DC lighting. Degree of perfection of D.C.D.B. should be IP 52

Suitable number of feeders shall be provided for feeding DC loads at 110-132 V at Sub-station and Pumping station.

The MCCB shall be provided with short circuit overload release and earth fault relay. The numbers of outgoing feeders indicated are tentative. If the system requires more feeders, the same shall be provided.

All non-current carrying metallic parts, instrument and relay cases shall be connected to earth bus bar by 2.5 mm2 stranded copper earthing conductor, green in colour. Power & control terminal blocks

shall be of unbreakable polyamide material. Protective covers shall be provided over open cable terminals.

Adequate space Shall be provided for termination of incoming cables.All meters and relays shall be flush mounting type.

Panel shall be fabricated of cold rolled sheet steel of thickness not less than 2.5 mm for front and rear equipment bearing surfaces and 2 mm for sides, top and bottom portions. The panel shall be free from undulations, dents and flaws and sufficiently re-in forced to provide level surfaces, resistance to vibration and rigidity during transportation and installation.

The perimeter of all doors, removable cover plates shall be gasketted all round with neoprene gaskets. Ventilating louvers, if provided, shall have fine brass or GI mesh screens. All doors shall be provided with concealed type hinges.

TESTS ON BATTERY AND BATTERY CHARGER:

The battery and Battery chargers shall be tested at the manufacturers’ works as per the approved QAP in the presence of the Engineer’s Representatives.

- EARTHING SYSTEM

The earthing and lightning protection system covers earthing conductors, earth electrodes and accessories. Metallic frame of all electrical equipment shall be earthed by two separate and distinct connections to earthing system, Crane rails, tracks, metal pipes and conduits also shall be earthed at two points. Steel RCC Columns, metallic stairs and rails of the building housing, electrical equipment also shall be connected to nearby earthing grid conductor. Metallic sheaths/ screens and armour of multicore cables shall be earthed at both ends. Metallic sheaths and armour of single core cables shall be earthed at the switchgear end only. Every alternate post of switchyard fence shall be connected to the earth grid by GS flat and gates by flexible lead to earthed post. Each Continuous laid length of cable tray shall be earthed at minimum two places by GS Flats to earthing system.

GENERAL

The entire earthing system shall fully comply with Indian electricity act and rules. The Contractor shall carry out all changes desired by the electrical inspector, in order to make the installation conform to I.E. Rules.

The main earth grid shall be laid at a depth of 1000 mm below Ground level, in trenches, earth strip shall be laid along the trench. It shall be protected against mechanical damage. Joints and tapings in

the main earth grid shall be made in such a way that reliable and good electrical connections are permanently ensured. All joints except the equipment end shall be welded. All joints buried in ground shall be suitably protected by applying two coats of bitumen and covering with hessian tape.

Conduits in which cables have been installed shall be bonded and earthed. Cable armors shall be earthed at both ends.

Earth pipe electrodes shall be installed as per IS 3043. Their location shall be marked on earth pit chamber covers.

The electrodes shall be tested for earth resistance by means of standard earth tester. A water tap for continuous water supply should be provided for each earth pit.

A disconnecting facility shall be provided for individual earth pit to check earth resistance.

All electrical equipment above 230 V shall be earthed at two points and equipment 230 V and below shall be earthed at one point.

Conductor size for connections to various equipment shall be as per the table as follows;

| Equipment | Conductor Size |
| --- | --- |
| Motors | 50 x 6 mm GI flat |
| Panels | 50 x 6 mm GI flat |
| Local control station, street light |  |
| pole & its junction box | 8 SWG GI wire |
| All switchyard equipment | 50 x 6 mm GI flat |
| Main earth grid | 50 x 6 mm GI flat |
| Indoor fixtures | 14 SWG GI wire |

All paint, scale etc. shall be removed before earthing connections are made. Anchor bolts or fixing bolts shall not be used for earthing connections.

EARTHING MATERIALS

The earthmat shall be made up of MS. Flats in the outdoor switchyard and also duly connected with the respective pump house earthmat. The earthmat risers shall be made available at the vicinity of the foundations of the steel structures within a radius of 2 m. approx. The contractor’s scope of earthing work shall be as under –To interconnect the earthing terminals of equipment with earthmat, by providing a suitable M. S. Flats for the said interconnection.

To provide the earth wire (Lightning shield wire) on the top of towers and earth mask to protect the outdoor equipment from the strokes of lightning. The wire shall be hot dipped galvanized, brand flew, best quality and of suitable size.

To provide the various clamps as required for fixing the earth wire on top of towers. It shall be noted that the earthing is to be provided for each of the following apparatus.All structures and steel works, the base of all equipment and control gear etc.All metal casing on metallic coverings of the electric apparatus.The earthing shall confirm to IS 3043. Bidder shall note that in carrying out the earthing work, no welding of. any MS. flat shall be made on the galvanized steel structures.

EARTHING STATION – PIPE ELECTRODE TYPE

The pipe electrode of 40 mm dia. x 3000 mm long GI pipe shall be provided. Salt and coke shall be filled in layers of 25 mm up to one meter and balance shall be filled with loose soil. However, care shall be taken that the earth pit does not sink. The brick chamber (600 x 600) shall be made 75 mm above Finished ground level (FGL) and shall have a heavy duty cast iron frame with hinged cover at top for inspection. A 40 mm NB GI Watering pipe shall be provided in the pit.Lightning Protection System This shall compromise vertical / horizontal air terminations, down conductors , test limits and earth electrodes. Air terminations, down conductors and test links shall be of galvanised steel conductors and earth connection below the ground level shall be of mild steel.

Lightning Protection System down conductors shall not be connected to other earthing conductors above the ground level.Applicable StandardsThe earthing and lightning protection system shall conform to the Indian Electricity rules,and the latest applicable standards indicated below:

- Code of Practice for Earthing: IS:3043

- Code of Practice for the Protection of Building and allied structure against lightning - IS:2309

Instrumentation Earth

An instrumentation earth bus, if required shall be provided in each control panel. This shall comprise a copper flat of cross section not less than 25 x 6 mm and length to suit the number of connections. It shall be mounted on at least two insulated supports and beprovided with a single earth connection to the instrument earth. If due to the physical sizeof a control panel, more than one instrument earth bar is required the additional bar shallbe connected again with a single earth connection to the same point as before. In this fashion all instrument earths shall be connected radially from the same earth point.The earth pit for instrumentation system shall be separate. Electric earth pit shall not be used for earthing of

instrumentation equipment. All signal cable screens (analogue and digital) shall be terminated onto the

instrument earth bar. Signal cable screens shall be earthed at the control panel end only. Screens at the field end shall be tied back and insulated.

LIGHTING SYSTEM

The cabling/wiring, installation and commissioning of complete illumination system shall comply with all currently applicable statutes, regulations, fire insurance and safety codes.Outdoor lighting shall be carried out by using 1.1 KV grade four core cable. The cabling for the outdoor lighting fixtures will be done in loop-in/loop-out at respective outdoor fixture mounted junction boxes. The indoor lighting of High bay/medium bay shall be carried out by using 2 Core, 2.5 mm2 copper cables. The indoor office area wiring shall be carried in conduits.Outdoor cabling shall be buried in ground whereas indoor lighting wiring (cable/conduit) shall be of exposed type.

GENERAL REQUIREMENTS

Location of lighting fixtures, switches and receptacles shall be shown on the drawing and shall be relocated if required to suit the site conditions. 5A, 3 pin & 15A, 5 pin receptacles with switches shall be provided on the light control switch boards.

LP’s shall be provided with labels indicating LP number and outgoing circuit feeder numbers.

LPS shall be provided with cable gland for incoming cable and knockouts for outgoing conduit termination.

Cable and Conduit supports shall be provided at an interval of 300-400 mm. for horizontal runs and 400-500 mm for vertical runs.Cables and Conduits shall be kept, wherever possible at least 300 mm away from pipes, heating devices and other equipment.For the purpose of calculating connected loads of various circuits, a multiplying factor of 1.25 will be made to the rated lamp voltage for lamp fixtures to take into account the losses in the control gear.Contractor shall supply junction boxes, pull boxes, terminal blocks. glands conduits and accessories (elbows, tees, bends etc.) and supporting/anchoring materials, to make the installation complete.

In all types of cabling. due consideration shall be given to neatness and good appearance.

The work for installation, testing and commissioning of the indoor lighting shall include the mounting of fixtures with necessary materials, laying of cable/conduit, pulling of wires through conduit and external earth wire, providing all accessories for cable/conduit installation, including conduit fittings. Providing of light control switch board with switches, switch board mounted 5A, 3 pin receptacles with switches etc.

TESTING

Lighting installation testing shall include but not be limited to the following:

Measure the insulation resistance of each circuit without the lamps being in place. It should be not less than 1 M Ohms to earth.

Current and voltage of all the phases shall be measured at the lighting panel bus bars with all the circuits switched on with lamps. If required, load shall be re-balanced on the three phases.

Check the earth continuity for all socket outlets. A fixed relative position of the phase and neutral connections inside the socket shall be established for all sockets.

After inserting all the lamps and switching on all circuits, minimum and maximum illumination level shall be measured in the area with an approved industrial light meter.

LIGHTING FIXTURES STANDARDS

| NO | STANDARD | DESCRIPTION |
| --- | --- | --- |
| 1. | IS 1913 | General & Safety requirements for electric lighting fittings |
| 2. | IS 1777 | Industrial lighting fittings with metal reflector |
| 3. | IS 5077 | Decorative lighting outfits |
| 4. | IS 2149 | Luminaries for street lighting |
| 5. | IS 6665 | COU for Industrial Lighting |

OTHER CONSIDERATIONS

Lighting system shall be designed considering following Lux levels.

-.	pump room area	100 Lux

- maintenance bays	200 Lux

- elect. Substation/ control room  250 Lux

- outdoor areas /110KV Switchyard	50 Lux

In order to have higher illumination for maintenance and repairs in the substation area outlets of 16 a spn shall be provided for the connection of portable lamps.

TECHNICAL PARAMETERS

| No. | Standard | Description |
| --- | --- | --- |
| 1. | Rated Voltage (with variations) | 230 V +/- 10% |
| 2. | Incoming cable, conduit entry for fixtures | Cable entry for LED lamps, Conduit for fluorescent tube lights |
| 3. | Painting | Vitreous enameled reflectors for LED lamps |
| 4. | Types of lamps – Indoor Outdoor | 250 W highbay fixture 70 W lowbay fixture single tube LED fixture, vitreous enamel reflector twin tube LED fixture LED lamp floodlight fixture |
| 5. | Type – Outdoor Indoor | Weather proof for outdoor fixture Commercial for office areas and Industrial for other areas |
| 6. | Earthing | One Terminal Outside. |

Lighting System Equipment

Main Lighting Distribution Board and Lighting Panels (AC & DC)

(a) Constructional Features

- Boards and panels shall be sheet steel enclosed and shall be fully dust and vermin proof, providing a degree of protection of IP 52. Outdoor panels shall in addition be completely weather-proof with a sloping canopy for protection against rain and providing a degree of protection of IP 55. The sheet steel used for frame, frame enclosures, doors, covers and partitions shall be cold rolled 2 mm thick.

- All boards and panels shall be provided with hinged doors for access to equipment. Doors shall be gasketted all round with neoprene gaskets. For the main floor mounted distribution boards with the switch fuse units arranged in tier formation, the hinged door of each unit shall be interlocked so as to prevent opening of the door when the switch is ON and to prevent closing of the switch with the door not fully closed. However, a device for by-passing the door interlock shall be provided to enable the operation of the switch with the door open, when necessary, for examination/maintenance. For wall mounting 1-phase ways lighting panels when provided with MCBs, a hinged, latched front door shall be provided with key-locking facility and a slotted backelite sheet shall be provided inside. Only the MCBs operating knobs or the fuse cap covers shall project out of the backelite sheet slots for safe operation and neat appearance. Incomer to lighting panels shall be provided with TPN MCB with ELCB.

- All accessible live connections/metals shall be shrouded and it shall bepossible to change individual fuses, switches, MCBs from the front of theboards/panels without danger of contact with live metal.

- For floor mounting type distribution boards, adequately sized mounting channels shall be supplied and for wall/column/structure mounting type panels suitable mounting straps shall be provided.

- Adequate interior cabling space and suitable removable cable entry platesshall be provided for top/bottom entry of cables through glands and or conduits as required. Necessary number of glands to suit the specified cable sizes shall be provided. Cable glands shall be screwed on type and made of

brass.

- Two earthing terminals shall be provided to suit the earthing conductor.

- All sheet steel parts shall undergo rust-proofing process which should include degreasing, de- scaling and a recognised phosphating process. The steel works shall then be painted with two coats of Zinc - chromate primer and two coats of final stove-enamelled finish paint of specified colour.

Panels/Boards’ Component Equipment

  - Switches/Miniature Circuit Breakers (MCB)

    - Switches/MCBs shall be hand operated, air break, quick make, quick break type conforming to applicable standards.

    - The switch shall be protected by fuse and the MCB shall be provided with overload/short-circuit protective device for protection under overload and short-circuit conditions. The minimum breaking capacity of MCBs shall be 6 kA r.m.s. at 415 V/220 V D.C.

    - Switch shall have provision for locking in both fully open and closed positions. MCBs shall be provided with locking facility.

    - The connections between switch and fuse shall be insulated and all live connections shall be shrouded.

  - Fuses

    - Fuses generally shall be of the HRC cartridge fuse-link type having a certified rupturing capacity of 80 kA at 440 V. Fuses upto 63A for distribution systems of medium short circuit levels may be of HRC cartridge screw-cap, D type, having a certified rupturing capacity of not less than 46 kA at 440 V and16 kA at 250 V D.C.

    - Fuses shall be provided with visible indication to show that they have operated.

    - Cartridge fuses shall preferably be mounted in moulded plastic carriers. If fuse-carriers are not provided, insulated fuse pulling handle shall be provided for each size of fuse for each switchboard.

  - Indicating Instruments and Meters

    - Whenever required, instruments and meters shall be of the flush mounting type. They shall be suitably mounted so as to provide for easy access to CTs and small wiring.

    - Instruments shall be of minimum 96 mm square size, shall have provision for zero adjustment outside the cover and black numerals on white dial Watt-hour meters shall be of direct reading electro- dynamometer typecomplete with cyclometer type dials and reverse running stops.

- Ammeter/Voltmeter selector switches having 3 positions and off, with stayput contacts rated 10A shall be provided when specified.

- Potential fuses shall be provided at the tap-off point from the busbars for the voltmeters.

  - Internal Wiring

    - Panels/boards shall be supplied completely wired, ready for the external connections at the terminal blocks. Wiring shall be carried out with 650/1100V grade, PVC insulated, stranded aluminium/copper conductors.Conductors of adequate sizes shall be used to suit the rated circuit current.

    - Engraved identification ferrules, marked to correspond with the wiringdiagram shall be fitted at both ends of each wire.

    - All wiring shall be terminated on terminal blocks. Terminal blocks shall be one piece moulded rated 500 V, of reputed make, preferably stud type for higher current ratings such that wires are connected by cable-lugs and complete with nuts and washers. Terminals shall be adequately rated for the circuit current, the minimum rating shall be 20 A.

    - Terminals for circuits with voltage exceeding 125 V shall be shrouded.

    - Terminals shall be numbered and provided with identification strip for identification of the circuit.

Light Control Switches

      - Light control switches of ratings and types, i.e. decorative/industrial shall be supplied as required. The switches shall be suitable for use on 240 V, 1 Ph, 50 Hz supply.

      - Switches shall be of flush type for mounting behind an insulated plate or incorporated with a switch plate for mounting flush with the surface of wall or switch box/suitable enclosure. The switch box/enclosure may be recessed into or mounted on a wall as per the requirement of project layouts.

      - The size of enclosure boxes shall be chosen to accommodate the number of switches to be installed at the particular location. The enclosures shall be 18 gauge sheet steel galvanised. The enclosure box shall be covered with perspex/insulating cover. An enclosure intended for surface mounting shall not have holes or gaps in its sides other than those expressly provided for cable entry.

Receptacle Units

- Receptacle units shall consist of socket outlet with associated switch and plug. The socket outlet and switch or MCB shall be flush mounted within galvanised 18 gauge steel enclosure with insulation cover. The box may be recessed into or mounted on a wall as per requirements of project layouts.

- The receptacle units shall be suitable for 240 V, 1 ph - N, 50 Hz/415 V, 3 Ph - N, 50 Hz supply as required.

- Single phase receptacles shall be associated with a switch/MCB of same current rating and the

receptacle shall become live only when the associated switch/MCB is in “ON” position.

- Three phase receptacles shall be associated with a TPN switch housed in the same enclosure. The

receptacle shall become live only when the associated switch is in “ON” position.

- The plugs shall be provided with cord grips to prevent strain and damage to conductors/wires at connection and entry points.

Lighting Wires

- The wires for wiring in lighting system shall be 250/440 V, 1/C, PVC insulated,unarmored with stranded copper conductors.

- The minimum area of conductors shall be 1.5 sq.mm. for light fittings and 5A Receptacles and 2.5 sq.mm for receptacles rated 15 A and above.

- The wires shall be coaded white for phase/positive of D.C. and black for neutral/negative of D.C.

Conduits

- Rigid steel/non-metallic conduits and their associated fittings as required shall conform to applicable standards. The minimum size of conduit shall be 20 mm for surface installation and 25 mm for concealed installation.

- Steel conduits shall be seamed by welding and hot dip galvanised. They shall be supplied in standard lengths of 5 m.

- Supply of conduits shall include all associated fittings like couplers, bends and tees as required for lighting system installation work. Junction Boxes

- Junction boxes with terminals shall be supplied for branching and terminating lighting cables when required for outdoor areas, 3 phase receptacles etc.

- The junction boxes shall be dust and vermin proof and shall be fabricated from 14 gauge sheet steel and shall be complete with removable cover plate with gaskets, two earthing terminals each with nut, bolt and washer. Boxes shall be additionally weather proof.

- The boxes shall have provision for wall, column, pole or structure mounting and shall be provided with cable/conduit entry knock outs, terminal blocks, HRC fuses as required.

- The terminal blocks, with specified number of terminals, shall be mounted securely on brackets welded to the back sheet of the box. The terminals shall be 600 V, grade, one piece construction complete with terminals, insulation barriers, galvanized nuts, bolts and washers and provided with identification strips of PVC. The terminals shall be made of copper alloy and shall be of box clamp type.

- The boxes shall be painted with one shop coat of Red oxide zinc chromate primer followed by a finishing coat of paint.

Lighting Poles and Flood Light Pole Mounting

- Lighting poles for street lights and flood lights shall be of stepped tubular steel polesconstruction as per applicable standard. These poles shall be coated with bituminouspreservative paint on the inside as well as embedded outside surface. Exposedoutside surface shall be painted with one coat of red lead oxide primer. After completion of installation two coats of aluminium paint shall be applied.

- Poles for mounting flood lights shall be supplied whenever required and as per typical attached drawing. Unless otherwise specified, poles, shall be painted with red lead oxide primer and two coats of aluminium paint. A steel ladder shall be provided. The length of each step of the ladder shall be at least 300 mm and spacing between two adjacent steps not more than 300 mm.

- The supply of poles shall be complete with fixing bracket/necessary pipe reducer for fixing the fitting and also include the necessary associated pole mounted junction boxes. The required sizes of poles and the junction box shall be as indicated in the drawings.

CABLING SYSTEM INSTALLATION

The cables shall be laid in trenches, trays or conduits or buried in ground. Tenderer to submit cable layout drawing for approval of KNNL. All cables shall be carefully measured and cut to the required length, leaving sufficient length for final connections to the equipment on both ends.

The Contractor shall ascertain the exact requirement of cable, for a particular feeder, by measuring at site along the actual finalized route.

Cables shall be laid in complete uncut lengths from one item of equipment to another. Cables shall be neatly arranged in the trenches, trays in such a manner, that crisscrossing is avoided and final takeoff to the motor, switchgear is facilitated. Arrangement of cables within the trench, tray shall be the responsibility of the Contractor.

Power and control cables shall be laid on different trays in one trench. Power and control cables shall be separated.  1.1 KV grade cable may be laid on one tray.

All cables shall be identified close to their termination point by cable numbers. Cable numbers will be punched on aluminum straps, (2 mm thick), securely fastened to the cable and wrapped around it.

Underground cables shall be provided with cable markers. These cable marker posts shall be located at every 50 meters and every comer or change of direction.

All temporary ends of cables shall be protected against dust and moisture to prevent damage to the insulation. While laying cables, the ends shall be taped with PVC tape.

Cables shall be handled carefully during installation to prevent mechanical injury to the cables. Ends of cables leaving trenches shall be coiled and provided with protective cover until the final termination to the equipment is completed. Where cables rise from trenches to motors, control stations, lighting

panels etc., they shall be taken up in GI pipes (rigid, flexible) for mechanical protection up to a minimum of 600 mm above grade level. The diameter of the GI pipe shall be at least 3 times the diameter of the cable.

Cable shall be carefully pulled through conduits to prevent damage.

If pipe sleeves installed are inadequate due to a greater number of cables being laid, then additional pipe sleeves shall be laid. After the cables are installed and all testing is complete, conduit ends above grade level shall be plugged with suitable weatherproof plastic compound.

Where cables pass through foundation walls or other underground structures, the necessary ducts or openings will be provided in advance for the same.

At road crossings and other places where cables enter pipe sleeves an adequate bed of sand shall be given.

Cables installed above grade level shall be run in trays, exposed on walls, ceilings or structures and shall be run parallel to or at right angles to, beams, walls or columns.

The cables shall be so routed that they will not be subjected to heat

Cables running along with structures will be clamped by means of GI saddles and saddle bars at a spacing of 300 mm.

Cable carrier system i.e. site fabricated ladder type cable trays and supporting steel shall be painted before laying of cables. Painting shall have two coats of red oxide and one coat of Aluminum paint

For all outdoor buried cables a 3 meter diameter loop shall be provided at both ends before termination.

TERMINATION

All PVC cables shall be terminated at the equipment/panel by means of double compression type brass glands and tinned copper lugs.

All XLPE cables shall be terminated at the equipment/panel by means of HT cable termination kits. Power cable cores shall be identified with red, yellow and blue PVC tapes.

In case of control cables, all cores shall be identified at both ends by their terminal numbers by means of PVC ferrules. Wire numbers shall be as per inter-connection diagrams, to be furnished to the Contractor.

The cable shall be taken through an adequate size gland inside the panel or any other electrical equipment.

Cable leads shall be terminated at the equipment terminals by means of crimped type solder less connectors.

Crimping shall be done by hand crimping/hydraulically operated tool and conducting jelly shall be applied on the conductor. Insulation of the leads should be removed immediately before the crimping.

TESTING OF CABLES

Before energizing, the insulation resistance shall be measured from phase to phase and phase to ground.

HT CABLES STANDARDS

No.	Indian Standard	Description

  - IS 7098	XLPE insulated electric Cables.

  - IS 5831	PVC insulation and sheath of electric cables.

  - IS 3975	Mild steel wires, strips and tapes for

armoring of cables.

  - IS 1753	Aluminum conductors for insulated cables

OTHER CONSIDERATIONS

The HT cable sizing shall be based on 250 MVA fault level at 6.6 KV. The short circuit withstand duration shall be 1.0 Sec for all feeders.

TECHNICAL PARAMETERS

| i) | Voltage grade |  | - If 11 KV is the incoming supply, the cable is laid from incoming GOS to metering cubicle and to the transformer. - 6.6 KV (E) grade (Earthed System) laid from the transformer to 6.6 KV Switchgear |
| --- | --- | --- | --- |
| Ii | Impulse level |  | As per IS. |
| Iii | No of cores |  | As per requirement |
| iv) | Nominal area of conductor |  | As per requirement to suit short circuit level. |
| v) | Conductor |  | Aluminum conductor complying with the requirements specified in I.S. |
| vi) | Type of insulation |  | Cross linked polyethylene (XLPE). |
| vii) | Shielding |  | Conductor shielding and insulation Shielding. |
| viii) | Armoured or Unarmored |  | As required |
| ix) | Cables to be used in earthed or : unearthed system |  | Earthed system. unearthed system |

CONDUCTOR

The conductor shall be made from high electrical purity Aluminum of circular shape. Conductor construction and testing shall comply to latest I.S.

INSULATION

High quality XLPE insulating compound of natural colour shall be used for insulation and shall be chemically cross linked by continuous vulcanization process. The cables shall be manufactured with dry cure system. This shall comply to latest IS.

SHIELDING:

The XLPE cables shall be provided with both conductor shielding and insulating shielding. Both conductor shielding and insulation shielding shall consist of extruded semiconductor compound. Additional insulation shall be provided with semiconductor tape and non-magnetic tape screen over the

extruded insulation conductor shielding. XLPE insulation and insulation shielding shall be extruded in one operation by a special process ensuring perfect bonding of inner and outer shielding with insulation.

OUTER SHEATH

A tough outer sheath of heat resisting PVC compound shall be extruded over the non-magnetic metallic part of insulation screening. This shall confirm to latest I.S. The outer sheath shall be embossed with name of manufacture, voltage grade and year of manufacture after every 1000 mm along the length of cable.

The outer sheath of the cable shall be provided with antirodent1 antitermite property.

The outer sheath of the cable shall be marked with progressive length and cable at one meter interval at the time of manufacturing.

The outer sheath of the cable shall have fire retardant low smoke property (i.e. FRLS) and shall be tested for IEC 332-3 category C.

MISCELLANEOUS

CABLE GLANDS AND LUGS

All cable glands shall be made out of brass and shall be of double compression type. All cable lugs shall be of tinned copper, crimping type.

CABLETRAYS

Cable carrier system shall comprise of site fabricated ladder type cable trays made out of structural steel and painted with two coats of red oxide primer and a final coat of enamel paint. The construction of the cable trays shall be as per the site requirement.

JUNCTION BOXES/MARSHALLING BOXES

Each equipment shall be provided with a junction box as near as possible to the equipment. In addition, one marshalling box for each bay shall be provided. Junction boxes/ marshalling boxes shall be fabricated from sheet metal steel and shall be outdoor type, weather and vermin proof with hinged door and lock. They shall be duly painted from inside the outside as per standard industrial type painting.

Each box shall have detachable gland plates for incoming and outgoing cables. Each box shall contain adequate terminal strips for cable connections. The terminals shall be ELMAX-10 type or equivalent.

WATER LEVEL INDICATOR

The electronic water level indicator of suitable range shall be supplied for indicating the water level in the sump which may vary from minimum W.L to maximum W.L

Minimum levels as per working table have to be recorded.

The instrument shall be wall mounting type & indication shall be digital to read the level in units of 0.1m.

The instruments shall operate on 230 Volts 50 cycles, AC supply, sets of adjustable contacts shall be provided to trip the pumps in events of water level reaching the lowest water level and to give an audible alarm in case of high or low water levels. The instrument provided should be of pressure sensing type of or capacitance sensing. The electrodes shall be provided with rubber sheathed suspension cable for suspension

## SPECIFICATIONS FOR OVERHEAD TRANSMISSION LINE

  - OVERHEAD TRANSMISSION LINE:

INTRODUCTION :

For extension of supply to the pumping stations HT line from nearby sub stations is to be constructed. The contractor shall survey, and propose the available the power from the nearby stations. The routing, design, supply and erection of Transmission Line has to be with the approval of KPTC and other Statutory authorities and in conformity with the specifications of the Transmission Company. The details mentioned herein is to be taken as guide lines. All the other works required for completion of the system, though not specifically mentioned in these specifications, are in the scope of the Contractor.

SCOPE:

SURVEY:

- Survey, Design, fabrication, supply of materials and transport to site, erection, testing, and commissioning of HT lines to the pumping station.

- Formation of take-off bay at the sending end of the KPTCL / ESCOM substation as per the requirement.

The bidder is required to carry out detailed survey. After the finalization of profiles, the contractor must fix up locations based on the approved spans indicated in the profile / tower schedule and only conspicuous variations in the chainage and physical features as indicated in the profile and as actually noticed during survey must be brought to the notice of the Engineer for checking. If the site of a tower location is not suitable for locating a tower, the location will have to be shifted suitably keeping in view, the limitation of span and the engineer will decide this. The contractor himself should arrange all the tools and the instruments required for carrying out the survey. WAY LEAVES AND TREE CUTTING:

Any way the contractor himself will arrange leaves and tree cutting, which may be required by him.The contractor shall submit proposals for way leaves and right of way. The Engineer shall not be held responsible for any claim on account of damages done by the contractor or his gangs to trees, crops or other property without authority from the Engineer.

The contractor shall take all possible steps to see that standing crops etc. are not damaged. When such damage is inevitable the compensation will be borne by the ENGINEER provided, the damage is with prior concurrence of the Engineer. The contractor shall bear the	compensation	for damages caused without prior concurrence of the Engineer concerned. In the event of any obstruction being encountered from the localvillagers or authorities, the contractor shall immediately notify the Engineer who shall take such steps as may be necessary to clear the obstruction. The

contractor or his representative or gangs shall not adopt antagonistic attitudes towards the village authorities with whom they may come into contact, but shall immediately report to the Engineer any case of obstruction which cannot be settled amicably. No trees shall be cut until The ENGINEER has made necessary arrangement with the Authorities concerned and permission is given to the contractor to fell such trees. The ENGINEER shall arrange to remove the obstacles as soon as possible. At times however, it may not be possible for the ENGINEER to arrange right-of-way for laying foundations or erecting the towers or stringing the line. At all such times, the contractor shall shift his gangs to other areas. The rates quoted shall cover all such contingencies and no extra payments shall be claimed for such contingencies.

STUB SETTING AND FOUNDATIONS: SETTING OF STUBS:

The contractor shall undertake full responsibility for the correct setting of stubs in accordance with the approved methods of the exact locations and alignment and in precisely correct level. Stub setting templates shall be used for proper setting of stubs.

Cement concrete foundations shall be constructed complying with the foundation drawings to be approved by the employer. The type of foundation to be laid at each location will be decided by the Executive Engineer after inspection of site and for this purpose the locations must be excavated for dry type foundations initially and offered for inspection. Foundation at a location shall be laid only on receipt of written communication from the ENGINEER indicating the type of foundation to be laid.

The rate for laying the foundations with 1:2:4 mix concrete shall cover the cost of stub setting and dewatering of pits during concreting and cost of cement but shall be exclusive of the excavation cost. The ENGINEER reserves the right to uncover and examine any foundation and if it is found to be not according to specification and the contractor shall be required to open up the tower foundations and rectify all defective foundations thereby discovered at his sole expense and cost.

EXCAVATION FOR FOUNDATIONS:

HARD ROCK: Hard rock will be that which requires drilling and blasting by any method. The cost of drilling and blasting shall be included in the quoted rates. In certain cases, when the area around the location happens to be an inhabited area consequent to which blasting cannot be resorted to, the excavation may have to be done either by the process of drilling, wedging, hammering and splitting or by the process of heating and splitting by sudden cooling. The rate quoted shall be taken into consideration for such contingencies also.

TYPES OF FOUNDATIONS:

Cement concrete footing shall be used for all types of towers in conformity with the present-day practices followed in the country. There will be mostly pyramid and chimney type. In very loose soils and wet locations R.C.C type of foundations may have to be provided to suit actual conditions. All the

four footings of towers will be similar. No separate rates shall be quoted for dewatering of pits for laying concrete. Bidder shall quote for concreting including cost for dewatering. In case of river crossings it may be necessary to use well foundations or other special type of foundations based on actual conditions.

CLASSIFICATION OF FOUNDATIONS:

Depending on the type of soil, the subsoil water table and the presence of surface water, five types of foundation designs shall be used for each type of locations classified in the following manner.

Normal dry type: To be used for locations in normal dry cohesive or non-cohesive soils.

Wet type: To be used for locations.

- Where sub-soil water is met at 1.5 meters or more, below the ground level Which are in surface water for long period with water penetration not exceeding one meter below the ground level e.g., the paddy fields.

- In black cotton soils.

- Partially submerged type: To be used at locations where sub-soil water table is met at more than 0.75 meter below the ground level.

- Fully submerged type: To be used at locations where subsoil water is met at less than 0.75 meters from the ground level.

- Rocky type: To be used at locations where hard rock is met with and where the bond strength between rock and concrete will be very high.

In addition to the above, depending on the site conditions more varietiesof foundationsmay be introduced suitable for intermediate conditions under the above classifications to effect more economy.

CONCRETE:

The cement concrete used for the foundations (pad, frustum and chimney) shall be of 1:2:4 mix ratio with 20 mm (3/4”) hard broken granite metal.

The cement required for the work will be supplied by the Contractor. The cement to be used for this line shall confirm to the specification as furnished below -

The cement required for the work have to be supplied by the contractor. Ordinary Portland cement of Grade - 43 manufactured as per IS - 8112 of 1989 shall only be used. Storage, certification, delivery and testing of the cement shall conform to IS - 8112 with latest amendments. IS certification mark is obligatory. Cement procured  from  major  cement manufacturing  plants	will only be accepted for which prior approval shall be obtained from the employer. Copies of invoices and test certificates from the cement manufactures shall be submitted by the Contractor to the

Engineer and obtainclearance before actual use. Such clearance will be given within a maximum period of one week.

The sand used for the concrete shall be composed of hard silicon materials. It shall be clear and of sharp angular grit type and free from earthy or organic matter and deleterious salts.

The aggregate shall be of clean broken hard granite or other stone specified or approved by the Engineer. It shall be of hard, close- grained quality. It shall also be as far as possible cube like, preferably angular, but not flaky, perfectly clean and free from earthy organics or other deleterious matter. 20mm aggregate shall be of size as will pass through 20 mm square mesh measured in clear. The water used for mixing concrete shall be fresh, clean and free from oil, acids and alkali. Saltish or blackish water shouldn’t be used.

The concrete should be mixed as stiff as the requirements of placing the concrete in the forms or moulds with ease warrant and the degree to which the concrete resists segregation will permit. The quantity of water used should be minimum. In the interest of speedy execution of works and to obtain homogeneous mix of concrete, mechanical mixers and Vibrators shall be used for mixing& consolidation of concrete, except in case of emergency (such as failure of mixer or where it is not practicable to have mixer up to the location) or for each concrete sub-base where hand mixing can be resorted.

Proper forms of moulds adequately braced to retain proper shape while concreting should be used for chimney or pyramid and slab portions. The mould should be made water tight so that cement cream will not come out leaving only sand and jelly consequently forming honeycombing in the concrete .The rate for concrete should be inclusive of form box. Sufficient number of form boxes for each type of foundation should be made so that the works are not held up on this account .The stub angle shall be free from rust and cleaned thoroughly and coated with cement paste made of one part of cement and 3/4 part of water (cement slurry) to thickness of 1.6 mm (1/16’’) before the cement slurry shall be done each time to such a height so that concrete will be laid to that height before the cement wash becomes dry. The form boxes shall be cleaned and oiled before these are used for concreting.The concrete shall be laid in 150 mm layers and consolidated well so that  the

cement cream works up to the top and no honey- combing is left in the concrete. After concreting the chimney portion to the required height, the top surface should be finished smooth, with slight slope towards the outer edge to drain off the rainwater falling on the copings. These copings and muffing should be done after the stringing is completed in respect of tension locations and the Engineer at site may decide such other locations. For Such locations an adhoc reduction of Rs.100 per location will be made while billing concrete and this will be released after coping and muffing are completed.

In special cases, The ENGINEER at site may authorize use of Quick setting or rapid hardening compound in certain foundations. The cost of such quick setting compound will not be paid extra.

Concreting is to be done continuously and monolithically, so that the subsequent layers are laid before the initial setting of the bottom layer begins. If, on rare occasions, fresh concrete is to be laid on old concrete in less than a week, the surface of the old set concrete chipped and cleaned thoroughly with wire brush and washed with a layer of thick cement slurry before the new concrete is laid. If, however the concrete is more than 10 days old, the top layer of the set concrete should be chipped and cleaned thoroughly with wire brush and fresh water, and layers of cement mortar 12 mm thick shall be laid only after giving a coat of cement slurry, as specified above to ensure proper bonding between old and new concrete.

In wet locations, the site must be kept completely dewatered both during the placing of the concrete and for 24 hours after completion. There should be no disturbance of concrete by water during this period .No extra rate will be paid for the dewatering and rate for concrete shall be inclusive of dewatering charges.

The forms of moulds shall not be removed before a lapse of about 24 hours after the completion of concreting. After removal of the forms, the concreted surface, where required, shall be repaired with a rich cement and sand mortar in the shortest possible time.

CURING AND BACKFILLING:

The concrete after it is 24 hours old shall be cured continuously for a period of 14 days after laying it. The concrete after it is 24 hours old shall be cured by keeping the concrete wet and no separate rate shall be payable for curing and it is to be included in the rate for concreting. The pits may be backfilled with selected andexcavated earth sprinkled with necessary amount of water and well consolidated in layers not exceeding 150 mm thickness after a minimum period of 24 hours on completion of concreting. As the uplift strength of the foundation depends upon proper consolidation of backfilled earth, extreme care shall be taken in this regard with special emphasis. Thereafter both the backfilled earth and exposed chimney top shall be kept wet for the remainder of the prescribed time of 14 days. The backfilling of foundations shall be so carried out that after one monsoon the level of the backfilled earth does not go below the surrounding ground level. However if any foundation settles below ground level after one monsoon, the contractor shall fill the same to make it to be in level with surrounding ground level without any extra charges. The stub setting templates shall be opened only after the completion of backfilling .No separate rate shall be payable for backfilling and so it is to be included in the excavation rate.

After back filling, about 150 mm high earthen embankment along sides of excavation pits will be made and sufficient water will be poured in the back filled pits so that standing water remains above

the back filled earth for at least 24 hours. The uncovered concrete chimney above the back filling earth shall be kept wet continuously for 14 days after concreting by providing wet empty cement bags fully wrapped around the concrete chimney for curing and ensuring that the bags are kept by frequent pouring of water on them

The excavated earth left over should be spread within the four legs of the tower location.

GROUNDING:

Pipe earthing or counterpoise earthing has to be done at such tower locations where it is found necessary depending upon the type of soil met with at the location and the earth resistance at that location.

PIPE EARTHING:

At location where pits can be excavated, the towers shall be earthed by G.I. pipe earthing as per the drawings to be approved by the employer. The grounding shall be effected by making about 325 mm dia and 3750 mm deep pit at a distance of not less than 3650 mm diagonally away from the stubs and filling in the pits with finely broken coke having granule sizes not more than 25mm thick. The coke shall be maintained up to a distance of 150mm from the pipe on all sides. The top edge of the pipe shall be at least 600mm deep from the ground level.

The tenderer shall quote the charges for each earthing inclusive of the cost of earthing sets, coke, salt, GI earthing sets, excavation and backfilling and measuring the tower footing resistance.

COUNTERPOISE EARTHING:

In places of high resistivity soils especially in rocky locations special earthing	arrangemen shall	be employed in the form of counterpoise earth to bring down the towers footing resistance to

- ohms. The counterpoise earth shall consist of 4 Nos. 7/8 SWG galvanized steel wires running radially form all the four tower legs for a distance of about 15 to 30 meters .The galvanized steel wire shall be connected to the tower legs by galvanized steel lugs forged or compressed at its one end, complete with 16 mm (5/8”) dia bolts and nuts, required for connecting the earthing to the tower and the counterpoise shall be buried radially from the tower base at 600 mm below ground level. The lugs should be preferably buried in chimney portion of the foundation to avoid pilferage. The Bidder shall quote per meter rate for counterpoise earthing. The rate is inclusive of excavation and backfilling and other materials such as 120 meter of steel lugs and also measuring the footing resistance.

MEASURING TOWER FOOTING RESISTANCE:

The tower footing resistance of all towers shall be measured by the contractor using his own instruments in dry weather after the erection in the presence of the engineer before the stringing of earth wire and furnish the same to the employer.

ERECTION OF TOWERS:

Towers shall be erected by piecemeal method on the foundations, not less than 14 days after concreting and after such time that the concrete has been acquired its full strength. The tower shall be erected in workmanship like manner and its members shall not be strained or bent during the course of erection. Care shall be taken to see that the jointing surfaces are clean and free from dirt or grit. The tower erection shall be done in strict accordance with the drawings to be approved by the employer.

After initial erection, all tower bolts shall be checked to ascertain that all nuts are fully tight. The contactor shall ensure that none of the bolts have been left out by adopting suitable means. The bolts threads shall be punched immediately after completion of theerection of each tower to avoid the nuts becoming loose. Punching of bolts shall be made by Chamfering the threads with center punch, in at least three places equally placed on the contact surface of bolts and nuts.All the bolts and nuts in the towers up to the height below the bottom cross arm level including the bolt connecting the cross bracing at the cross arm level shall be seam welded in the upper half round portion (25mm length) of the bolt and nut circumferentially by using 10 gauge welding rods. This shall be done immediately after the tower is erected and its verticality is checked and found to be within the limits. After seam-welding surface matching the galvanized portion of tower shall be painted. Cost of this paint shall be included in the rate of round welding.

The contractor shall entirely be responsible for the correct erection of all towers as per the approved drawings, and their correct settings on an alignment approved by the engineer. If the stubs or superstructures after erection are found to differ from approved drawings or to be out of alignment, the contactor shall dismantle and re-erect them correctly at his own cost without extension of time. The towers must be truly vertical after erection and no straining will be permitted to bring them to vertically. Tolerance allowed for verticality is 25 mm in a height of

9.15 meters i.e., 1 in 360 of tower height. Verticality of each tower shall be measured by the contractor and furnished to the Executive Engineer.

The rate for tower erection shall be inclusive of punching of bolts, erection of danger, number and phase plates and anti climbing and anti perch devices or other tower accessories where necessary. Anti perch devices are to be fixed on all tangent towers.

Anti climbing devices, danger boards and phase plates are to be erected at all railway crossings, important road crossings etc., No extra charges shall be admissible even though separate gangs may have to be sent by the contactor for fittings these accessories and attachments on the towers at the appropriate time.

INSULATOR HOISTING:

Suspension insulators shall be used up to deviations of 2 degree on all tangent type towers in the line and tension insulators on all angle type towers.

For ensuring insulation co-ordination suspension or tension strings on approach and terminal towers near station ends up to a length of1.5 kilometers shall be provided with adjustable arcing horns on tower side and fixed arcing horns on line side keeping the arcing gap as may be stipulated by the Engineer at site. Insulator strings shall be assembled on the ground. These shall be cleaned and examined before hosting. They shall be kept on tarpaulins at the tower site so that, once they are cleaned there is no scope for the insulator to get contaminated. All accessories shall be properly fitted. It shall be ensured that all current carrying parts are smooth, and without dirt, cracks, or chips. Those having glazing defects exceeding half-centimeter square	shall not  be  used and such insulators shall be accounted for under 1% wastage allowed.No separate rates shall be quoted for rigging and hoisting of insulator strings. The charges for the same shall be included in the rate of stringing of conductor.

STRINGING OF CONDUCTOR AND EARTHWIRE:

The stringing of the conductors and earth wire shall be done by a standard method used for such lines, which shall be indicated in the tender .The Bidders shall give details of the stringing method and they shall also indicate the tools and equipment required for stringing and erection tools and other equipments.

Before the commencement of the stringing, the contractor shall submit the stringing charts for the conductor and earth wire showing the initial and final sags and tensions for various temperatures and spans along with equivalent spans in the line, for approval by the engineer.

The Contractor shall be entirely responsible for any damages to the Tower or conductor or Earth wire during stringing. He shall also be responsible for proper distribution of the conductor drums to keep the numbers and lengths of cut pieces of the conductor to the minimum. Pieces left over shall be accounted for under 1% wastage allowed.

HANDLING OF CONDUCTOR:

The contractor shall be entirely responsible for the proper handling of the conductor and earth wire drums in the field. Handling and transporting of the conductor drums shall be carried out in such a manner as to minimise the possibility of damage from abrasion through rough handling, or dirt and grit into reel and on the conductor, injury to conductor etc; particular care shall be taken at all times to ensure that the conductors do not kinked, twisted or abased in nay manner. Drum lifting jacks shall be used for paving out conductor. Trestles shall be provided in the spans in which theconductor is proposed for paving out and it shall be ensured that at no time conductor touches the ground

(whether hard or soft). If the conductor is damaged, the section effected shall be replaced or repaired by putting joint or using repair sleeve or polishing with emery cloth, so as to give satisfactory corona performance. At all stages of construction proper care shall be taken so that the conductor surface is smooth enough to give satisfactory corona and radio-interference performance.

All equipment used in handling and /or transporting the conductor, such as grips, pulleys, slings, cable car etc; shall be so designed and maintained that the surfaces which comes in to the contact with the conductor are kept free of foreign matter or defects which may lower the corona inception voltage of the conductor to an unacceptable level.

PULLING IN OPERATION:

The earth wire shall be strung and securely clamped to the towers before the conductors are drawn up, in the order of the top conductor first, then the middle and the bottom conductor at the end. It shall be ensured that all conductors of one section should be identically tensioned.

The pulling of the conductor into the travelers comprising aerial and ground rollers shall be carried out in such a manner that the conductor is not damaged or contaminated with any foreign substance and that it may not be rubbed with the rough ground surface. The travelers shall have a size and shape most suitable for the type of stringing and size of conductor involved and as recommended by the conductor manufacturer. The engineer before use shall approve these. The travelers surface in contact with aluminum surface of conductor shall be such a material that conductor is not damaged, like neoprene rubber, aluminum or stainless steel. These shall be equipped with high quality ball or roller bearings for minimum friction and easy movement in blocks during stringing and sagging.

During pulling out operation the tension in each conductor and earth wire shall not exceed the designed working tension of the conductor at the actual prevailing temperature. After being pulled, the conductor and earth wire shall be allowed to hang in the stringing blocks for more than 96 hours before pulled to the specified sag. During the time the conductors and earth wire are on the stringing blocks, before sagging in it shall be ensured that the conductors and earth wire are not damaged due to wind, vibration or other causes.

SAGGING IN OPERATION:

The conductors and earthwire shall be sagged in accordance with approved stringing charts before they are finally attached to the towers through the earth wire clamps for the earth wire and insulator strings for the conductor.

The conductors and earth wire shall be pulled up to desired sag left in travelers for at least one hour after which the sag shall be rechecked and adjusted, if necessary, before transferring the conductors from the travelers to the suspension clamps.The conductors shall be clamped within 36 hours of sagging in. Prestressing of conductor is not required. Instead, the conductorshould be

strung to sag on one inch to a foot less than the sag shown on the final sag charts provided by the erection contractor.

The sag will be checked in the first and last spans of the section in case of sections up to eight and in one intermediate span also for sections with more than eight spans. The contractor shall be responsible for any damage caused to the towers or to the conductors through overstressing during stringing. Dynamometers shall be used in checking the tension in the conductors and earth wire and these instruments shall be periodically checked with a standard dynamometer. The sag also to be checked when the conductors have been drawn up and transferred from aerial rollers to the insulator clamps.The stringing block, when suspended on the transmission structure for sagging shall be so adjusted that the conductor on the traveler will be at the same height as the suspension clamp to which it is secured.At sharp vertical angles, the sag and tension shall on both sides of the angle. The conductor and the earth wire shall be checked on the travelers for equality of tension on both sides. The suspension insulator assemblies shall normally assume vertical position when the conductor is clamped. Sagging operation shall not be carried out under wind, extremely low temperature or other adverse weather conditions which prevent satisfactory sagging.The contractor should ensure that

  - Any departure from the correct sag in any span does not exceed 4%.

  - The sag of any conductor does not depart by more than 3 % from the mean sag of the entire conductor in the same span.

CONDUCTOR DAMAGE AND REPAIR:

If the conductor is damaged for whatever reason and the damage is not repaired by repair sleeves or by rubbing with emery cloth, it shall be brought to the notice of the engineer and shall not be used without his approval. Even repairing of conductor surface shall be done only in case of minor damages, scuff marks etc., which are safe from both electrical and mechanical points of view. The final conductor surface shall be clean, and smooth, without any projections, sharp points cuts or abrasions etc., for giving satisfactory corona and R.I performance.

The joints on the conductor or the earth wire shall be of compression type in accordance with the recommendations of the manufactures for which the necessary tools and equipments like compressors and dies, grease guns, presses etc, shall have to be arranged by the contactor. These shall be made in the best workmanship like manner and shall be perfectly straight and having maximum strength. Each part of joints shall be cleaned by wire brush to make it free of rust or dirt etc., and properly greased before the final compression is done with the compressors.

All joint or splice shall be made at least 15 meters away from the structures. No joint or splice shall be made in spans crossing over main roads, railways, small rivers or in tension Span. Not  more

than one joint per conductor shall be allowed in one span. The compression type fittings used shall be of self – setting type or care shall be taken to make the cable to indicate when the fitting is centered properly. During compression or splicing operation, the conductor shall be handled in such a manner as to prevent lateral or vertical bearing against the dies. Care shall be taken to protect the conductor from scratches abrasions or other damages.After pressing, the aluminum sleeve shall have all corners rounded, burrs and sharp edges removed and smoothened.

ACCESSORIES:

Accessories like vibration dampers; Armour rods etc., for the conductors shall also be fitted on the line as desired by the Engineer according to the recommendations of the manufacturers. Armour rods shall be provided at all suspension supports of the conductors and vibration dampers shall be provided on both sides of the suspension and tension supports at suitable distances from the supporting points for each phase conductor. While fixing these on the line, care must be taken that conductor is not damaged in any way and no sharp edges are left at any point. All accessories shall be clean, smooth and in perfect condition before fitting. The charges for fitting of these accessories shall be included in the stringing rate for power conductor.

STRINGING RATE:

The rate for stringing of the conductors per route length of line shall include paving, stringing, tensioning, clamping and jointing of six /three conductors as specified in schedule for erection and fitting of all necessary accessories, specified above or otherwise, which are normally required or are usual with such line. Similarly the rate for stringing of the earth wire shall also include the stringing and fixing of the necessary accessories like suspension and tension clamps, earth bonds, compression joints etc., as required. Wherever necessary ground clearance has to be measured to ensure obtaining adequate ground clearance and the rate should include this also. The performance of the jumpers on the angle towers will be watched during the period of performance guarantee and for the failure of a jumper during this period resulting in the breakdown of the line an amount of Rs.10,000/ per jumper will be recovered from the annuity bills of the contractor due for payment by the employer against any of the works executed by him for the employer.

FINAL CHECKING, TESTING AND COMMISSIONING:

After the completion of the works, final checking of the line shall be done by the contractor to ensure that all the foundation works, tower erection and stringing have been done as approved by the Engineer, and also that they are complete in all respects. All the works shall be thoroughly inspected, keeping in view the following main points

- Sufficient backfilled earth is lying over each foundation pit and it is adequately compacted

- All the tower members are correctly used strictly as per the drawings and are free from any defect or damage, whatsoever,

- All the bolts are fully tightened and they are properly punched and half-round welded as per contractual provisions.

- The stringing of the conductors and earth wire has been done as per the approved sag and tension charts and desired clearances are available.

- No damage,minor or major to the conductor,earth wire, accessories and insulator strings still unattended are noticed.

- The jumpers provided at the cut points are connected rigidly to the tension hardware utilizing all the jointing bolts provided for the purpose.

After final checking, the line shall be tested for insulation in accordance with tests prescribed as standards. All arrangements for such testing or any other test desired by the Executive Engineer shall be done by the contractor and necessary labor, transport and equipment shall be provided by him. Any defects found out as a result of such test, shall be rectified by the contractor forthwith without extra charges to the Employer.

The contractor shall submit a report to the above effect to the Engineer. In case it is noticed later that some or any of the above are not fulfilled the Engineer will get such items rectified through other agencies and recover the cost of such works form the bills payable to the contractor against the contract against this specification or any other contracts executed by him for the employer.

The bidders shall note that recoveries will be effected in the payments in respect of the following. For each Jumper failure at a cut point	Rs.10,000/-

During the performance guarantee period.

After satisfactory tests on the line and on approval by the ENGINEER the line shall be energized at full operating voltage before handing over.

RECTIFICATION OF DEFECTS DURING THE GUARANTEE PERIOD:

After commissioning and handing over of the line to The ENGINEER the contractor shall arrange for thorough patrolling of the line during the first six months of the guarantee period so that the defects if any noticed during that period may be rectified by the contractor free of cost to the employer without having to wait for The ENGINEER to suggest such rectifications. During the balance period of the guarantee period however, the contractor shall arrange for rectification of the defects free of cost to The ENGINEER as and when pointed out by the employer.

EXECUTION OF WORKS RELATING TO POWER LINE CROSSINGS	AND RAILWAY CROSSINGS:

Works such as erection of towers underneath an existing power line and paving out of conductors and earth wire and stringing the power line crossing span or a railway crossing span, will have to be done only after receipt of approval from the concerned officer, which, sometimes, may not match with the programme of the contractor. In such cases, the contractor shall execute such works as and when approvals are received. His rates for tower erection and stringing shall take into consideration, such contingencies also.

The contractor shall indicate in detail the components of the material covered along with technical parameters

DRAWINGS AND DESIGN DATA:

Drawing showing the arrangement of line is to be submitted by the contractor before taking of the work. After completion of work the contractor shall submit final drawing making all modifications done during execution. The contractor shall furnish all design details for scrutiny and approval of the engineer before taking of work.

SCHEDULE OF MATERIALS TO BE SUPPLIED, ERECTED AND COMMISSIIONED BY THE CONTRACTOR

- Transmission towers

All types of Galvanised DC Transmission Towers including stubs, stub setting templates, the connected accessories such as flat washers, U-Bolts, Hangers, Bird Guards etc.,.

- Power Conductor : ACSR

- Earthwire: 7/3.15 mm Galvanised steel wire.

- Suspension insulator strings with hardware.single and double suspension insulator strings withArmour grip type clamp or equivalent hard ware.

- Tension Insulator Strings with hardware.single and double tension insulator strings with compression type hardware.

- Midspan compression joints for power conductor and groundwire. 7.Vibration dampers.

8.Compression type repair sleeves for Power conductor.

9.Suspension and tension (compression type) clamps with earth bonds for earth wire.10.	G.I Bolts and Nuts with flat washers and Spring, Washers

11.Cement required for foundations. 12.Reinforcement steel required for foundations 13.Earthing set (Pipe Type) including G.I. Earth strip.

14GI Step bolts, Number plates, danger boards and anti climbing devices and phase plates wherever necessary.

If the pumping station requires 11 KV source, the following specification shall be generally followed –

- KV TRANSMISSION LINES:

INTRODUCTION:

The laying of Transmission Line has to be with the approval of ESCOM and other statutory authorities and in conformity with the specifications of the Transmission Company. The details mentioned herein is to be taken as guide lines. All the other works required for completion of the system, though not specifically mentioned in these specifications, are in the scope of the Contractor.

SCOPE:

- This specification covers design, fabrication, supply of materials and transport to site, erection, testing, and commissioning of HT lines.

- Construction of take-off bay at the sending end.

SURVEY:

The bidder is required to carry out detailed survey. After the finalization of profiles, the schedule and only variation in the chainage and physical features as indicated in the profile and as actually noticed during survey must be brought to the notice of the ENGINEER for checking. The ENGINEER will examine & approve the position of locations if found technically suitable. The contractor himself should arrange all the tools and the instruments required for carrying out the survey.

WAY LEAVES ANDTREE CUTTING:

The Contractor will himself will arrange way leaves and tree cutting which may be requied. The contractor shall submit proposals for way leaves and right of way. ENGINEER shall not be held responsible for any claims on accont of damages done be the contractor or his gangs to trees, crops or other property without authority from ENGINEER. The contractor shall take all possible steps to see that standing crop etc., are not damaged. When such damage is inevitable, compensation shall be borne by ENGINEER, provided the damage is with prior concurrence of the Engineer. The contractor shall bear the compensation for damages caused without prior concurrence of the Engineer concerned. In the event of any obstruction being encountered from the local villagers or authorities, the contractor shall immediately notify the Engineer so as to enable him to take necessary steps to clear the obstruction.

CONSTRUCTION OF 11 KV LINE-

The construction of 11 KV line shall be on standard 9 mtr RCC poles with an average conductor span of about 40 mtrs. All the materials used in the line construction shall be as per the standard specified by

ESCOM and shall conform to IS specifications.	Necessary switchgear shall be provided at the sending end and receiving end at the pumping station.

FINALCHECKING,TESTINGANDCOMMISSIONING:

After completion of the works, final checking of the line shall be done by the Contractor to ensure that all the foundation works, pole erection and stringing have been done as approved by the Engineer and also that the they are complete in all respects. All the works shall be thoroughly inspected, keeping in view the following main points -

- Sufficient back filled earth is lying over each foundation pit and is adequately compacted.

- The stringing of the conductors and earth wire has been done as per the approved sag and tension chart and desired clearances are available.

- No damage, minor or major to the conductor, earth wire, accessories and insulators are noticed.

- The jumpers provided at the cut points are connected rigidly to the tension hardware utilizing all the jointing bolts provided for the purpose.

- After final checking the line shall be tested for insulation in accordance with the tests prescribed as per standards. All arrangements for such testing or any other test desired by the Engineer shall be done by the contractor and necessary labour, transport and equipment shall be provided by him. Any defects found out as a result of such test shall be rectified by the contractor forthwith.

- The contractor shall submit report to the above effect to the Engineer.

- The Contractor shall arrange for all the statutory approvals and clearances before energizing the line.

- After satisfactory tests on the line and approval by the competent authorities, the line shall be energized at full operating voltage before handing over.

RECTIFICATION OFDEFECTS DURING THE GUARANTEE PERIOD:

After commissioning and handing over of the line, the contractor shall arrange for thorough patrolling of the line during the first six months of the guarantee period so that the defects, if any noticed during that period may be rectified. During the balance period of the guarantee period, however, the contractor shall arrange for rectification of the defects, as and when pointed out by the owner.

EXECUTION OF WORKS RELATING TO POWERLINE CROSSINGS AND RAILWAY CROSSINGS:

Works such as erection of the line supports underneath an existing power line and paving out of conductors and earth and stringing the power line crossings, railway crossings will have to be done

only after receipt of approval from the concerned departments. In such cases, the contractor shall follow up with the concerned departments and arrange for the approvals early.

The contractor shall indicate in detail, the components of the material covered along with technical parameters

PUMP DUTIES:

DUTY POINT DISCHARGE:

The pump shall have to give a discharge at normal water level conditions at duty head and shall give corresponding higher discharge for the lesser heads.

DUTY POINT PUMP HEAD:

Duty point pump heads for pumps, as corresponding to normal W.L. shall be designed by the bidders.

No loss of head what-so-ever in entry, strainer, bell mouth, bowl assembly, column pipes and discharge tee is accounted for in the calculations of pump head. The bidder/manufacturer shall have to account for these losses while designing the pumps. However, head loss delivery pipe, valves fittings, rising mains and velocity head beyond discharge flange on discharge head/pumps casing are to be included. Thrust bearing loss may be declare separately by the manufacturer.

DUTY POINT EFFICIENCIES:

The Tenderer should evaluate the above efficiencies and specify the same in their offer along with calculations. The curves for both types of efficiencies viz., pump efficiency and overall efficiency for entire starting from shut off to the static head should be invariably submitted along with the offer.

HEAD RANGE AND PARALLEL OPERATIONS:

The pumps will satisfy the head requirement as per the system resistance curves, while operating in solo and in any combination, as per design requirement. The pumps should be suitable for operation in head range. The system resistance curves of the pumps shall be submitted by the bidders.

POWER MARGIN:

The pumps shall be capable of operating in the range without being overloaded at any point and keeping a margin of at least 5% of power in the motor pump over entire operating range. Requirement of power at shut off should not exceed power requirement at duty point. The pump should be capable of starting against fully closed Butterfly valve without being overloaded at any point up to valve fully open.

PUMP CHARACTERISTICS:

The pump characteristics shall be of stable nature and such that the efficiency is fairly steady for the water level variations as mentioned in the foregoing clauses. The maximum efficiency point will be nearer to the duly point and fairly constant for larger range on either side. The pumps should run smoothly from lowest head to shut off point, without cavitations and vibration (within H.L.S. limitations for vibrations). The variation in the efficiencies for any point of operation in the entire operating range should be minimum.

NPSH CONDITIONS (NET POSITIVE SUCTION HEAD CONDITIONS):

NPSH required by pumps offered by the Tenderer should be lesser by at least 0.5 meters than N.P.S.H.A. at duty point and shall not exceed the N.P.S.H. available at any point of operation in the range, with solo and parallel operations. The Tenderer shall take following values of the corresponding parameters for the purpose of calculation of N.P.S.H.A. at the site.

- Atmospheric : 9.6 Meter column of water

- Vapour pressure of water : 0.6674 Meters

(at 37.80 C Normal temperature) column f water.

SPEED:

Pump speed should be decided by the tenderers based on optimum and cost economic consideration.

SOLID HANDLING CAPACITY:

The pumps shall be suitable for pumping of raw river water containing silt coarse sand and gravel / suspended solids upto 20 mm size. Tenderer to get water analysis done and suitable preventive special alloy coating needs to be provided to the impellers and casings to avoid any damage due to abrasive material in raw water.

CLASS OF OPERATION:

The pumps shall be suitable for non-stop continuous 24 hours’ operation without interruption.

SUMP MODEL TESTING:

OBJECTIVES

The objectives of model studies is to

- ensure swirl free flow conditions at suction bell mouth of stage

- observe levels in sump along with velocity of approach

- to ensure swirl free suction condition of booster pumps (where offered by Bidder) by providing appropriate hydraulic elements. The behaviour would be studied for various operation heads.

It is obligatory on the part of the Contractor to carry out Sump Model tests at C.W.P.R.S. Pune or Indian Institute of Science Bangalore or any such reputed laboratory with prior approval of the Engineer, at his own cost and at the earliest after issue of Work Order. The Contractor must fully satisfy himself about the suitability of the proposed design and layout of the sump, to ensure vortex free and cavitations free operations of the pumps.

MODEL

The composite model shall be made to a scale of 1:10 .The suction side piping needs to be made of transparent material to enable visual inspection of flow conditions. Necessary instrument such as vortex meter for measurement of swirl conditions shall be provided along with other measuring devices/instruments. The methodology for carrying out model experiment shall be approved by the Engineer.

The sump model studies include,

- Construction of scaled model of sump chamber,

- Simulation of pump flow conditions as per site requirement and operating conditions,

- Study of flow conditions in the existing sump design conditions,

- Incorporation of recommended modifications/appurtenances in the scaled model and restudying the flow conditions and improvements,

- Preparation of report and submission and

- Suggestions of possible modifications to the existing civil structure inclusion of appurtenances in the scope of supply.

DEFINITIONS OF EFFICIENCES:

For all purpose of this contract, the various efficiencies will have the same meaning and effect as defined in the IS 1710-1972 (page 5) which are reproduced below.

BOWL EFFICIENCY:

The ratio of bowl assembly output to bowl assembly input expressed as percentage.

PUMP EFFICIENCY:

The ratio of pump output to pump input expressed as percentage.

OVERALL EFFICIENCY:

The ratio of pump output to driver input expressed as percentage.

CONSTRUCTION FEATURES FOR V.T. PUMPS:

The pump shall vertical, spindle suspended and non-pullout type. Number of stages should be decided by the tenderers. The pumps shall comprise of Bowl Assembly, line shaft enclosing tubes, line shaft bearings, line shaft bearing holders, discharge head thrust bearings, sole plates, base frames, flexible coupling etc.

1.5 A) The pump shall be self water lubricated type or

1.5 B) The pump shall be forced water lubricated type as the case may be

The pump bowl/bowls shall be flanged with machined mating faces. The bowl shall be flange joined to the discharge nozzle or suction nozzle. Bowl wearing rings be of replaceable type. The casing shall be provided with water lubricated bearings.

A Ni-Cl bell mouth shall be fitted to suction nozzle to reduce inlet velocity to 1.5 mtrs/sec. Maximum. The suction strainer shall be of galvanized MS and sufficiently strong to stand the suction pressure. Area of opening shall not be less than 2.5 times bell mouth area.

Impellers shall be enclosed type, cast in one piece and balanced both statistically and dynamically. The impellers shall be provided with wearing

ring on it. The interior surfaces and passages shall be smoothly finished to obtain the highest efficiency and shall be designed to ensure smooth operation free from any cavitation or vibrations. As raw water is being pumped, balancing holes/ devices will not be accepted for balancing the hydraulic thrust.

The pump height (i.e., impellers) should be adjustable from the top of pump head. There should be a sufficient vertical clearance between the bowl and impeller to accommodate for the line shaft elongation due to hydraulic thrust, while in operation.

The impeller shaft will not have overhung at the bottom and will be rotating in bearing support at its bottom.

The line shaft shall be solid type and will be designed to take all types of loads such as torsion, tensile and dynamic etc. Impeller shaft will have muffled coupling arrangements.

The line shafts bearing shall be water lubricated type with cutlass rubber, grooved to facilitate lubrication. Line shaft bearing shall be provided at suitable intervals to ensure that first critical speed is at least 25% more than rated speed. Suitable steel sleeves be provided to line shafts.

The line shaft protection tubes shall be provided for forced water lubrication to line shaft bearings. The line shaft protection tubes should be of heavy duty seamless steel tubes and shall withstand all mechanical and hydraulic forces exerted on it with an allowance for corrosion and wearing.

The column pipe shall be of extra heavy weight, electrical fusion welded (EFW) single longitudinal joint, or electrical resistance welded (ERW) pipes with both ends flanged, machined on surfaces, edges and spigotted to facilitate the alignment. The flanges shall have grooves to accommodate the rubber rings.

The discharge head/motor stool shall be of full dia, flanged at ends, flanged surfaces and Tee ends machined, fabricated out of MS in smooth 900 bend to have minimum loss of head in and stress relieved before machining. The pump discharge head shall be fabricated and suitably reinforced to withstand all types of static, dynamic loads, hydraulic thrust, torsional loads imposed by the pump, motor and to limit vibrations. The pump discharge head/motor stool shall house thrust bearings with cooling arrangement and contain cast iron stuffing box in which the pump top shaft shall be sealed. A sufficient opening should be provided so as to have an easy access and workability on stuffing box. Non-reverse rotation ratchet arrangement is to be provided either in pump or in motor so as to prevent the pump from rotating in reverse direction.

The column assembly shall be in standard lengths as far as possible.

The clearance between bell mouth, strainer and sump floor and nearing walls should be such that the vortex free operation is obtained. Any changes in this clearance if required other than those specified shall be clearly mentioned in the offer, with reasoning thereof.

The pump shall be subsurface discharge type with discharge-head with integrated or separate motor stools suitable for mounting in the R.C.C. floor of pump house. The construction should be such that the pump discharge head with thrust bearings, motor stool along with the motor shall be resting on the pump floor only.

Steel sole plates of adequate thickness shall be provided under the pump discharge head/pump head/motor stool, together with all necessary anchor bolts, nuts and washers to provide precise horizontal and vertical alignment. The sole plate shall be fixed on steel based frames to be anchored in R.C.C. floors. The surfaces of base frame, sole plate and base plate shall be smoothly and snugly fitted so that no vibration shall occur. The fastening of base frame to sole plate and sole plate to base of pump/motor shall be through nut bolts or headed studs.

The opening in the sole plates and the base frame shall be of sufficient dia to pass the complete bowl assembly including suction bell and strainer.

The erection and dismantling of both the pumps and motors shall be possible from the motor floor, with EOT / HOT crane available in the motor hall. The motor or the pump discharge head shall not be rested either on the pump floor or motor floor while erecting or dismantling on places other than respective base frames/sole plates. The above components should always be carried from or to the service bays directly,

while assembling, or dismantling. The contractor will be responsible to get design from the pump manufacturer and approved from ENGINEER. The steel base frames fabricated from plates together with machined bottom pieces, sole plates, all anchoring arrangement, support etc., for pump and motor mounting. These components shall be forms manufactures. The complete assembly consisting of steel base frames, sole plate, bottom pieces shall be stress relived after fabrication and before machining. Test certificate from manufacturer regarding stress reliving with observation sheets from column pipe, discharge head, base frame, motor stool etc., shall be furnished. All necessary details regarding pump and motor maintaining shall be furnished well in advance by the contractor for prior approval and to ensure necessary pocket in civil works.

Work of erection pumps, motors, including layers of foundation, grouting, shaft alignment, doweling and painting etc., shall be done by the contractor at his own cost as per general and miscellaneous specifications mentioned earlier.

The thrust bearing shall be anti friction heavy duty type. The bearing shall be designed to accommodate all possible loads under normal operations or shut of condition and shall be suitable for reverse rotation up to at least 1.5 times the normal forward speed. The bearing shall be oil lubricated type and shall be provided with oil level gauge and temperature measuring and sensing system and cooling system as given below.

One no. temperature probe suitable for dial type thermometer with dial temperature.

One no. 3 wire platinum element having DC resistance f 100 ohms at 00 C suitable for use with a digital temperature, scanner as specified in electrical section.

The cooling water supply for the pump thrust bearing if required, shall be taken from a adequate tapping from the pump discharge head or line shaft bearing lubrication (forced water). Necessary valves, strainers and non-flow sensors and annunciation system on panel board shall be provided for this cooling system. The life of thrust bearings shall not be less than 40000 hours of operation.

FORCED WATER LUBRICATION AND COOLING SYSTEM:

The forced water lubrication system for transmission bearing and supply of cooling water to pump thrust bearing and for motor cooling shall be generally as mentioned below.

Set of manual type Pressure filters along with differential pressure switches, pressure gauge built in valves etc., are to be provided to clean stream of water from main header containing fine, un-dissolved solids like sand, dust, abrasives etc. The raw water should be made to enter into the inlet of Pressure filter at sufficient pressure. The contaminant should be separated and should pass downwards and ultimately discharging out of the drain of the Pressure filter. The clean and solids free water free from the outlet of

filter should be used for the thrust bearing cooling and lubrication of line shaft/transmission rubber bearings of the V.T. Pumps and for cooling of vertical motors.

The system shall comprise of following:

One set of manual Pressure filter of adequate size for each pump shall be provided having sufficient design capacity of V.T. Pump lubrication and cooling to thrust bearing and motor cooling.

Booster pump sets complete with motor, base plate, switches and starter etc. (One working + One stand bye) suitable for group of 5 or less V.T. pumps sets shall be provided having adequate capacity in discharge and head with sufficient margin.

Suction pipe for Booster pumps with valves etc., for raw water to be taken off from the R.C.C. storage tank being provided for the purpose by the Contractor.

All Pumping valves, gauges press switches, Solenoid valves etc., shall be provided as per schematic drawing.

Electrical interlocks with suitable sensors must invariable be provided for forced water lubrication system and cooling system. The arrangement should trip the main pump motor in the event of failure of water supply from booster line to either of line shaft lubrication system thrust bearing cooling or motor cooling. The arrangement for tripping the main pump motor should be such as to allow contains time lay for the stand by booster to take over.

Automation with all relays, sensors, switch gears and solenoid valves etc., shall be provided so that if any Booster pumps trips or fails to deliver water the stand-bye set should start automatically and feed V.T. Pumps sets the lubrication and cooling system and stop the defective Booster pumps.

The water storage tank provided to initial start could be made the only source of water for feeding the booster pumps. These tanks could be continuously fed with water from the delivery system so as to keep the water level more or less constant. So, that the tank could feed the booster pump on a continuous basis. To avoid head load on pressure filtration system water to be drawn from the storage tanks at a level not lower than the middle level of the tank.

A suitable arrangement to take out the entrapped air in the pump column discharge tee shall be provided with pipe fitted in the tapping at suitable place in the pump, with valve, etc., complete the make the system work satisfactorily.

Suitable topping appropriate place shall be provided for mounting a delivery pressure gauge. The pressure gauge shall be Bourdon type and shall be provided with piping U type and tabulating socket etc. This pressure gauge shall be provided and located at operating level i.e., motor floor level. Gauge range shall

be twice the head to be measured. Drain cocks should be placed immediately below the gauged so that frequent tests could be made to determine whether pipe connections of the gauge are filled with water. The bourdon type gauge shall be fixed in such a way that no strain is placed on its case so that readings are not affected. Gauge shall be calibrated prior to after the tests and shall be fixed in upright position.

In case of emergency i.e. failure of Booster pumps of filtration system, necessary system shall be installed by the contractor for supply of raw water for lubrication of Pumps and motor by necessary tapping from pump delivery line, by passing the regular cooling/lubrication system.

MATERIALS OF CONSTRUCTION FOR V.T. PUMPS/BOOSTER PUMPS:

Bell mouth, pump bowls, suction casing	Ni-CI conforming to IS 210 grade 20 And discharge nozzle

Impellers shaft for V.T. Pumps and Booster Pumps

Stainless steel AISI SI 410

Column pipes	Mild steel IS 2062 EFW/ERW pipes

Line shaft protection tubes	Seamless MS

Flexible coupling	Forged steel conforming to IS 3495

Wearing rings for V.T. Pumps and Booster pumps

Gun metal/stainless steel as Appropriate

Column flanges	Mild steel IS 2062

Nut bolts and washers upto bottom of	Stainless steel AIST ST 304/316 Discharges lead

Line shaft	Stainless steel AISI-410

Line Shaft coupling

Line shaft bearing	Stainless steel AISI – 410

Pump shaft bearing	Thordon / Cutlass rubber

Discharge head	Cutlass rubber

BOWL	Mild Steel fabricated IS 2062

Strainer	Gun Metal

Casing of Booster Pumps	Ni-CI or galvanised steel

Pressure filters	Ni-CI conforming to IS 210 grade 20

Body and flanges Filter media

MS fabricated S304

Sealing material	Suitable design

PRESSURE FILTER:

Design Duty	50 Micron

Degree of filtration

End connections	2” NB 150

Fluid	Water

Viscosity	1 cp

Flow rate	Adequate with sufficient margin

Design pressure	Adequate

Pressure drop	0.2 kg/cm 2 (Clean condition)

Hydrants Pressure	1.5 Times of design pressure

Applicable standard	IS 2825

PUMPS STARTING/CLOSING LOGICS AND INTERLOCKS:

LOGIC OF PUMPS STARTING:

After single push button command, following operations shall take place in sequence. Taped water lubrication system/pre-lubrication starts.

After a time delay, the main pump motor will start and capacitor cubicle circuit will be ON. The delivery valve start opening.

LOGIC OF PUMP CLOSING:

The delivery valves will be closed.

After closing of valves completely, the main pump motor will STOP and capacitors cubicle circuit will be OFF. Forced water lubrication and cooling system will be closed.

INTERLOCKS:

V.T. Pumps will not start if lubrication system and cooling has not started functioning.

V.T. Pumps will not start unless valve opening command in passed on.

TESTING AND INSPECTION FOR V.T. PUMPS:

All the nos. of vertical turbine pumps proposed shall be inspected and tested at the manufacturing works

and site as below in the presence of Engineer’s representatives.

HYDROSTIATIC TEST / DYNAMIC BALANCING / DYE PENETRATION TEST FOR V.T. PUMPS:

All pumps bowl assemblies shall be subjected to Hydrostatic test at manufacturer’s works. The test pressure shall be either One and One Half times the shut off head developed by pump level assembly or twice the rated head, whichever is greater and applied for standard time.

All pumps discharge heads and columns upto 10% shall be subjected to hydrostatic test pressure as specified at (a) above.

Dynamic balancing test of impellers and impeller shafts together shall be arranged at manufacturer’s works,

which will be witnessed by engineers (as per IS 1940-1973 II)

Dye penetration test for impellers shall be arranged at manufacturer’s works, which will be witnessed by the

engineer.

PERFORMANCE TEST AT FACTORY FOR V.T. PUMPS:

All pumps shall subjected to performance test as IS 1710 of 1972 at manufacturer’s works at full load and

full speed by shifting one of electric

motors for respective pumps to be supplied under this contract as primer mover. Performance testing shall include determination of head, discharge, power demand and efficiency over a range of cutoff to shut off head.

Site conditions for minimum no positive suction head shall be simulated as near as possible for testing purpose. The tenderer shall furnish the facility available agency and place for conducting above test. The following values of parameters applicable for the site may be considered for calculation for NPSH by the contractor.

Atmospheric pressure	9.60 meters column of water Vapor pressure of water

(at 37.80 C normal temp.)	0.6674 meters column of water

OTHER INSPECTIONS AT FACTORY FOR V.T. PUMPS:

Contractor shall arrange for following inspections at manufactures works.

Inspection for critical dimensions to components viz. dia, of line shaft, dia and wall thickness of column pipe, flange thickness of column pipe, thickness of sole plate etc.

Inspection for verification of metallurgy of various components by reviewing metallurgical tests carried out by the manufacturer.

Inspection for machining or finish quality and undue wear of fast moving parts after trial runs by stripping down the machine.

Inspection for verification of test observations and reports for stress relieving of components, specified earlier in detailed specifications.

X Ray test for impeller shafts shall be arranged at Manufacturers works, which will be witnessed by Engineer.

Vibration and noise level tests

TEST REPORT AND OTHER DOCUMENTS FOR V.T. PUMPS:

Contractor shall furnish to the Engineer the following documents before dispatch of material.

Test reports for chemical analysis of materials of construction for major components like impellers, pump shaft, line shafts bowl assembly etc.

Pump performance test reports with sample calculations and actual pump performance curves and pump performance test acceptance report.

Other test and inspection reports as above. Final construction drawings of the pump.

Operation, maintenance and spare parts manual for pumps.

De-Watering Pump-

Two submersible type sludge type pump for dewatering the turbine pit shall be provided to handle water having high turbidity.

## CIVIL WORKS

### SECTION I

- EXCAVATION

  - Scope of Work

- The work to be done under these specifications consists of the excavation in various strata, and the conveyance and disposal of the excavated stuff for canals (including distributaries, laterals etc.,) for cut-off trenches of embankment, for diversion channels, drains and ditches, for the trenches of pipelining, for training of nallas, for catch water drains, for service road and inspection path and for structures. The contractor shall furnish all tools, plant, labour and materials and execute the work satisfactorily.

- When existing public facilities like road drainage, drinking water supply pipe lines, telephone lines and power lines etc. are to be disturbed for constructions activities, the contractor shall, after due approval of the Engineer, provide and maintain in satisfactory condition at his cost, temporary structure like diversion roads for ensuring un interrupted and satisfactory functioning of the facilities. Precautionary measures like signal, night lamps, fencing and barricading etc. will also be provided by him at his cost. The cost of permanent measures for the rehabilitation of the facilities, however, will be borne by the Nigam.

  - Indian Standards for Reference

- IS : 1498-1970	Classification identification of soils for general Engineering purpose.

- IS : 2720-1983	Method for test for soils (part-I to X and part XIV)

- IS : 3764-1966	Safety code for excavation work.

- Is : 4081-1967	Safety code for blasting and related drilling operations.

- IS : 4668-1967	Ammonium nitrate for explosive (Reaffirmed 1978)

- IS : 4701-1968	Code of practice for earthwork on canals.

- IS : 5441-1969	Pneumatic portable drilling machine.

- IS : 6609	Method of test for commercial blasting (part-I to V)	explosives and accessories.

- IS : 7209-1974	General requirements for blast hole drilling

rigs

- IS : 7293-1974	Safety code for working with construction

machinery.

- IS : 7632-1975	Detonators

- IS : 3696-1966	Safety code for scaffolds and ladders Part-I (part I)	Scaffolds.

- IS : 3696-1966	Safety code for scaffolds and ladders - Part II (part II)	Ladders.

  - SETTING OUT WORKS

- In the vicinity of the Canal Distributaries, temporary Bench Marks are established by the Department which the contractor shall use as control points for the entire length of the canal. The contractor shall establish sufficient number of reference Bench Marks for facilitating setting out of works and taking levels for purpose of measurements.

In setting out levels for the canals and structures, the contractor is responsible to check all levels against the Bench Mark at the head of the respective canal, with the precision specified for second order surveys.

- Before starting any work, the contractor shall erect permanent Bench Marks, reference lines and check profiles at convenient locations approved by the Engineer-in-charge. The Bench Mark shall be 20 cms. X 20 cms. X 60 cms. With 40 cm sw, embedded under firm ground and 20 cms. Projecting above ground. The word B.M. showing value of R.L. shall be conspicuously pointed on the Bench Marks. The reference line shall comprise the base line properly dog belled on the ground with the numbered concrete masonry pillars, suitably spaced.

- The check profiles shall be located 30 meters apart or closer as directed by the Engineer-in-charge so as to ensure execution of all slopes, steps and elevation, to the profile or profiles indicated in the approved drawings. All important levels and all control points with respect to Bench Marks and reference lines shall be fixed and got correlated by the Engineer-in-charge.

- All materials and labour for setting out works including construction of Bench Marks, reference line, check profiles and surveys, as may be required at the various stages of constructions, shall be supplied by the contractor at his cost. The cost of such work shall be deemed to have been included in the costs of the items in the schedule - B.

  - PREPARATION OF SITE

    - CLEARING THE SITE

- The contractor shall clear the entire area, required for setting out, of all tree stumps, roots, brush wood, rubbish of all kinds, loose stones and all other objectionable materials. The ownership of the useful materials so removed from clearing site and / or excavation shall rest with the Nigam. Cutting of trees, covered under this item shall not be resorted to without the permission of the Engineer-in- charge. The contractor shall remove all the stumps and roots of trees for which no additional payment will be made. The roots of trees shall be grubbed to a depth of 100 cms. The contractors shall dispose off all such materials as directed by the Engineer-in-charge.

- No separate payment will be made to the contractor for complying the requirements of this paragraph and all cost shall be deemed to have been included in the rates quoted in schedule-B for the items of excavation.

    - STRIPPING

Before commencing the excavation for canal, the stripping shall be carried out as specified in para

2.3 of section - II. Measurement and Payment shall be as mentioned in para 2.3 of section II.

  - RECORDING OF CROSS SECTIONS

- After clearing the site prior to the beginning of excavation, initial cross sections of existing ground shall be taken at every 5 mtrs. interval or closer, depending on the nature of ground, normal to axis of canal up to sufficient distance outside the limits of the work. Levels on these cross sections shall be taken at 5 mtrs. or closer intervals for canal works, while for structure works, they shall be taken at 3 mtrs. or closer intervals as directed by Engineer-in-charge and entered in the field books by the Engineer-in-charge in the presence of the contractor or his authorised agent if he so desires and these shall be binding on the contractor. The contractor or his authorized agent shall sign the field book in token of acceptance. These cross sections shall form the basis of all future measurements and payments. The original cross sections duly signed by the contractor and the Engineer-in-charge shall be preserved.

- No separate payment will be made to the contractor for the labour and materials required for taking the cross sections.

  - PLANNING

Prior to the commencement of the work, all relevant data shall be collected by the contractor for planning (i) the excavation, (ii) the disposal of the useful materials of the excavation and (iii) the disposal of the remaining excavated stuff. He shall prepare drawings showing therein the location and quantities of

excavation and bank work in different kinds of material and the location of canal structures along with their requirement of rubble, broken stone, filing around foundations etc. based on the data, a scheme for disposal of the excavated materials shall be evolved and shown in the same drawing. If within the reach, there is a surplus of useful excavated material the disposal of the same in separate heaps/stacks for being used in other reaches in the neighborhood may also be though of and provided for in the scheme. The drawing shall be submitted to the Engineer within 15 days before starting the work and got approved.

  - DRILLING AND BLASTING

- GENERAL:

Blasting where required will be permitted only when proper precautions have been taken for the protection of persons and property in accordance with IS : 4081-1967 (Indian Standard specification for the safety code for blasting and related drilling operations). While carrying out excavation, adequate precautions in accordance with IS : 3764-1966 (Indian Standard specifications for safety code for excavation work) shall be taken.

- EXPLOSIVES

It shall be the responsibility of the contractor to procure the explosives required for the work.

- EXPLOSIVES AND BLASTING

The contractor shall acquaint himself with the applicable laws and regulations concerning acquiring, storing, handling and the use of explosives. All such laws, regulations and rules, as prevalent from time to time shall be binding upon the contractor.

The provisions detailed in the specifications are supplementary to the above laws and regulations and are also applicable except where they conflict with the aforementioned laws, from time to time. Further, the Engineer-in-charge may issue modifications, alterations and new instructions from time to time. The contractor shall comply with the same without these being made a cause for any claims.

- MATERIALS

All the materials such as explosives, detonators, fuse coils, tamping materials etc., that are proposed to be used in the blasting operations shall have the prior approval of the Engineer-in-charge. Only explosives of required make and strength are to be used.

Black powder and safe explosive (as commonly current in India) shall be used wherever possible. Explosives with nitro-glycerine shall be used where the above explosives are not effective.

The use of fuse with only one protective coat is prohibited. The fuse shall be sufficiently water resistant as to be unaffected when immersed in water for thirty minutes. Rate of burning of the fuse shall be uniform and not less than 4 seconds per 25 millimeters of length with 10% tolerance on either side. The fuse known as instantaneous fuse shall not be used.

Before use, the fuse shall be inspected and moist, damaged or broken once discarded. The rate of burning of all new types of fuses or when they have been in stock for long shall be tested before use. The detonators used shall be capable of giving an effective blasting of the explosives.

- PERSONNEL

Excavation by blasting will be permitted only under the personal supervision of competent and licensed persons and trained workmen employed by the contractor at his cost. All supervisors and workmen in- charge of make up, handling, storage and blasting work shall be adequately insured by the contractor.

The storage shall be in-charge of a very reliable person approved by the Engineer-in-charge, who may, if necessary cause police enquiry being made as to his reliability, antecedent etc. the contractor shall have to produce security for the person-in-charge of the explosives, if and required by the Engineer-in-charge or the civil authorities of the District.

The contractor shall make sure that his supervisor workmen are fully ; conversant with all the rules to be observed in storing, handling and use of the explosives. It shall be assured that the supervisor-in-charge is thoroughly acquainted with all the details of the handling and the blasting operations.

- EXPLOSIVES

The location and design of stores for explosives, method of their transport and general precautions to be taken by the contractor to prevent accident shall be in accordance with the provisions of Indian Explosive Act and the regulations and rules framed there under.

The contractor shall provide portable magazine for storing the explosive at work spot. The site of the portable magazine shall be subject to approval by the Engineer-in-charge and the Inspector of Explosives.

A careful and day to day account of the use of explosives shall be kept by the contractor in register in a manner approved by the Engineer-in-charge. The Engineer-in-charge may also pay surprise visits to the storage magazine. In case of any unaccountable storage of the explosives, or if the account is not found to have been maintained in a manner approved by the Engineer-in-charge, the contractor shall be liable to be penalized in which case, he shall not be entitled to any compensation for the losses etc. The action taken under this clause shall be in addition to that which might be taken by the competent civil authorities in the court of Law.

- USE OF EXPLOSIVES

For the transport of the explosives and detonators between the store and the site, closed and strong containers made of soft materials such as timber, zinc, copper, leather shall be used.

Explosives and detonators shall be carried in separate boxes. For the conveyance of primer, special container shall be used.

The boxes and containers used, shall be kept closed. Explosive shall be stored and used chronologically to ensure the ones revived earlier being used first. A makeup house shall be provided at each working place in which cartridges will be made up by competent and licensed men as required for the work. The make up house shall be separated from other buildings. Only electric storage lamps will be used in this house.

No smoking shall be allowed in the make up house or generally while dealing with explosives.

- DISPOSAL OF DETERIORATED EXPLOSIVES

All deteriorated explosives shall be disposed off in an approved manner, the quantity of deteriorated explosives to be disposed off shall be intimated to the Engineer-in-charge prior to its disposal.

- PREPARATION OF PRIMERS

The primers shall not be prepared near open flames or fire. The work of preparation of primers shall always be entrusted to the same personnel. Primers shall be used as early as possible after they are ready.

- CHARGING OF HOLES

The work of charging of holes shall not commence before all the drilling work at the site is completed and the contractor's supervisor satisfies himself to that effect by actual inspection. While charging open lamps shall be kept away. For charging with powered explosives, naked flame shall not be allowed. Only wooden tamping rods without any kind of metal on the rod shall be allowed to be used. The tamping rods shall have cylindrical ends. Bore hole must be of such size that the cartridges can easily pass down them, they shall not however be too big.

Only one cartridge shall be inserted at a time and gently pressed into the hole with the tamping rods. The sand clay or other tamping materials used for filling the holes completely shall not be tamped too hard.

- BLASTING

Blasting shall be carried out during fixed hours of the day which shall have the approval of the Engineer-in- charge. The hours once fixed shall not be altered without prior written approval of the Engineer-in-charge. The site of blasting operations shall be prominently demarcated by red danger flags. The order to fire shall

be given only by the contractor's supervisor-in-charge of the work and this order shall be given only after giving the warning signal three times, so as to enable all the labour, watchman etc. to reach safe shelters.

A whistle/bugle with distinctive note shall be used to give warning signals. The bugle shall not be used for any other purposes. All the labour shall be made acquainted with the sound of the bugles and shall be strictly warned to leave their work immediately at the first warning signal and to move for safe shelters. They are not to leave the shelters until the all clear signal has been given.

All the roads and footpaths leading to the blasting area shall be watched.

In special cases, suitable extra precautions shall be taken. The Engineer-in-charge may however permit blasting for underground excavation, without restriction of fixed time, provided that he is satisfied that proper precautions are taken to give sufficient warning to all concerned and that the work of other agencies on the site is not hampered For lighting the fuse, a lamp with a strong name such as carbide lamp shall be used.

The contractor's supervisor shall watch the required time for the firing of the fuses and shall see that all the workmen are under safe shelters in good time.

- ELECTRICAL FIRING.

Only the contractor's supervisor in-charge shall possess key of the exploder an short firing accessories and he shall keep it always with himself. Special apparatus shall be used as a source of current for the blasting operations, power lines shall not be tapped for the purpose.

The detonators shall be checked before use For blast in series, only detonators of the same manufacture of the same group of electrical resistance shall be used.

Such of the electrical lines as could constitute danger for work of charging shall be removed from the site.

The firing cables shall have a proper insulating cover so as to avoid short circuiting due to contact with water and metallic parts of rock.

The use of the earth as a return line shall not be permitted.

The firing cables shall be connected to source of current only when nobody is in the area of blasting. Before firing, the circuit shall be checked by a suitable apparatus. After firing whether with or without an actual blast the contact between the firing cable and the source of current shall be cut off before any one is allowed to the leave the shelters.

During storms, charging with electrical detonators shall be suspended. The charges already placed in the holes shall be blasted as quickly as possible but taking all the safety precautions, and giving necessary warning signals. If this is not possible the site shall be abandoned till the storm has passed.

- PRECAUTIONS AFTER BLASTING

After the blast, the contractor's supervisor must carefully inspect the work and satisfy himself that all the charges have exploded. After the blast has taken place in underground works, workmen shall not be allowed to go to the place till all the toxic gasses are evacuated from the place.

- MISFIRES

If it is suspected that part of the blast has failed to fire or is delayed, sufficient time shall be allowed to elapse before entering the danger zone.

When fuse and blasting caps are used a safe time should be allowed and then the contractor's supervisor alone shall leave the shelter to see the misfire.

None of the drillers are to work near this hole until one of the two following operations have been carried out by the supervisor.

Either (i) the supervisor should very carefully (when the tamping is on damp clay) extract the tamping with a wooden scraper or jet of water or compressed air (using pipe of soft materials) and withdraw the fuse with the primer and detonator attached after which a fresh primer and detonator with fuse should be placed in this hole and fired out or

(ii) the hole may be cleared of 300 mm. of capping and the direction then be ascertained by placing stick in the hole. Another hole may be drilled at least 225mm. away and parallel to it.

This hole should then be charged and fired. The balance of the cartridge and detonators found in the muck shall be removed.

Before leaving his work, the contractor's supervisor inform the supervisor of the relieving shift of any case of misfires and should point out the position with red cross denoting the same, also stating what action if any, he has taken in the matter.

A register of misfires and their location and how they were dealt with shall be maintained by the contractor.

The contractor's supervisor should also at once report at the contractor's office all cases of misfires, the cause of the same and what steps were taken in connection therewith.

The names of the day and night shift supervisors of the contractor must be noted daily in the contractor's office.

If misfire has been found to be due to a defective detonator, or dynamite, the contractor's office for inspection and shall be disposed off.

Drilling in holes not completely exploded by blasting shall not be permitted for underground excavation The contractor should produce the firer's license and furnish the particulars in the following statement :

Sl. No.	Name	No. of firer's License & Date	Validity period

- SAFETY OF PUBLIC AND PROPERTY

Blasting operation, when considered necessary shall be resorted to only with the written permission of the Engineer-in-charge. Prior inspection shall be carried out for the safety and stability of the public and property. Blasting operations in the proximity of over head power lines, communication lines, utility lines or other structures shall not be carried on until the operator or the owner or both of such lines have been notified and precautionary measures deemed necessary have been taken.

The drilling pattern, the method of blasting, the charge per hole, the finishing order etc., shall also be suitably designed to the satisfaction of the Engineer.

- CONTROLLED BLASTING

  - The objectives of controlled blasting techniques include

    - Minimization of over breaks and or fracturing of rock beyond the designed boundary of excavation so as to achieve smooth post blast surface for the canal and a sound foundation for the canal structure.

    - Control of fly rock and or ground vibration within permissible limits and

    - To serve both the above purposes.

  - TECHNIQUES FOR MINIMISING ROCK DAMAGE.

The main purpose of controlled blasting is to minimize fracturing and loosening of the rock mass beyond the predetermined excavation line / profile. The objective is normally achieved by minimizing and judicious use of explosives in the blast holes. Several controlled blasting techniques such as line drilling, pre splitting, smooth blasting, cushion blasting and buffer blasting are used to achieve the objective.

LINE DRILLING :

The line drilling ; may be one of the technique used for over break control. In line drilling, a single row of closely spaced, unloaded, small diameter holes is drilled along the neat excavation line. This provides a plane of weakness to which the primary blast can break and to some extent reflects the shock waves created by the blast, reducing the shattering and stressing in the finished wall. Line drilling is best suited to homogenous formations where bedding planes, joints and seams are at a minimum.

Line drilling has very limited application. The only place where it is applicable is in areas where even in the light explosive loads associated with other controlled blasting techniques may cause damage beyond the excavation limit, or where line drilling is used between loaded holes to promoted shearing and guide the pre-split line.

PRESPLITTING

Pre-splitting involves a single row of holes drilled along the excavation line. Pre-spilt in the rock forms a discontinuous zone which minimizes or eliminates over break from the subsequent primary blast and produces a smooth, finished rock wall. Pre-splitting is also used to reduce ground vibration in some critical cases.

SMOOTH BLASTING

Smooth blasting is sometimes referred to as contour blasting, perimeter blasting, or sculpture blasting. This method is widely accepted method for controlling over break in canal, underground headings and slopes. In smooth blasting the holes are drilled along the excavation limits, lightly loaded with well distributed charges and fired after the main excavation is removed. By firing instantaneously or with minimum delay between the holes, a shearing action is obtained which gives smooth walls with minimum over break.

Smooth blasting, presplitting etc., techniques differ mainly from the line drilling principle in that some or all of the holes are loaded with relatively light, well distributed charges of explosives. The fact that the firing of these charges tends to crack or split the rock between the holes permits wider hole spacings than when line drilling. Consequently drilling costs are reduced and in many cases better control of over break is obtained. However in the case of presplitting, it is difficult to determine results until excavation of the primary blast is complete to the finished wall.

CUSHION BLASTING :

Cushion blasting is sometimes referred to as trimming, slabing or slashing, line smooth wall blasting, a single row of holes is drilled along the excavation line, loaded with light, well distributed charges, and fired

after the main excavation is removed. In cushion blasting, the charged holes are further decoupled by reducing the diameter or using stemming materials of crushed stone or sand to provided cushioning effect. This cushions shock from the finished wall as the holes are detonated and minimizes, the stresses and fractures in the finished wall. This technique is rarely used today because the reduction in decoupling could be achieved by the use of small diameter explosive cartridges which serves the same purpose. The holes are blasted using the last delay number in the same blasting round preferably with jumping delay of 50 Ms.

The suitable parameters for controlled blasting for minimizing rock damage shall be established through trial blasts. Usually it needs to establish the optimum hole spacings and the charge per hole. Slopes of the canals are designed and prescribed by the Engineer in accordance with the geology of the rock. The controlled blasting methods shall be such as would enable maintain the prescribed slope.

  - GROUND VIBRATION CONTROL TECHNIQUE

When an explosive charge is detonated inside a blast hole it is instantly converted into hot gases and the expanding gases exert intense pressure on the blast hole walls. A high intensity shock wave travels through the rock mass which attenuates sharply with distance. Simultaneously the rock around the blast hole up to twice the radius of the original hole gets completely crushed. Expanding gases continue to work on the rock, extending the cracks and moving the rock outward and upward. These activities consume a major part of the explosive energy. However a small left over portion passes beyond the zone of intended work in the form of elastic ground vibrations. As seismic waves travel through the rock mass, they generate particle motions which are termed as ground vibrations. The velocity of oscillation of rock particles is called "particle velocity" and its maximum value is called "peak particle velocity (PPV) "Internationally, peak particle velocity is used to express the intensity of ground vibrations from blasting. Damage caused by ground vibration is dependent on the ground velocity and on the frequency of the ground motion. Even though, the use of explosives has unwanted side effect in the form of vibration, explosive provide an inexpensive source of energy for rock excavation in mining and civil engineering projects.

The principal factors that effect vibration level at a given point of interest are the maximum charge per delay, the distance from the blast, the delay period used and the blast geometry.

SAFE LIMITS OF VIBRATION :

The permissible peak velocity (mm/s) at the foundation level of structures is as follows :

Type of structures	Dominant excitation frequency, Hz

<8 Hz	8.25 Hz	>25 Hz

- Building/structures not belonging to the owner

| (i) | Domestic houses / structures | 5 | 10 | 15 |
| --- | --- | --- | --- | --- |
|  | (Kutcha, Brick and Cement) |  |  |  |
| (ii) | Industrial Buildings | 10 | 20 | 25 |
|  | (R.C.C. & framed structures) |  |  |  |
| (iii) | Objects of historical importance & | 2 | 5 | 10 |
|  | sensitive structures |  |  |  |
| (b) | Buildings belonging to the owner with |  |  |  |
|  | limited span of life |  |  |  |
| (i) | Domestic houses / structures | 10 | 15 | 25 |
|  | (Kutcha, Brick and cement) |  |  |  |
| (ii) | Industrial Buildings | 15 | 25 | 50 |
|  | (R.C.C. & Framed Structures) |  |  |  |

VIBRATION CONTROL PROCEDURES

  - The most common method of controlling ground vibration is by minimizing the charge weight per delay. Delay blasting permits to divide total charge into smaller charges which are detonated in a predetermined sequence at specified intervals. Blasting without delay or sufficient delay numbers increases ground vibrations due to increases in maximum charge per delay.

  - Vibration can be significantly reduced by optimizing blast design parameters. The contractor shall establish optimum burden, hole spacing, powder factor and hook up to control vibration in the vicinity of the existing structures.

  - FLY ROCK CONTROL TECHNIQUES

The rock fragments ejected from the blast called "fly rock" is a serious hazard of blasting operations, particularly when the blast is conducted in the vicinity of village and structures. The factors which influence the fly rock distance include.

- Height of stemming column in the blast holes and type / quality of stemming materials.

- Irregular shape of free face

- Excessive large burden or blasting without free face

- Muffling of the blast area and the muffling material type

- Scattering and overlapping of delay timings of the delay detonators/relays.

- Presence of water in blast holes.

The first four parameters can be controlled by properly designing the blasting pattern whereas the last two parameters are not easily controllable.

Fly rock shall be controlled by proper blast design and by muffling / covering. From the experience it is found that unless blast design is proper, muffling will not be effective. Proper blast design and accurate implementation of the blast are the two areas of fundamental concern for controlling the fly rock. The third important parameter is understand the local geology and adjusting the explosive charge with regard to the geological features.

The reliable and effective method of controlling fly rock fragments from the mouth of the blast holes (vertical fly rock on the rear side) is he height of stemming column. It has been observed that the fly rock, particularly towards and rear side, was effectively controlled by maintaining the height of stemming column in all holes greater than the burden. The height of stemming column should be 1.2 to 1.5 times the true burden in all holes.

A good stemming material should retain bore hole pressure till the burden rock starts to move. Dry angular materials under the effect of the impulsive gas pressure tends to form a compaction arch which locks into the wall of a blast hole, thus increases its resistance to ejection. In general drill cutting is better stemming material as compared to sand and should be preferred except in case of watery holes. In case of watery holes only sand free of clayey materials should be used as stemming material.

If fly rock is originating from the face and flying far distance, it could be an indication that too little burden is used or that mud seams or other geological discontinuity are prevalent. Most fly rock however, is not produced from the face., It is produced from the top.

When the fly rock towards the face side is also to be contained, the blasting should be done using the technique of buffer blasting along with muffling. Buffer blasting is a technique in with in a buffer of blasted rock of 4 to 6m thick should be left against the next round of blast.

Muffling or covering of holes including entire area to be blasted is one of the most common method to contain the distance of travel of flying fragments particularly when blasting is done within the danger zone as specified by DGMS.

In mining blasts, the most common practice is cover the blast using wire mesh of 50 mm x 50 mm to 75 mm x 75 mm. Gunny bags and cartridge empty boxes 4 to 5 numbers are filled with sand or drill cutting and place over the wire mesh. Sometimes the entire area to be blasted is covered by old belt conveyors over

the wire net which was found to be more effective as compared to wire nets alone. Gunny bags filled with sand, free of pebbles, weighing at least 30 to 40 kg are placed over the belt conveyor which is placed over the wire nets at an interval of 2 in between and within the rows. This method will contain the vertical fly to a great extent.

Flying fragments is excessive when blasting is done in shallow holes and where bench height or hole depth is less than two times the burden. Therefore for controlling fly rock, the bench height must be greater than two times the true burden and preferable three times the burden. The fly rock is also excessive in watery holes.

The contractor shall establish by trial blasting suitable technique for the control of fly rocks wherever necessary. The technique adopted shall be got approved from the Engineer. For excavation within the danger zone specified by DGMS, the prior approval of the blasting methods shall be obtained from the chief Inspector or Regional Inspector authorized under the Mines Act 1952 (35 of 1952) as per the statutory requirements.

  - ALL ITEMS OF ROCK EXCAVATION RATES TO INCLUDE COST OF CONTROLLED BLASTING FOR MINIMISING ROCK DAMAGE.

  - CLASSIFICATION OF EXCAVATED MATERIALS.

    - CLASSIFICATION

All materials of excavation shall be classified by the Engineer-in-charge in the following groups.

- SOIL

This shall include the following :

  - Ordinary soils, viz. vegetable or organic soil, turf, sand, silt, loam clay, mud, peat, black cotton soil, soft shale, loose murrum, a mixture of all these and similar materials which yield to the ordinary application of pick and shovel rake or other ordinary digging implement. Removal of gravel or any other nodular material having diameter in any one direction not exceeding 75 mm. occurring in such strata shall be deemed to be covered under this category.

  - Hard soils viz. stiff/heavy clay, soft shale, or compact murrum requiring grafting tool or pick or both shovel, closely applied.

  - Gravel, cobble stone, soft laterite, kanker and boulders having maximum diameter in any one direction up to 300 mm.

  - Soft conglomerate, where in stones may be detached form the matrix with picks ;

  - Soling of roads, water bound macadam layers, asphalted roads.

  - Lime concrete and stone masonry in lime mortar or in lean cement mortar.

  - Marshy soil excavated below the original ground level of marshers and swamps and soils excavated from other areas requiring continuous pumping or bailing of water.

  - Generally any material which requires the close application of picks, or scarifies to loosen and not affording resistance to digging greater than any item mentioned in (I) to (VII) above

- SOFT ROCK WITH OR WITHOUT BLASTING

This shall include

- Highly disintegrated granite, trap or lime stone where the rock material is completely disintegrated except for a few un weathered rock fragments.

- Sand stone, hard literate, laminated limestone, heavily jointed trap, breccia, red bole, hard shale, hard conglomerate and moderately to highly weathered granite.

- Closely jointed fissured and fractured hard rocks.

- Un reinforced cement concrete beds of lean proportions up to and including C.C. 1:3:6 and stone masonry in C. M. 1: 3 or of richer mix laying below ground level.

- Generally any material or combination of materials which requires excavating efforts similar to excavation of items (i) to (iv) above.

Soft rocks are of such hardness that they cannot be excavated by picks and hand shovels. They may be either (a) quarried or split with crow bars, or (b) excavated by drilling and blasting, depending upon jointing pattern, the degree of weathering and moisture content.

- HARDROCK WITH BLASTING / CONTROLLED BLASTING

This shall include

- Massive and sheet rock formations of lime stone, granite, quartzite, trap, dolerite and pegmatite

- Slightly weathered to fresh hard rock formation of solid rock of trap, lime stone, granite and quartzite &dolerite pegmatite, gneiss and any other hard rock formation

- The hard rock boulders of size more than 520mm (0.14 cum) requiring blasting for removal surrounded by sand or by soft material.

- C. C. of 1: 2: 4 proportion or of richer proportion and R. C. C.

- Any material requiring excavating efforts similar to items i) to iv) above

    - Under the hard rock, there may be one more classification for the purpose of measurements and payments, when the schedule - B provides for an item of payment for controlled blasting to control fly rock and vibrations vide para 1.7 (xvi) above.

1.8.3. AUTHORITY FOR CLASSIFICATIONS

The classification of excavation shall be decided by the Engineer-in-charge and his decision shall be final and binding on the contractor. Merely the use of explosives in excavation will not be considered as a reason for higher classification unless blasting is clearly necessary in the opinion of the Engineer-in-charge.

The excavated materials from hard rock shall be stacked on the site as directed by the Engineer-in-charge for facilitating measurements. The stacks shall be measured and 40% deducted for voids. The quantity arrived at by section measurement shall be verified with the quantities of stacks. In special circumstances, stacking may be dispensed with, with the prior approval of the Chief Engineer in which case suitable deduction towards the stacking charges will be made based on the current schedule of rate. When stacking is waived by Chief Engineer, the cost of rubble also would be recovered.

  - EXCAVATION FOR CANAL

    - GENERAL

- Excavation for canals in rock shall be to the underside of the lining shown on the drawings. Excavation for canals in materials other than rock shall be left 200mm. above the underside of the concrete lining until immediately before placing the concrete lining. Before placing the concrete lining the sub-grade shall be wetted if necessary and compacted at optimum moisture content and carefully excavated to the underside of the grade M15 concrete lining. The employer reserves the right, during the progress of the work, to vary slopes of excavation and the dimensions dependent thereon.

- Blasting shall be done in such a manner so as not to cause over breakage which in the opinion of the Engineer-in-charge is excessive. Special care shall be taken to prevent over-breakage or loosening of material on bottom and side slopes against which concrete lining is to be placed. To achieve this techniques for minimizing rock damage as specified in para 1.7 (xvi) shall be followed for the sides and bed of canal. The smooth blasting shall e such that on the finished surface at least 50% of the drill hole surfaces could be seen. If satisfactory rock surface is not obtained through controlled blasting the final cutting may be by chiseling or with the help of pavement breakers. All these operations shall be carried out at contractor's cost without any claim for separate payment.

If excavation is required to be done within 50 meters from existing transmission / power lines or 300 meters from village limits and if it is not considered expedient by the department to shift the power lines or the

village to safer distances or otherwise extend protection, the excavation shall be carried out with extra care to control vibrations and fly rocks as specified in paras 1.7. xvi(3) and 1.7 xvi(4) and the payment are regulated as in para 1.7xvi(6).

- Except the areas of rock, all areas to be excavated for canal sections shall be pre wetted so that at the time of excavation moisture content shall be about optimum. However, in case the excavated materials from canal is not to be used for embankment, such pre wetting need not be done.

- The contractor shall not be entitled to any additional rate above the rates quoted in schedule-B on account of the requirement for allowing additional time for drying, stockpiling and re handling the excavated material which have been deposited temporarily and stock-piled for re-use.

    - CONVEYANCE AND DISPOSAL OF EXCAVATED MATERIALS

The usable excavated material available from the canal excavation shall be used in the appropriate zone of the canal embankment by conveying the same with all leads and lifts. Lead charges for 50 mtrs., are included in the excavation items and the additional lead charges, if any, shall be included in the respective items of embankment. If usable excavation material is in excess of the requirements of banking the same shall be used for the construction of approaches to the road bridges and for selected bedding materials and backfill around structures for which payment will be made at the rates entered in schedule-B, remaining material from the excavation shall be used to strengthen the embankment on either side of canal, or deposited in low areas on either side of canal to backfill borrow pits or spread in other approved location as directed by the Engineer-in-charge. Usable rubble available from hard rock excavation shall be sorted out and arranged in separate regular stacks without any extra charges as and where directed by the Engineer- in-charge. The balance excavated stuff will be deposited in spoil banks. The spoil banks shall not be constructed continuous. A gap of 10m., shall be provided at 150m., interval. Spoil banks shall not be allowed within 30 m., on either side of the structure on both the banks of canal unless otherwise directed by the Engineer-in-charge.

    - DEWATERING CANAL TRENCHES AND EXCAVATION UNDER WET CONDITIONS

Water encountered in canal excavation shall be diverted to nearby drain and nalas by cutting an open channel within the canal section to be excavated. When the drain / nalla bed is higher than the encountered water level this water shall be evacuated into the nalla by pumping and no separate payment will be made for dewatering by pumping. No distinction shall be made in payment whether the material being excavated is dry, moist or wet. Removal of accumulated silt, slush and dewatering shall be done by the contractor, without any extra cost till the work is finally handed over to the Department or till the expiry of the contract period, whichever is earlier.

    - OVER EXCAVATION

Over excavation caused by the contractor beyond the limits shown in the drawings for any purpose or reason, except as directed by the Engineer-in-charge shall not be measured and paid for. The over excavation shall be rectified at the expense of the contractor by filling and compacting with suitable soil in the case of excavation in soils. The over excavation in rock of canal bed and side slopes shall be back filled with cement concrete 1: 5 : 10, if the over excavation is within 15 cms and with U.C.R. masonry in C.M. 1 :

5 proportion, if the over excavation is more than 15 cms. The over excavations in case of canal embankment should be filled with respective materials excavated and should be compacted. The cost of back filling the over excavation will be considered as included in the rate quoted for excavation items and no separate payment will be made for this.

    - TOLERANCE IN ALIGNMENT AND GRADE

Departure from established alignment : + 20 mm on straight section.

+ 50mm on tangents.

+ I 00 mm on curves.

Departure from established grade ;	+ 20 mm

    - PAY LINE

- Pay line is the limit of excavation as required by design without any allowances for over breaks. The canal shall be excavated as indicated on drawing or as directed by the Engineer-in-charge excavation.

- In case of changes in canal section and side slopes, the contractor shall carry out work at the rates quoted for the item without claiming any extra rate because of these changes. Modifications in the slopes prescribed will however, be intimated to the contractor in writing by the Engineer-in-charge.

    - MEASUREMENT AND PAYMENT

Payment as per payment schedule on percentage basis.

  - EXCAVATION FOR STRUCTURES

    - GENERAL

- The foundation levels shown on the plans accompanying the tenders or in the detailed drawings furnished at the commencement of work are tentative and the actual levels will be decided by the Engineer- in-charge on the basis of actual site conditions revealed after opening of the foundation.

- Blasting shall be done in such a manner as not to cause over breakage which in the opinion for the Engineer-in-charge is excessive. Special care shall be taken to prevent over breakage or loosening of material on bottom and side slopes against which concrete is to be placed. To achieve this technique for minimizing rock damages as specified in para 1.7.xvi (2) shall be followed on the sides and if found necessary the final cutting in foundation bed shall be carried out by chiseling or with the help of pneumatic pavement breakers for which no extra rate will be payable. If excavation is required to be done within 30 mtrs., from an existing structure, 50 mtrs., from power transmission lines, or 300 mtrs., from the village, limits the same shall be carried out by controlled blasting, to control vibration and fly rocks as specified in para 1.7 xvi. The method of drilling and blasting shall be to the approval of the Engineer-in-charge.

- The quantities to be paid will be to the dimensions shown on the drawings or instructed in writing by the Engineer-in-charge.

- The recommended side slopes for pay lines are considered safe without shoring and strutting. However, if necessary arises the contractor shall provide shoring and struting without extra costs.

- Whenever water is met with during excavation for structures, dewatering shall be resorted to by the contractor. The rate for the excavation for structures includes the cost of dewatering and desilting. No extra claim for dewatering and desilting will be entertained.

- Usable material removed from the excavation for structures shall be used for backfill and embankment, otherwise it shall be disposed of as directed by the Engineer-in-charge.

    - OVER EXCAVATION.

(a) Over excavation performed by the contractor beyond the limits shown on the drawings for any purpose or reason, except as directed by the Engineer-in-charge shall not be measured. The over excavation in the bed shall be rectified at the expense of the contractor by filling back with same grade of concrete as that specified for leveling course. In the case of over excavation of the sides, the same shall be filled back with suitable soil at the expense of contractor to the same specification as that for the item of back filling in foundation trenches.

    - PAY LINE

- Regardless of whether the excavation for construction of any structure precedes or follows the excavation of the canal at the site of structure, measurement for excavation for structures shall include only the required excavation outside the pay lines for the canal excavations and below the original ground surface, measured to the dimensions and slopes specified below:

| Sl. No. | Strata of Excavation | Slope for pay line |
| --- | --- | --- |
| 1. | Soil, murrum | 1 to 1 |
| 2. | Soft rock | 0.5 to 1 |
| 3. | Hard rock | 0.25 to 1 |

- The pay line for excavations of foundations of structures, shall be determined from the bottom edge of the foundations based on the slopes given in sub para (a) above. alternatively, steeper slopes can be retained by providing shoring and strutting for which no separate payment will be made. In all cases payment will be regulated for the slopes as mentioned in the sub-para (a) above.

    - MEASUREMENT AND PAYMENT

Measurement and Payment as per payment schedule.

(a)  The rates for excavation include all excavation clearing of site, all leads and all lifts, disposal of excavated stuff/material as per the specifications, providing all tools, plants, machinery, material, preparation and maintenance of haul roads, transport material to temporary stockpiles, rehandling of excavated material temporarily deposited in stockpiles to disposal areas or points of final use, disposal of excavated waste materials, maintaining excavated slopes and trenches including dewatering and desilting, diverting surfaces flows etc., the cost of sorting and stacking useful excavated material above high flood levels and all incidental operations required for carrying out the work in accordance with the specifications.

  - SLIPS

Slips shall be avoided but if any slip occurs in account of nature of soil or due to failure of slopes in the opinion of the Engineer-in-charge, extra excavation shall be done as directed by the Engineer-in-charge to restore stability. In such case payment for necessary excavation and back filling will be made for this extra work under relevant items.

  - MONSOON DAMAGE

Damages due to rain or flood either in cutting or in banks shall be repaired by the contractor till the final section is handed over to the department. The responsibility of desilting and repairing damages due to rain or flood rests with the contractor. No extra cost is payable for such operation and the contractor shall take all necessary precautions to protect the work done during the construction and prescribed maintenance period.

  - MEASUREMENTS FOR PAYMENT

Payment	as	per	payment	schedule

### SECTION II

##### EMBANKMENT

  - SCOPE OF WORK

- The work to be done under these specification consists of all canal embankments, rock fill embankments, CNS layers backfilling of cut-off trench, earth work for approaches to the road bridges, dyke embankment for nalas/drains, back filling around the canal structures rock toe and filters of different type and sizes. The contractor shall furnish all materials, tools and plants, labour and execute the work satisfactorily.

##### INDIAN STANDARDS FOR REFERENCE

- IS : 1888-1971	Method of load test on soils

- IS : 2131-1963	Method for standard penetration test for soils.

- IS : 2809-1972	Glossary of terms and symbols relating to soil Engineering.

- IS : 4332-1967	Method of sampling and preparation of

(Part-I) (reaffirmed stabilized soils for testing 1978)

- IS : 4558-1983	Code of practice for under-drainage of lined canals

- IS : 5529-1969	Method of test for in-situ permeability test,

code of practice for Part-I is over burden.

- IS : 7894-1975	Code of practice for stability analysis of earthen dams

- IS : 8237-1976	Code of practice for protection of slope for

reservoir embankments

- IS : 8414-1977	Guidelines for design of under seepage control

measures for earth and rock fill dams.

- IS : 8419-1977	Filtration media - sand and gravel. (part I)

- IS : 8826-1978	Guidelines for design of large earth and rock fill dams

In addition to the above, Indian Standards mentioned under para 1.2 of section-I may also be referred to, where relevant.

##### STRIPPING

    - GENERAL

Before the embankment works commence, the base shall be stripped of unsuitable surface soil, including all vegetation, grass, organic matter, bushes, roots and other unsuitable matter and shall dispose off the same as directed with a lead up to 100 mtrs. and all lifts. Similar operations shall be done in the borrow areas and in such cutting reaches of canal which yield useful embankment materials. Stripping shall be done to such depth as directed.

    - RECORDING OF CROSS SECTION

- After clearing the site for embankment and prior to stripping the natural ground surface cross sections shall be surveyed (as described in Para 1.5)

- After stripping is completed, the initial cross section shall be taken as described in Para 1.5. The natural ground surface cross sections and initial cross sections shall form the basis for arriving at the quantities of excavation for stripping.

    - MEASUREMENT AND PAYMENT FOR THE SEAT OF EMBANKMENT.

The payment will be done as per payment schedule.

##### PREPARATION OF FOUNDATION UNDER EMBANKMENT

- No materials shall be placed for the earth fill of the embankment until the foundation of the embankment has been dewatered, suitably prepared and approved by the Engineer-in-charge. All portions of excavation made for test pits or other sub-surface investigations and any existing cavities below the foundations of the embankment shall be filled with soil of same quality as specified for the earth fill and suitably compacted.

- Pools of water shall not be permitted in the foundation of the embankment and any water shall be drained off and cleared prior to placing the first layer of embankment materials.

- SOIL FOUNDATION

Soil foundations of the embankment shall be scarified and loosened by means of a plough, ripper or any other means to depth of about 15 cms to 20 cms to the satisfaction of the Engineer-in-charge. Roots or

other debris turned up during scarifying shall be removed from the foundation area which thereafter shall be moistened to slightly above the optimum moisture content of the foundation soil and shall be compacted by the compaction equipment to the same degree of compaction as that of the embankment. The purpose of using higher moisture than optimum is to ensure forcing of the soil into any soft zones existing below the surface. The first four layers of the fill for the embankment shall be 10 cms. to 15 cms thick and shall be carefully placed and uniformly compacted to form satisfactory bond between the foundation and the fill. These layers in the hearting zone should be composed of most impervious materials. Sheep foot roller shall preferably be used for the compaction of impervious soil and vibratory type rollers for compaction of pervious and semi-pervious soils and rock.

- ROCK FOUNDATION

  - The treatment of the rock surface under the embankment shall be so done as to ensure a tight bond between embankment and the foundation. This shall be attained by the following procedure.

  - The area of the rock surface which is to be in contact with the embankment shall be fully exposed by removing all the loose and disintegrated rock leaving a rugged rock surface. Hard rock projections and overhang shall be knocked off and removed. If blasting is to be restored to care shall be taken to avoid objectionable shocks to foundation rock. As far as possible the whole contact area shall exposed at one time to enable examination of the surface characteristics of the rock and for planning the method of treatment.

  - If the foundation rock is fairly impervious but has a highly rugged surface, it shall be treated by laying embankment material in 10 cms thick layers at a moisture content slightly above the O.M.C. and compacted with mechanical equipment / pneumatic tampers to ensure that all irregular depressions in the rock surface are filled with soil to create an effective and complete bond.

- SAND FOUNDATION

Sand encountered in foundation shall be tested for its natural relative density. It shall be compacted by any approved methods to obtain a minimum relative density of 70% before the filling commences.

- PAYMENT

No separate payment will be made for the preparation of the foundation under embankment as cost of this operation is deemed to have been included in the respective embankment items.

24.4.1BACK FILLING OF CUT-OFF TRENCHES

- The cut-off trench shall be backfilled with same kind of materials and in same manner, as the earth fill of the impervious core of the canal embankment. Each layer of the fill shall be continuous and

approximately horizontal layer of specified thickness and compacted under optimum moisture content to the specified degree of compaction.

- During placing and compaction of impervious materials in the cut-off trench where dewatering is involved, the sub-soil water level at every point in the cut-off trench shall be maintained below the bottom of he earth fill until the compacted fill in the cut-off trench at that point has reached a height of 3 mtrs., after which the water level shall be maintained at least 1.5 mtrs., below the top of compacted fill.

##### BORROW AREAS

    - GENERAL

(a) All materials required for the construction of impervious or pervious zones of embankment and back fill for cut-off trench and structures which are not available from canal excavation, excavation for structure or from excavation of other ancillary works, shall be obtained from the designated borrow areas or as designated by the Engineer-in-charge in consultation with field laboratory. The depth of cut in all borrow areas shall be designated by the Engineer-in-charge and the cut shall be made to such designated depth only. Each designated borrow area shall be fully exploited before switching over to the next designated borrow area. Haphazard exploitation shall not be permitted. The type of equipment used and the operations in the excavation of materials in borrow areas shall be such as to produce the required uniformity of the mixture of materials for the embankment/CNS layer.

    - STRIPPING OF BORROW AREAS

- Borrow areas shall be stripped of top soil and any other objectionable materials to the required depth. Stripping operations shall be limited only to designated borrow areas. Materials from stripping shall be disposed of in the exhausted borrow areas or in the approved adjacent areas.

- Stripping of borrow area shall not be measured and paid for separately. The cost of stripping is to be included in the unit rate for the respective embankment/CNS layer item in schedule B.

    - BORROW AREA WATERING

- Borrow areas watering shall be done by the contractor wherever necessary and in the manner specified by the Engineer-in-charge.

- The initial moisture content of the material in the borrow areas shall be estimated with the help of laboratory test. The optimum moisture content for the material in the particular borrow areas shall be determined by field tests. The additional moisture requirements if any shall be introduced into the borrow areas by watering well in advance of the excavation to ensure uniformity of moisture content. All care shall

be taken to reduce excessive moisture in any of the locations of a borrow area before or during excavation to secure the materials with moisture contents close to the optimum to avoid formation of pools in the borrow areas during excavation operation, drainage ditches from borrow areas to suitable outlets shall be excavated, wherever necessary. On exhausting all useful materials or abandoning borrow areas the pits shall be fully drained to ensure no ponding of water.

##### EMBANKMENT

    - GENERAL

The embankment may comprise of different zones viz.

- Impervious zone of earth fill of controlled compaction at controlled moisture content.

- Semi pervious/pervious earth fill of controlled compaction at controlled moisture content, and

- All in fill of controlled compaction at random moisture content.

    - EARTH FILL

- Bushes, roots, sods or other organic or unsuitable materials shall not be place in the embankment. The suitability of each part of the foundation for placing embankment materials thereon and of all materials for use in embankment construction will be determined by the Engineer-in-charge on the basis of field laboratory tests. The difference in elevation of the canal embankment within each working length of not less than 50 mtrs., shall not exceed 1.2 mtrs., anywhere in cross section unless specifically permitted by the Engineer-in-charge. Placing of the layers for the embankment portion programmed for construction in the season shall be continuous and approximately horizontal.

- Placement of fill within the zones as shown on the drawings shall be performed in an orderly sequence and in an efficient and workman like manner.

- Chemical and physical tests of the soil in the embankment shall be carried out by the quality control organization of the department to ensure that the soil does not contain soluble lime, soluble salts or cohesion less fines and unsound materials in quantities harmful to the embankments. Useful materials from canal excavation and excavation of structures and from borrow areas shall be classified, transported and placed in the specified zones of embankment as directed by the Engineer-in-charge.

- Normally, the contractor shall utilize not less than 80% of suitable excavated material from the canal and structures to construct embankment, whenever such utilization is economical in the opinion of the Engineer by conveying from the spoil heaps with all leads and lifts as mentioned in schedule B and he will not be authorized to obtain material from borrow areas until he does so. The balance of soils shall be

obtained from borrow areas approved by the Engineer-in-charge. If the contractor fails to utilize at least 80% of the usable excavated materials from the canal and structures and obtains instead material from the borrow area, payment for this material shall be made as if obtained from canal excavation within the leads mentioned in schedule-B. The decision of Engineer about the usability of soils available from the canal excavation is final and binding upon the contractor.

- Embankment materials shall be spread in successive horizontal layers extending to full width of the embankment plus 45 cms on either side to facilitate satisfactory compaction in the full designed width. No payment shall be made for placing the additional 45 cms. widths or for their subsequent removal. No addition shall be allowed to the slopes of the bank after the bank is raised. Trimming of inside slopes to final dimensions, lines and grades shall precede the lining work. This shall be done not more than two days prior to lining.

- Thickness of embankment layers may be adjusted by the Engineer-in-charge if the contractor by carrying out trial compaction and requisite tests satisfies the department that the type of compactors used by him provide required density. The thickness of loose layers in embankment shall be normally as under.

| Sl. No.Type of compaction Machine | Weight | Thickness of loose layer |
| --- | --- | --- |
| 1. 1.5 mts. Dia.drum sheep foot rollers | 6000 kgs./running mrts. | 25cms. to 30 cms |
| 2. 1 mtrs. Dia drum sheep foot rollers | 3000 kgs/running mrts. | 20 cms to 22 cms. |
| 3. Pneumatic Tamper | ................................ | 7.5 cms to 10 cms. |
| 4. D. R. R. | 10,000 kgs. | 20 cms to 25 cms. |
| 5. Vibratory roller | ................................ | 30 cms to 45 cms. |

- No embankment layer shall be laid until the previous layer is properly watered, compacted and tested as per requirement. The work of spreading and compaction shall be so adjusted as not to interfere with each other and in such a way that neither of the operations is held up because of non-completion of the rolling and watering. If the work is held up due to failure of machinery, no claim whatsoever will be entertained even in case of machinery is supplied by the department. The surface of embankments shall at all time of construction be maintained true to required cross section.

- The distribution of materials in each layer shall be such that the compacted materials will be homogeneous and free from lenses, pockets or other imperfections. The excavating and placing operations shall be such that the materials when compacted will be blended sufficiently to secure the best practicable degree of compaction, impermeability and stability.

- The material of the earth fill zones of controlled compaction and moisture content shall be compacted to a density as specified on the drawings but not less than 96% of the standard proctor density. The material having less than 1.5 gms/cc. Standard proctor density shall not be used unless specifically permitted by the Engineer-in-charge.

- In the above zones, no lumps or stone or pebbles having larger dimension than 7.5 cms in impervious core and 13 cms. in pervious/semi pervious zones shall be permitted. The total percentage of lumps or stones or pebbles of permissible size shall not exceed 5% in the case of impervious core and 15% elsewhere. The percentage is in respect of every 3 cubic metre of batch material conveyed to the site of placement.

- The homogeneous section for canal embankment shall be provided in the reaches where design requirements are met with without hearting. The homogeneous zone shall be formed of materials, with a permeability of less than 3 mtrs. Per year and with a standard proctor's dry density not less than 1.5 gms/cc. The soil for the embankment shall generally be in accordance with recommendations contained in IS : 8826-1978 (Para 8). The available coarser and more pervious material shall be placed near the outer slopes in order to have increasing permeability from inner to outer side.

- The impervious hearting zone wherever shown in the drawings shall be constructed of material having required percentage of clay so that it can be compacted at optimum moisture content by suitable compacting equipment to achieve not less than 96% of the standard Proctor density. Water tightness of material shall be checked by carrying out permeability tests both at the site and laboratory. Permeability of impervious materials shall not be greater than 30 cms/year.

- The casing zone shall consist of material which provides support to impervious core under various conditions of saturation and draw down. The distribution of material shall be such that the compacted material shall be homogeneous, free from cracks, pockets or other imperfections. The excavating and placing operations shall be such that the material when compacted shall be blended sufficiently to secure the best practicable degree of compaction, impermeability and stability. The casing material should normally have a standard Proctor density not less then 1.75 gms/cc.

- All suitable material with dry density greater than 1.35 gms/cc. Shall be used in all-in-fill zone. Suitable sub-zones shall be formed within the all-in-fill if so directed by the Engineer-in-charge, by depositing materials of different type, texture and particle size in different sub-zones. In general, fragments of smaller size shall be deposited towards the inner slope and larger fragments towards the outer slope of all-in fill. Formation of service roads and inspection paths in reaches of full cutting will be treated as all-in-fill and will be paid for accordingly.

- The top surface of the bank shall be leveled with a gradient of 1 to 80 away from the inner edge to facilitate proper drainage. The canal embankment shall be constructed to the top width and height equal to designed height shown on the drawing, plus 2.5% of the designed height to allow for settlement. The embankment width, at various levels should be regulated accordingly. However, the bottom width of embankment shall as shown on the drawing or as directed by the Engineer-in-charge.

- For proper bond between embankment placed in a previous season with the current embankment, work shall be carried out and finished as under:

  - Where an existing embankment is to be extended horizontally it shall be cut to a slope not steeper than 1 in 3 and the surface so prepared shall be scarified loosened at least to a depth of 15 cms and wetted. Following, the embankment material shall be laid in layer and compacted to the required degree of compaction.

  - If the old bank is to be raised vertically, vegetation shall be cleared followed by scarifying, and watering and placing of the new earth layer as specified above. Raising shall be done after the bottom layer is tested. No extra payment will be made in this regard for the operations of clearing, scarifying and watering etc.

  - The surfaces which are damaged due to rain shall be repaired by filling with proper material duly compacted by tampers.

- The finished fill shall be free from lenses, pockets, streak of layers of materials differing substantially in texture or gradation from the surrounding materials. Successive loads of the materials shall be dumped on the earth fill so as to produce best practicable distribution of the materials subject to the approval of the Engineer-in-charge.

    - MOISTURE CONTROL

- Prior to and during compacting operations the material in each layer of earth fill zones of controlled compaction and moisture content shall have optimum moisture content. The permissible variation in the OMC is +/-3.

- As far as possible, the material excavated from the borrow area shall have adequate moisture content. If additional moisture is required, it shall be added preferably at the borrow area and only to a limited extent, if required, on the embankment by sprinkling water before placement. If moisture content is more than required, the material shall be allowed to dry before compaction. The moisture content shall be uniform throughout the layer of material for which plough, disc harrowing or other methods of mixing shall be applied. If the moisture content is more than the required moisture content specified above or if it is not

uniformly distributed throughout the layer, rolling shall be stopped and shall be started again only when the above conditions are satisfied.

    - COMPACTION

- Material shall be placed in layers of specified thickness as shown in the table under Para 2.6.2(6). the proper moisture content where prescribed shall be uniformly distributed throughout the material, before it is compacted. Compaction shall be done in strips overlapping not less then 0-.30 mtr. The compacting equipment shall travel in a direction parallel to the axis of the canal. Turns shall be made carefully to ensure uniform compaction. Each layer of soil placed in the bank as specified above shall be compacted with 8 to 10 tonnes power rollers or suitable crawler tractor drawn, heavy sheep foot rollers. The compaction shall have to be uniform over the full width of the bank. the roller shall be made to travel over the entire designed width of each layer so that the soil is uniformly compacted to the required degree and it leaves no visible marks on the surface. Where flat roller are used, the surface of each layer of compacted materials shall be roughened with a horrow or thoroughly furrowed/pick-marked as directed before depositing the succeeding layer of materials and care shall be exercised to avoid the occurrence of horizontal seams.

- In those parts of the structure which are inaccessible to the specified rolling equipments, or around and in contact with structures and in proximity to structures, where the rolling equipment is not permitted to operate, compaction shall be accomplished by mechanical or pneumatic rammers of approved type as directed. Rollers shall not be permitted to operate within 0.60 metre of concrete or masonry structures and the earth fill within this distance shall be tamped by mechanical or pneumatic rammers. All materials to be so tamped shall be spread in layers. 7.5 cms to 10 cms thick when loose and the moisture content of the material and the amount of tamping shall be such as to produce a degree of compaction equal to the specified degree of compaction for rolled fill portion Special care shall be exercised to obtain good contact and bond with surface of concrete or masonry structures.

- Where canal embankment covers barrels of cross drainage structure first 45 cms. of the embankment shall be compacted with pneumatic hand tempers in loose layers 7.5cms. to 10 cms thick. Further fill shall be compacted by using suitable light rollers to avoid damage to the structures, by adjusting the thickness of layers until sufficient height is achieved to permit compaction by heavy rollers. Density test shall be conducted from time to time on site to ascertain whether the compaction is attained as specified above. Separate tests shall be conducted for each layer of hearting and casing zone of embankment at least one field density test shall be taken in each zone for every 30 mtrs. or less of compacted earth work. A minimum of three density tests one is hearting one in inner casing and one on outer casing shall be taken

per day. In case the specified densities are not attained, suitable measures shall be taken by the contractor either by moisture correction or by removal and relaying of layer or by additional rolling so as to obtain the specified density which shall be checked again at the same locations. In addition, tests shall also be carried out at the limits of the embankment and adjacent to filters at the discretion of the Engineer-in- charge. Necessary unskilled labour required for collection of samples shall be provided by the contractor at his cost. However, testing charges shall be borne by the department.

- At least three standard proctor tests shall be carried out at regular intervals for the material to be used to account for variation in the borrow area material as well as excavated material. Wherever materials from different sources are used for embankment i.e. material from borrow areas or from excavation, at least three tests shall be carried out to determine standard proctor density of each material.

- The department might review the design if necessary on examination of density and other test results and the contractor shall have no claim arising out of such a review and consequent change if any in the design.

- Where compaction of cohesion less free draining materials such as gravel is required, the materials shall be deposited in horizontal layers and compacted to the specified relative density. The excavating and placing, operations shall be such that the material, when compacted, shall be blended sufficiently to secure the highest practicable unit weight and best stability. Water shall be added to the materials as may be required to obtain the specified density by method of compaction being used.

    - COMPACTION OF ALL-IN FILL

The all-in-fill zone of the bank wherever shown in the drawings or instructed to provide, shall be formed in layers of uniform thickness and for the full width of zone. The thickness of loose layer shall not be more than that given in the table in para 7 in clause 2.6.2. When construction of controlled earth fill zone proceeds the formation of the all-in-fill zone, the slope of the earth fill zone at the junction shall be stepped if so directed to ensure proper bonding between the two zones.

All clods and lumps of soil shall be broken to a size not exceeding 7.5 cms. The finer of the materials available shall be deposited on the inner side and the coarser materials towards the outside of the embankment. Each layer shall be well compacted by the flat rollers, sheep foot roller vibratory rollers, crawler tractor or by combination of any of the above as is best suited to the type of the fill material, as directed. The minimum relative density of the compacted material shall not be less than 70% of the dry density as determined in laboratory tests in the case of cohesion less materials. In the case of cohesive materials, the degree of compaction should not be less than 90% of the proctor's density. A minimum

number of passes of the compacting equipment would be prescribed and followed to obtain optimum compaction.

    - LAYING AND COMPACTING COHESIVE NON-SWELLING MATERIAL.

- where the canal is excavated through soils, a layer of cohesive non-swelling (CNS) material shall be placed between the expansive soil and the concrete lining in accordance with paragraph 5.2 of IS : 9451- 1985. The CNS material shall have the following properties:

-Gradation

Clay (less than 2 micron)	15 to 20%

Silt (0.06 mm.- 0.002 mm.)	30 to 40%

Sand (2mm.-0.06.)	30 to 40%

Gravel (Greater than 2 mm.)	0 to 10%

-Index properties

Liquid limit - less than 55% but greater than 30% Plasticity Index-less than 30% but greater than 15%

- If the CNS material does not conform to above properties, it should be suitably blended with suitable soils to achieve the properties as directed by the Engineer-in-charge.

- Immediately prior to placing the first layer or CNS material, the surface of the excavation and embankment to receive the material shall be adequately wetted, as approved by the Engineer-in-charge.

- After the canal prism has been shaped to a reasonably true and even surface, CNS material shall be placed compacted to not less than 96% of standard proctor density unless otherwise specified, on adequately wet surface in specified layers depending upon the type of compacting equipment deployed. Each layer of CNS material shall be moistened before compaction.

- In case of distributaries with smaller bed width in cutting reaches it may not be possible to compact the CNS layer by power rollers. In such cases the CNS material filled up in the excavated section shall be hand tamped in suitable layers till adequate width is available for compaction, by power rollers. Further layers shall be compacted by power rollers. In case of wider section of the distributaries, the placing and compaction of the CNS layers shall be done on both the side slopes independently. After compaction is done, the canal section shall be cut to the required neat lines and excavated CNS materials shall be re-used in further reaches. Laying and compaction of CNS layers shall be done as per drawings to achieve specified field densities.

    - WHETHER CONDITIONS

- Embankment material shall be placed only when whether conditions are satisfactory to permit accurate control of the moisture content in the embankment material. Before closing the work on embankment, in any continuous reach prior to monsoon, the top surface shall be graded away from the canal and rolled with a smooth wheeled roller to facilitate runoff. Prior to resuming the work, the top surface shall be scarified and moisted or allowed to dry as the case may require.

- The contractor shall provide suitable protection works to protect the slopes from erosion due to rain. No payment whatsoever shall be made for providing such protection work and repairing any monsoon damages.

##### ROCK FILL

24.7.1GENERAL

Rock fragments available from the canal excavation shall be used in all-in-fill embankment if found suitable, as per the directions of the Engineer-in-charge. The thickness of loose layer of rock fill shall not be more than 60 cms using well graded rock fragments varying form 0.014 cum (1/2 cft) to 0.75 cum. (1 cubic yard). The rock fill shall be placed or dumped in approximately horizontal layers with finer materials in the interior of the embankment and larger materials towards the outer edge. Voids in the rock fill shall be filled and packed with smaller stones of not less than 7.5 cms in size, in such a manner as to obtain a dense fill with minimum of voids to the satisfaction of the Engineer -in-charge. Compaction shall be done by movement of crawler tractor or loaded tippers. The relative density of the hand packed and compacted rock fill shall not be less than 70%.

##### ROCK TOE

- Materials for rock toe shall consist of suitable free draining rock fragments, cobbles and boulders. The stones / rubble available from the excavation shall be used. If the materials is not sufficient, stones/rubbles shall be brought from the approved quarries.

The material shall be got approved by the Engineer-in-charge prior to being brought to site. The material shall be clean and well graded consisting principally of rock fragments. Fragments less than 0.01 cum. shall not be used. Sufficient fine material such as rock spells, cobbles and coarse gravel to fill the voids among the larger stone shall be used. Use of stones above 0.028 cum is not obligatory. The material shall be selected and placed in such way that the larger stones shall be placed near the outer slope and the smaller ones adjacent to the inner slope. The stones shall near the outer slope and the smaller ones adjacent to

the inner slope. The stones shall be properly hand packed, so as to produce a dense and well graded fill with no large voids and cavities. The surface of the outer slope shall be fairly even and uniform.

- Suitable outfall for draining the seepage water collected in the rock toe shall be provided depending upon the site conditions.

- The dimensions of the rock toe zone shown in the drawings are tentative and if required, modifications may be ordered by the Engineer during execution of the work. The contractor shall work according to such modifications without any increase in unit rates.

##### LAYING OF FILTERS

Filters media shall be provided to the dimensions shown in the drawing or as directed by the Engineer - in- charge. The number of layers, the thickness of each layer and gradation of filter material shall be as specified in drawing or as directed by the Engineer - in-charge. The placing of the filter materials shall be such that the segregation within the layer is prevented. The Filter materials shall be watered and compacted so as to achieve a relative density of not less than 70%. Care shall be taken not to mix up the filter materials of a layer with soil or with filter materials of adjoining layer.

Suitable transition filter is intended to be provided between earth fill and all-in -fill zone consists of less than 50% of minus 80 mm. material. The contractor shall provide the transition filter as shown in the drawing or as directed by the Engineer-in-charge for which payment will be made at quoted rates. Horizontal filter blanket shall be provided, wherever prescribed, connecting the inclined filters as shown in the drawings or as directed by the Engineer-in-charge. Before placing the horizontal filter layers, the foundation thereof shall be cleared and brought to level by filling in depressions (if any) with selected im-previous materials compacted at OMC. Each layer of filter media shall be adequately watered and compacted by moving the hauling and spreading equipment over it or by other means approved by the Engineer-in-charge. The rock toe, if prescribed, shall then be laid in such a way as not to damage the filter blanket in any way.

Inclined filters abutting the outer slope of the impervious core shall be provided as per approved drawings or as directed by the Engineer - in - charge. Filter materials shall be so placed that it conforms to the position indicated in the drawing and the continuity of each layer is ensured. The thickness and location of each individual filter layer shall be maintained by placing the material between temporarily placed mild steel sheets or wooden boards which shall be withdrawn before compaction. The inclined filter and the embankment material adjacent to it shall be raised together with the maximum difference in height of

0.6 mtr. between filter and the adjacent embankment.

    - FILTERS DRAINS

Filters drains shall be provided at suitable locations and to the dimensions shown in the drawing to collect seepage from the embankment and to discharge the same away from the embankment by suitable means according to the site conditions as directed by the Engineer-in-charge.

    - FILTER MATERIALS

- The filter materials shall consist of well graded sand, gravel or crusher broken aggregate. The material shall be free from debris, brush wood, vegetable matter, decomposed rock, and other deleterious matter. Sand in filter media shall confirm to the specifications in IS : 383-1970 or its latest version. Silt and clay content in sand shall be less than 5% (IS : 1498-1970)

- Filter materials shall not be placed until the sub-grade has been inspected and finally approved by the Engineer-in-charge. The filter material shall be laid in layers not exceeding 15 cms. in thickness or as prescribed by the Engineer-in-charge. The number of layers, the thickness of each layer and the size of the ingredients shall be as per the final design which will be furnished to the contractor based on the laboratory test satisfying primarily the following filter criteria.

  - D15(F) < 4 D 85(B)

  - D15(F)  = between 4 and 40 D 15 (B)

Where D 15 and D 85 are particle diameter corresponding to 15% and 85% passing

'F' denotes filter material 'B' denotes base material. The percentage being determined by weight after mechanical analysis.

- The gradation curves of the filter material shall be nearly parallel to the gradation curves of the base material

- The requirement for grading of the filter shall be established by the field laboratory on the basis of mechanical analysis of adjacent materials

- The size and grading of filter material shall generally be as indicated in the drawing. The Engineer-in- charge may at his discretion modify the gradation in the filter layer to satisfy the filter criteria. The contractor shall do the necessary processing of the filter materials at his own cost.

- The material brought by the contractor to the site shall be tested by the quality control organization of the department in the laboratory at the project site. The result thereof shall be final and binding. All

material not conforming to the requirement so determined shall not be permitted for us on the said work.

##### BACK-FILL IN FOUNDATION TRENCHES AND AROUND STRUCTURES

    - GENERAL

- The type of material used for backfill and manner of depositing the material, shall be subject to approval. As far as practicable, backfill material shall be obtained from the excavating for structures or from adjacent canal excavation or from excavation of other ancillary works.

- Back-fill material shall contain no stones larger than 7.5 cms. size, or as prescribed by Engineer-in- charge.

- The backfill material shall be placed to the lines and grades as shown on the drawings or as prescribed in this paragraph or as directed by the Engineer-in-charge.

- The backfill material shall be placed carefully and spread in uniform layers of specified thickness and each layer will be moistened and compacted to required degree of compaction at specified moisture contents. The backfill shall be brought up as uniformly as practicable on the both sides of walls and all sides of structures to prevent unequal loading. The backfill material shall be placed at about the same elevation on both side of the pipe portions of the structures and culverts and difference in elevation shall not exceed 15 cms. at any time. The contractor shall be responsible for providing adequate earth cover wherever necessary such as over the pipes or pipe culverts, to prevent damage due to loads of construction equipments.

- If a haul road is built over a pipe, all backfill around and over the pipe shall be placed to a uniform surface and no humps or depressions shall be permitted at the pipe crossings.

    - COMPACTION OF BACKFILL

When compacting soil against abutment of masonry or concrete structures, width to an extent of 0.6 mtr. shall be compacted with pneumatic tampers. Roller shall not be used close to structures to avoid damage. The size and weight of compacting equipment shall depend on nature of material, the height and load assumed in design of a structure. The backfill close to the structure upto the rolled layer shall be compacted in suitable uniform layers, using pneumatic tampers to a dry density of at least 96% of standard proctor. The moisture content of the earth fill placed against the rock or the structures shall be about 2% higher than O.M.C. to allow for penetration into cavities. Compaction at joints of earthwork and backfill around structures shall be carried out with special care without claiming any extra cost.

##### WEATHER CONDITIONS

- Embankment material shall be placed only when weather conditions are satisfactory to permit accurate control of the moisture content in the embankment material. Before closing the work on embankment, in any continuous reach prior to monsoon, the top surface shall be graded away from the canal and rolled with a smooth wheeled roller to facilitate runoff. Prior to resuming work, the top surface shall be scarified and moistened or allowed to dry as the case may require.

- The contractor shall provide suitable protection works to protect the slopes from erosion due to rain. No payment whatsoever shall be made for providing such protection work and repairing any monsoon damages.

##### INSPECTION AND TESTS

    - . GENERAL

- The Engineer-in-charge would exercise thorough check on the quality of fill material delivered to the embankment and on the degree of compaction. He would further arrange to obtain and record the data of in-situ properties of the high banks after compaction, for comparison with design assumptions. To achieve these objectives, a programme of field testing and inspection shall be planned.

- The scope of testing and inspection is as under:

  - The quality of materials used for bank work will be checked periodically.

  - Checks on the effectiveness of placement and compaction procedures shall be made by field density tests at prescribed intervals.

  - Record tests of compacted fill shall be made at regular intervals.

    - BEFORE COMPACTION

- Material delivered to the fill shall be visually examined and their properties estimated by way of inspection.

Borrow Area

  - Excavation of borrow areas shall be limited in extent and depth as indicated on plans.

  - Estimation of moisture content of materials shall be made by visual examination and feel.

  - Sample shall be taken for laboratory analysis in case of soil is of different characteristics.

- These inspection /checks shall be supplemented by sampling the materials at prescribed intervals and by testing the samples in the laboratory for gradation and moisture content etc.

EMBANKMENT

  - Moisture contents tests shall be carried out in the laboratory while placing the fill materials.

  - Moisture contents shall be controlled by adding water or allowing the solid to dry up to the extent required.

  - It shall be ensured that the methods of dumping, spreading and moisture conditions are such as will result in reducing segregating and variation of moisture content to a minimum,

    - DURING COMPACTION

Inspecting during compaction shall ensure:

      - That the layer thickness of the material is as specified.

      - That the fill is compacted at least up to 90% of standard Proctor density or as otherwise specified or 70% relative density as the case may be.

ii)	That no excessive rutting, waving or scaling of the fill occurs during compaction.

    - AFTER COMPACTION

The conditions of the fill after compaction shall be observed and recorded particularly with respect to rutting or waving. However, the properties of materials after compaction shall be determined primarily by field density tests. Routine tests on samples taken from constructed embankment shall include density tests, and moisture content tests. The record tests shall include grain size distribution, Atterburg limits. Permeability & consolidation characteristics.

    - FREQUENCY OF TESTING

- Before and after compaction the sampling and testing of materials shall be done at sufficient frequencies so that effective checks on the full operations are maintained. Testing frequencies shall be as per standards prescribed by the department. However, the actual frequencies shall be adjusted to suit to the nature and variability of materials placed and the rate of fill placement as per the directions of the Engineer-in-charge.

- Testing shall be performed at higher frequencies than those specified above during initial stages of construction in order to establish control and testing techniques. Testing shall be conducted

additionally, as and when required in case of special problems such as variation in the construction materials, in equipment performance and weather.

- In addition, these tests shall be made

  - In areas where the degree of compaction is doubtful and

  - In areas where embankment operations are concentrated.

- Locations of likely insufficient compaction shall cover the following or any other areas so determined by the Engineer-in-charge.

  - The junction between areas of mechanical tamping and rolled embankment along structures.

  - Areas where rollers turn,

  - Areas where improper water content has been encountered.

  - Areas where dirt clogged rollers have been encountered.

  - Areas containing materials differing substantially from the average.

    - . RECORD AND REPORT

The contractor shall maintain chronological and location wise record of the source of materials and the embankment placing operations in order to have a continuous check on the works. Thus, it should be possible to have a complete description of materials that has gone into in any portion of the embankment.

##### PROTECTION

The contractor shall take all precautions necessary for the protection of all works by diversion of adjacent streams, surface drainage, rain water etc. any damage to earth work due to any reason whatsoever shall be repaired by the contractor at his cost till the work is certified as completed and taken over by the Department.

##### TURFING

Turfing the downstream slope shall be done with locally available approved good quality grass according to the directions of the Engineer-in-charge. Turfing shall be laid on 25 cms thick soil of approved quality over the finished embankment face. The rate shall include the cost and conveyance and laying of 25 cms thick solid and approved grass and watering. The rate shall also include maintaining the Turfing till the end of the maintenance period, including watering and replacement of grass wherever necessary.

##### MEASUREMENTS FOR PAYMENT

Payment as per payment schedule

SECTION – III

PLAIN AND REINFORCED CONCRETE

  - SCOPE OF WORK

The specification cover the requirements of plain and reinforced concrete for use in various components of structures. The work covered under this section consists of furnishing all materials including form work, equipment, labour for the manufacture, transport, placing, vibrating, finishing and curing of the concrete for the structures and performing all the operations necessary and ancillary thereto including dewatering and desilting etc., as required. For the reinforced concrete structures, granite, quartzite, dolerite or trap shall only be used as coarse aggregate.

##### APPLICABLE PUBLICATIONS

All concrete, its constituents, methods and procedures of manufacture, placement etc. shall conform to Indian Standard Specifications and other publications listed below unless otherwise specified.

    - INDIAN STANDARDS FOR REFERENCE

- IS : 303-1975	Plywood general purpose

- IS : 432-1966 (part-I)	Mild steel and medium tensile steel bars

- IS : 516-1976	Portland slag cement

- IS : 516-1959	Methods of test for strength of concrete

- IS : 2505-1980	Concrete vibrators immersion type.

- IS : 2506-1964	Screed board concrete vibrators.

- IS : 3370-1965-1967	Code of practice for concrete structures (All parts)	for the storage of liquids.

- IS : 3558-1983	Code practice for the use of immersion vibrators for consolidating concrete.

- IS : 4656-1968	Form vibrators concrete

- IS : 4990-1981	Plywood for concrete shuttering works.

- IS : 5242-1979	Method of test for determining shear strength of mild steel.

- IS : 8989 -1978	Safety code for erection of concrete framed structure.

- IS : 9077-1979	Code of practice for corrosion protection of steel reinforcement in R.B. and R.C.C construction.

In addition to the above, relevant Indian Standards referred in Section-III shall also apply.

    - OTHER PUBLICATIONS

- Indian road congress standard	Section I specifications and code of	Section II &

practice for road bridges.	Section III

- Concrete Manual	U.S.B.R.

(Latest Edition)

- American Society for testing of materials	C. 494.80

- Design aids to IS : 456-1978 for	SP	16 (S & T)    reinforced concrete.		1980

##### COMPOSITION

- Concrete shall be composed of cement, fine aggregate (natural sand of manufactured sand or both), coarse aggregates (manufactured or natural gravel) admixtures and water, well mixed in proportion and brought to the proper consistency. The design mix proportions shall be adjusted to produce a durable and workable concrete, suitable for specified conditions of placements and design strength.

- For all items of concrete in any portion of the structure or its associated works, controlled concrete shall be used where specified.

###### Materials

    - CEMENT

- Only 43 grade ordinary Portland cement shall be used for R.C.C. constructions while puzzolona Portland cement (P.P.C.) shall be allowed to be used for plain concrete.

- Immediately, upon receipt at the site of the work, cement shall be stored separately in dry, water tight and properly ventilated structures. All storage facilities shall be subject to approval and shall be such as to permit easy access for inspection and identification. Sufficient cement shall be kept in stock for completion of concreting undertaken. Cement shall be used in order of receipt and cement older than 90 days shall not be used unless the test results satisfy the minimum strength requirements. The provision made in para 3.5.1 shall also apply.

    - FINE AGGREGATES

The provisions made under para 3.5.2 shall apply.

    - COARSE AGGREGATES.

- coarse aggregates shall consist of hard, strong, durable particles of crushed stone or gravel and shall be free from thin elongated soft pieces, organic or other deleterious matter. It shall have no adherent

coating. It shall be from a source, approved by the Engineer-in-charge. Coarse aggregates shall conform to IS : 383-1970 and IS : 515-1959.

- Coarse aggregates shall be washed if necessary to remove all vegetations and other perishable substances and objectionable amounts of other foreign matter. The cost of washing and screening shall be borne by the contractor.

- Following table gives an indication of the maximum size of coarse aggregate for the different items of work. However maximum size of coarse aggregate shall be adopted as indicated on the drawings.

Sl. No.Item of work	Maximum Nominal size of coarse

Aggregate (MSA)

  - Foundation floor and gravity	40 mm retaining walls (mass concrete)

  - R.C.C. Rafts, piers, Abutments	40 mm Barrels, cutoff walls, Breast walls

Staunching rings etc.

  - R.C.C. work in main and cross girders,	20 mm Deck slab, wearing coat, kerb, parapet

walls, approach slab, pier caps, diaphragm wall and other thin

walled members and in zones of congestion

- For heavily reinforced concrete members, as in the case of ribs of main beams, maximum size of aggregate shall usually be restricted to 5 mm. less than the minimum lateral clear distance between the main bars or 5 mm less than the minimum cover to the reinforcement, whichever is smaller. However, if required under special circumstance, the Engineer may permit an aggregate of maximum size 25% more than this/critical spacing / cover, provided that proper vibration is ensured. The other provision of section

3.5.3 shall apply.

    - REINFORCEMENT STEEL

The provisions of section V shall apply.

    - WATER

The provision of para 3.4.5 shall apply.

    - ADMIXTURES

Admixtures like water reducing agents, air entraining agents, water proofing agents etc. shall be used only if permitted by the Engineer. The kind of admixture its make and quality, the proportion and the manner of mixing shall be subject to Engineer's approval.

    - EPOXY

Use of epoxy for bonding fresh concrete for repairs shall be permitted on written approval of the Engineer. Epoxy shall be applied in accordance with the instructions of the manufacturers. The cost of such repair shall be borne by the contractor.

##### CONCRETE FOR STRUCTURES.

Controlled concrete shall be used for the structures in three grades designated as M-10, M-15 and M-20. The mix shall be designed using representative samples of available coarse and fine aggregate as well as cement and water to achieve the required workability strength and durability standards. Mix design studies and test will be made by the KNNL.

##### STRENGTH REQUIREMENT OF CONCRETE

The compressive strength requirement for the various grades of controlled concrete shall be as per table No. I given below.

TABLE NO.1

Grade of	Compressive test strength in N/Sq mm of 150 mm

Concrete	cube conducted in accordance with IS : 516-1959

|  | Min. at 7 days | Min. at 28 days |
| --- | --- | --- |
| M-10 | 7 | 10 |
| M-15 | 10 | 15 |
| M-20 | 13.5 | 20 |
| M-25 | 17.0 | 25 |

Note : in all cases, the 28 days compressive strength specified in table shall alone be the criteria for acceptance or rejection of the concrete on the basis of its strength. Where the strength of a concrete mix as indicated by tests lies in between the strength for the two grades specified in table, such concrete shall be classified for all purpose as concrete belonging to the lower of the two grades between which its strength lies.

PROPORTIONING CONCRETE

- Concrete mix shall be designed on the basis of preliminary test. The proportion of ingredients shall be such that concrete has adequate workability for conditions prevailing on the work in question and can be properly compacted with the means available. Samples of construction material required for evolving design mix shall be supplied 3 months in advance.

- Unless it can be shown to the satisfaction of the Engineer-in-charge that supply of properly graded aggregates of uniform quality can be maintained till the completion of the work, grading of aggregate shall be controlled by obtaining the coarse aggregate in different sizes and blending them in the right proportions as required. Different sizes shall be stacked in separate stockpiles. Required quantity of materials shall be stock piled at least 3 days in advance before use. Grading of coarse and fine aggregates shall be checked as frequently as possible, frequency for a given job being determined by the Engineer-in-charge to ensure that the supplies are maintaining the uniform grading as approved for samples used in the preliminary tests. In proportioning concrete the quantity of both cement and aggregate shall be determined by weight. Water shall either be measured by volume in calibrated tank or weighed. All measuring equipment shall be maintained in a clean serviceable condition. Their accuracy shall be periodically checked.

- It is most important to maintain the specified water cement ratio. To this end, moisture content in both fine and coarse aggregates shall be periodically determined and the amount of mixing water shall be adjusted to compensate for any variations in the moisture content. For the determination of moisture content in the aggregates IS : 2386-1963 (Part III) shall be referred to. Suitable adjustment shall also be made in the batched weight of the aggregate depending upon the variations in their moisture content.

- The quantity of water shall be just sufficient to produce a dense concrete of required workability and strength for the job. An accurate and strict control shall be kept on the quantity of water.

- Incase of reinforced concrete work, workability shall be such that the concrete surrounds and properly grips all reinforcement. The degree of consistency, which shall depend upon the nature of work and methods of vibration of concrete, shall be controlled by regular slump tests. Following slumps shall be adopted for different types of works.

Type of work	Slump Allowed

  - Mass concrete for RCC foundations,	40 mm to 50 mm footing and retaining walls

  - Beams, slabs and columns	40 mm. to 50 mm.

  - Thin RCC section with congested steel	50 mm. to 60 mm.

##### PRODUCTION OF CONCRETE

    - PRODUCTION OF AGGREGATES.

Production of aggregates may include quarrying of the raw material and processing viz. transporting, crushing, screening and washing. Water used for washing aggregates shall be clean and free from alkali, salts and other impurities. After washing, fine aggregates must be stored in stock piles with a free draining base for at least 3 days to ensure that sand, delivered to the batching plant will have a reasonably uniform moisture content. The storage and handling shall be in such a manner as to prevent inter mingling of various sizes of aggregates required separately for grading purposes. No foreign matter shall be allowed to mix with aggregate.

    - BATCHING

- The prescribed amount of the various materials of concrete, including water, cement, admixtures the groupings of fine aggregates and each individual size of coarse aggregates shall be measured and controlled within the specified limits of accuracy. The amount of water, cement and aggregates shall be determined by weighing. In the case of fine aggregates, the surface moisture shall be determined in accordance with the method prescribed in Appendix D of IS : 456-1978 and its subsequent amendment or publications. In the case of coarse aggregates, percentage of free water shall be determined by weighting representative sample, then surface drying each particle individually with a clean piece of cloth and reweighing.

- The batching equipment shall be constructed and operated so that the combined inaccuracies in feeding and measuring the materials shall not exceed 1% for water and cement and 2% for each size of aggregate.

- The operating performance of each scale or other measuring device shall be checked by test weight and the test shall cover the ranges of measurements involved in the batching operations. Tests of equipments in operation shall be made at least once every fortnight and adjustment, repairs or replacement, be made as necessary to meet the specified requirements for accuracy of measurement.

- Aggregate shall not be batched for concrete or mortar when free water is dripping from the aggregate.

- Incase uniformity in the materials used for concrete has been established over a period of time, proportioning may be done by volume batching, provided periodical checks are made on mass / volume relationship of the material. When weigh bathing is not practicable, quantities of fine and coarse aggregate

(not cement) may be determined by volume. If fine aggregate is moist and volume batching is adopted, allowance would be made for bulking in accordance with IS : 2386-Part III - 1963.

    - MIXING

- The concrete ingredients shall be mixed thoroughly in batch mixers of satisfactory type and size, which are so designed as to ensure uniform distribution of all the constituent materials throughout the mass at the end of mixing period. The plant shall be so designed and operated that all materials entering the mixer can be accurately proportioned and readily controlled. The entire batch within the mixer shall be discharged before re-charging. The volume of mixed materials per batch shall not exceed the rated capacity. A mixer will be considered unsatisfactory, if from three tests of any one batch, a range in slump exceeding 25 mm or a range in air content exceeding one percent is noticed between representative samples taken at different portions of the mixer discharge.

- For any one batch, uniformity of fresh concrete weight of air free mortar of two samples one taken at the front and one at the end of the mixer discharges, when determined in accordance with the provisions of the mixer performance test, designation 26 in the appendix of the seventh edition of the United States Bureau of Reclamation concrete manual, shall not exceed 1.6 percent of the mean value. The adequacy of mixing shall also be determined in accordance with "Method of sampling and analysis of concrete" as per IS : 1199-1959 and its subsequent amendments. Excessive variation on the unit weight of air free mortar incidicates that mixing time should be increased. Mixer efficiency test shall be made at the start of a job and at such intervals as may be necessary to ensure compliance with the requirements for effective mixing. The minimum mixing time specified herein may be reduced if mixer efficiency test conform that the reduced time permits satisfactory mixing.

- The first concrete batch at the start of continuous mixing operation or after a lapse of 30 minutes in continuous mixing operation shall be made richer by the addition of extra cement as directed.

- For any one batch, the difference between the unit weight of coarse aggregate from concrete samples from the front and end of the mixer or mixer discharge, when determined in accordance with the above mentioned mixer performance test shall not exceed 10% of the mean value.

- The mixing of each batch shall continue, for not less than the period stated in table I of IS : 457- 1957 reproduced at para 3.6.3 unless tests of mixer performance show that variation in the prescribed time is necessary or acceptable. Each mixer shall have a timing device for indicating the completions of the required mixing period.

- The actual time of mixing shall be checked at least twice during each shift and in the case of central batching plant where the timing device is provided, the same shall be adjusted if there is error. The timing

device shall be so interlocked with the discharge gate of the batch hopper that timing does not start until the discharge gate is fully closed and all ingredients are in the drum. A suitable record shall be kept of the average time consumed in charging, mixing and discharging a batch during each run.

- The full contents of the drum shall be discharged quickly to avoid segregation.

- The minimum periods specified are conditional on the materials being fed into the mixer in a manner which will facilitate efficient mixing and an operation of the mixer at its designed speed. The following sequence of charging the mixer may be adopted.

- Five to ten percent of the total quantity of water required for mixing adequate to wet the drum thoroughly, shall be introduced before the other ingredients in order to prevent any caulking of the cement on the blades or sides of the mixer.

- All dry ingredients (cement and the fine and coarse aggregate) shall be simultaneously fed into the mixer in such a manner that the period of flow for each ingredient is about the same. Eighty to ninety percent of the total quantity of water required for mixing shall be added uniformly along with the dry ingredients.

- The remaining quantity of water shall be added after all the other ingredients are in the mixer.

- Portion of the coarse aggregate, however, may be added last. This will facilitate clearance of the chutes and removes any fine aggregates or cement adhering to the sides.

- Excessive mixing, requiring additions of water to preserve the required concrete consistency will not be permitted.

- When the mixer is stopped, before placing again any ingredients in the mixer, all hardened concrete or mortar shall be removed from the inner surface of the mixer.

- The re tampering of partially hardened concrete or mortar requiring renewed mixing with or without the addition of cement aggregate or water shall not be permitted.

##### TEMPERATURE OF CONCRETE AND WEATHER CONDITIONS

The temperature of concrete at the time of placement shall not exceed 35 degree C. concreting operations shall be temporarily suspended during excessively hot weather when their temperature inside the form exceeds 45 degree C. or when conditions are such that the concrete cannot be placed at the required temperature. Wherever necessary, exposed surfaces of fresh or green concrete shall be adequately shaded from the direct rays of the sun and protected against premature setting or drying by curing under continuous fine spray of water.

##### TRANSPORTING OF CONCRETE

- Concrete shall be transported from the mixing plant to the placing position as rapidly as practicable by methods that will prevent segregation of loss of ingredients, or slump loss in excess of 25 mm and or a loss in air content of more than one percent before the concrete is placed in the works. Whenever the length of haul, from the mixing plant to the place of deposit is such that the concrete unduly compacts or segregates, suitable agitators or transit mixers shall be used for conveying concrete.

- Where the tie of haul exceeds 20 minutes, mixed concrete shall be transported in suitable agitators or transit mixers as stated herein above.

- If buckets are used for conveying low-slump concrete, they shall be capable of promoting discharge in controlled quantities without splashing or segregation and shall be of such capacity that there is no splitting of batches in loading buckets. Buckets shall be of the bottom dump type permitting an even, controlled flow into the forms or hopper without undue splashing or segregation. Conveying vehicles shall be designed to facilitate uniform delivery rather than quick dumping.

- Chutes used for conveying concrete shall be of such size and shape as to ensure a steady uniform flow of concrete in a compact mass without separation or loss of ingredients and shall be protected from wind and sun where necessary to prevent loss of slump by evaporation and shall be furnished with a discharge hopper. Free fall or drop of concrete shall be limited to 150 cms. Chute sections shall be made of or lined with metal and all runs shall have approximately the same slopes not flatter then 1 vertical to 2.5 horizontal. The required consistency of concrete shall not be changed in order to facilitate chuting. Where it becomes necessary to change the consistency, the concrete mix shall be completely redesigned. Wherever there is free fall within the conveying system, suitable baffle plates, splash board, or down spouts shall be provided to prevent segregation, splashing or loss of ingredients. Whenever it is necessary to hold the discharge end of a chute more than 3 meters above the level of the fresh concrete, a flexible down spout shall be used to break the fall and confine the flow. The lower end of the spout shall be held close to the place of deposit. Whenever depositing is intermittent, a discharge hopper shall be provided. All chutes shall be thoroughly cleaned before and after each run. All wash water and debris shall be disposed off outside the forms.

- Equipment used for transporting concrete from the mixer to the forms shall be maintained free from deposits of stiff concrete and leakage of mortars. Batch containers, transit mixers, agitators, chutes, concrete pumps. Pipe lines and discharge hoppers shall be thoroughly cleaned after each run. All wash water and debris shall be disposed of outside the forms.

##### PREPARATION FOR PLACING CONCRETE

    - GENERAL

- Concrete shall not be placed until all form work required is completed, embedded parts if any installed and checked and surface prepared for placing. No concrete shall be deposited until the foundation has been inspected and approved.

- All surfaces of forms and embedded materials that have become encrusted with dried mortar or grout from concrete previously placed shall be cleansed of all such mortar or grout before fresh concrete is placed and shall be oiled with a commercial form oil or alternatively covered with LDPE film as specified in para 4.13.4

    - FOUNDATION SURFACES

- Immediately before placing concrete, all surfaces of foundations upon or against which the concrete is to be placed shall be free from standing water, mud and debris. All surfaces of rocks upon or against which concrete is to be placed shall in addition to the foregoing requirements be cleaned and free from all lubricants, objectionable coating and loose semi-detached or unsound fragments. The surface of absorptive foundations upon or against which concrete is to be placed shall be moistened thoroughly and kept sufficiently wet for at least 24 hours prior to placing concrete so that the moisture will not be drawn from the freshly placed concrete. The cleaning and roughening of the surfaces of rock shall be performed by the use of high velocity air water jets, wet sand blasting, stiff brooms, picks or by other effective means. The washing and scrubbing process shall be continued until the wash water collected in puddles is clear and free from dirt. In the final cleaning process the wash water may have to be removed by sponges. If any drilled holes are left in the foundation surface which are not longer needed, the same shall be cleared with air water jetting and filled up completely with cement slurry.

- In the case of earth or shale foundations, all soft or loose mud and surface debris shall be scraped and removed. The surface shall be moistened to a depth about 15 cms (6 inches) to prevent the sub grade from absorbing water from he fresh concrete. Just before placing the concrete, the surface of the earth shall be tamped or otherwise consolidated sufficiently to prevent contamination of concrete during placing. If subsoil water is met within the foundation, it shall be dewatered as directed till the placing and setting of concrete. All concrete shall be placed upon clean damp surface free from standing water and never upon soft mud, dried porous earth or upon fills that have not been subjected to approved rolling and desired compaction.

- Foundation of porous or free draining material shall be thoroughly compacted by flushing and by subsequent tamping or rolling, if necessary. The finished foundation surface shall then be blanketed with a layer of tar paper or closely woven burlap carefully lapped and fastened down along the seems so as to prevent the loss of mortar from the concrete.

    - SURFACE OF CONSTRUCTION AND CONTRACTION JOINTS

- The surface of construction / contraction joints shall be clean, rough and damp but free from standing pools of water when receiving the next lift. Clean up shall comprise removal of all laitance, loose or defective concrete coating, sand, curing compounds if used and other foreign materials, if necessary by scrapping, chipping or other suitable means.

- The surface of construction /contraction joints shall be cleaned by use of high pressure wear jet or by wet sand blasting and swashed thoroughly. Water jetting and blasting and washing shall be performed just prior to the placing of concrete.

- The method used in disposing of water employed in cutting, washing and rinsing of concrete surface shall be such that the waste water does not stain, discolor or effect exposed surfaces of the structures. Methods of disposal of waste water shall be subject to approval.

##### PLACING AND COMPACTING CONCRETE

- After the surfaces have been cleaned and dampened as specified, surfaces or rock and construction joints shall be covered, wherever practicable, with a layer of mortar approximately 10 mm to 15 mm thick. The mortar shall have the same proportions of water, air entraining agent if any, cement and fine aggregate as the concrete mixture which is to be placed upon it. The water cement ratio of the mortar which is placed shall not exceed that of the concrete to be placed upon it and the consistency of the mortar shall be suitable for being spread uniformly and worked thoroughly into all irregularities of the surfaces.

- In so far as it is practicable, concrete shall be placed directly in its final position and shall not be caused to flow in a manner to permit or cause segregation. Methods and equipments employed in placing concrete will ensure that aggregate is not separated from the concrete mass.

- In placing mass concrete in a lift successive batching of concrete shall be placed in a systematic arrangement in order to avoid exposure of parts of the live surface of a concrete layer.

- In mass concrete placement, delay may occur resulting in cold joints within a lift. When placement is resumed while concrete is so green (and therefore capable of ready bonding) that it can be dug out with a hand pick, the usual contraction joint treatment will not be required if the surfaces are kept moist and the concrete placed against the surface is thoroughly and systematically vibrated over the entire area adjacent

to the older concrete. If the delay is short enough to permit penetration of the vibrator into the lower layer during routine vibration of successive layers, the vibration will assure necessary bonding.

- If for any cause, the working surface is left exposed until it has hardened to a considerable extent, it shall be left to set and cured for not less than 56 hours or longer. If for any reason a strength greater than

15.2 kg/sqm (500 PSI) has been attained before completing the lift, the surface thus interrupted shall be given a thorough clean up as for normal lift joint surface and the work shall be commenced with a mortar layer as specified.

- In placing mass concrete, the exposed area of fresh concrete shall be maintained at the practical minimum by first building up the concrete in successive approximately horizontal layers to the full width of the block and full height of the lift over a restricted area at the downstream end of the block and then continuing upstream in similar progressive stages to the full area. The slope formed by the unconfined upstream edge of the successive layers of concrete shall be kept steep as practicable in order to keep its area minimum. Concrete along these edges shall not be vibrated until adjacent concrete in the layer is placed, except that it shall be vibrated immediately when weather conditions are such that the concrete will be harden to an extent the later vibration may not fully consolidate and integrate in with more recently placed adjacent concrete.

- Re tampering of concrete shall not be permitted. Any concert which has become so stiff that proper placing without re tampering cannot be ensured shall be wasted.

- In formed work, structural concrete placement shall generally be started with an over sanded mix containing 20 mm maximum size aggregate and an extra sack of cement for one cubic metre and having a 125 mm slump placed several centimeters deep on the joins at the bottom of the form. Concrete placement shall commence immediately thereafter.

- Concrete shall be compacted to the maximum practicable density, in such a manner that it is free from pockets of coarse aggregate and is in intimate contact with surface of forms and embedded materials. Unless otherwise permitted, all concrete shall be compacted by mechanical vibrator.

- Compaction of concrete shall whenever practicable be carried out by use of immersion type vibrators having vibrating heads of 100 mm or more in diameter shall be operated at speed of at least 6,000 revolutions per minute when immersed in the concrete.

- Vibrators having vibrating heads less than 100 mm. in diameter shall be operated at speed of at least 7,000 revolutions per minute in the concrete. Normally formwork shall be designed to provide for the insertion and operation of mechanical vibrators in the placed concrete. Form vibrator shall be used wherever internal vibration is not possible or would be inadequate.

- In compacting each layer of concrete, the vibrator shall be operated in almost vertical position and the vibrating head shall be allowed to penetrate and re vibrate the concrete in the upper portion of the underlying layer. In the area where freshly placed concrete in each layer joins previously placed concrete, more vibration than usual shall be performed the vibrators penetrating deeply at close intervals along these contacts, Layers of concrete shall not be placed until layers previously placed have been vibrated thoroughly as specified. Contacts of the vibrating head with surface of the forms shall be avoided.

- During placing and until curing is completed, the concrete shall be protected against the harmful effect of exposure to sunlight, wind and rain as directed.

##### FORM WORK

    - GENERAL

- Form work shall be used wherever necessary to confine the concrete and shape it to the required lines, or to ensure against contamination of the concrete by material caving or sloughing from adjacent surface left by excavation or other features of the work All exposed concrete surfaces having slope steeper than of one horizontal to one vertical shall be formed.

- Form work may be of timber, steel or precast concrete panels or such other suitable - materials or combination of such materials as may be directed by the Engineer. Form work shall be substantially and rigidly constructed to the shapes, lines and dimensions required, efficiently propped and braced to prevent de formination due to placing, vibrating and compacting concrete, other incidental loads or the effect of weather.

- The surfaces of form work shall be made such as to produce surface finishes as specified and formwork joint space be tight enough to prevent loss of liquid from concrete. Joints between the form work and existing concrete structures shall also be "grout tight". The form work shall be arranged to facilitate easing and removing of the various parts in correct sequence, without jarring or damaging the concrete. Fixing blocks, bolts or similar devices may be embedded in the concrete, provided they do not reduce the strength or effective cover of any part of the structure below the required standard but he use of through bolts shall be avoided as far as possible.

Temporary opening shall be provided at all points necessary in the forms to facilitate cleaning and inspection immediately before placing of the concrete.

- Forms shall overlap the hardened concrete in the life previously placed by not less than 75 mm and shall be tightened singly against the hardened concrete so that when concrete placement is resumed, the forms will not spread and allow off-set or loss of mortar at construction joints. Additional bolts or form ties

shall be used as necessary to hold forms tight against hardened concrete. Particular attention shall be paid in setting and tightening the forms for construction joints so as to get a smooth joint free from sharp deviations or projections.

- Moulding strips shall be placed in the corners of forms so as to produce chamfered edges as re assured on permanently exposed concrete surface.

    - MATERIALS TO BE USED

- Materials used for form sheathing and lining shall conform to the following requirements :

Required	Timber Sheathing or lining	Steel sheathing or lining

finish

| F1 | Any type and grade meeting | Steel sheathing permitted |
| --- | --- | --- |
|  | the dimensional requirement | steel lining permitted |
|  | of surface finish except | except on surfaces of |
|  | that metal form shall be | internal transverse and |
|  | used on surfaces of internal | longitudinal joint in the |
|  | transverse and longitudinal | structure component where |
|  | joints in mass concrete | steel sheathing is |
|  | gravity walls. | Required. |
| F2 | Common grade timber or | Steel sheathing permitted |
|  | plywood sheathing or lining. | steel lining permitted if strongly supported. |
| F3 | For plain surface common grade | Steel sheathing permitted, |
|  | timber or plywood. | steel lining not permitted. |
| F4 | For warped surfaces timber which | steel sheathing permitted, |
|  | is free from knots and other | steel lining not permitted. |
|  | Imperfections and which can be |  |
|  | cut and bent accurately to the |  |
|  | required curvatures without |  |

splintering or splitting.	 Steel sheathing denotes steel sheets not supported by a backing of timber boards, steel lining denotes steel sheet, supported by a back of timber boards.

- Timber sheathing or lining shall be of such kind and quality or shall be so treated or coated that there will be no chemical deterioration or discoloration of the formed concrete surfaces. The type and condition of form sheathing and lining and the ability of forms to withstand distortion caused by placement and vibration of the concrete and the workmanship used in the form construction shall be such that the

formed surfaces will conform to applicable requirements of this specification pertaining to finish or formed surfaces.

- Forms for concrete surfaces required to receive F2 and F3 finish shall be constructed so as to produce uniform and consistent texture and pattern on the concrete faces Metal patches on forms for these faces will not be permitted. The form sheathing or lining shall be so placed that all horizontal form marks are continuous across the entire surface. Where finish F2 is specified the sheathing or lining shall be placed so that the joint marks on the concrete surfaces will be in general alignment both horizontally vertically and the form sheathing material used for such surfaces shall be restricted to one type in any one major features of the work.

- Forms for surfaces required to receive F4 finish shall be constructed so as to conform accurately to the required curvature of the section. Where necessary to meet requirements for curvature the form sheathing shall be built up of laminated splices cut to make right, smooth form surface. The forms shall be constructed that the joint marks on the concrete surface shall in general, follow the line of water flow.

- After the forms have been constructed all surface imperfections shall be corrected. All the nails shall be hidden and any roughness and all angles on the surface of the forms caused by matching the forms materials shall be dressed to curvature.

- Embedded ties for holding forms shall remain embedded and except where F1 finish is permitted, they shall terminate not less than two diameters or twice the minimum dimension of the tie or ten millimeters, whichever is greater from the formed faces of the concrete. The use of metal rods or other similar devices embedded in he concrete for holding forms shall be permitted if the ends of the rods are omitted or subsequently removed to a depth as specified above from the surface of the concrete without injury to the concrete, provided that for walls subjected to water pressure on one side and required to be watertight the rods shall not be taken through the wall. Complete removal of embedded rod shall not be permissible. Removal of embedded fasteners on the ends of the rods shall be done so as to leave holes of regular shape for reaming. All holes left by the removal of fasteners from the ends of the rods shall be immediately reamed with suitable toothed reamers so as to leave the surfaces of the holes clean and rough and completely filled with dry patching mortar and the surfaces shall be finished to match the adjacent concrete. Wire ties shall be permitted only where specifically approved and shall be cut off flush with the surface of the concrete after the forms are removed. Wire ties shall not be used when permanently exposed finished surfaces are required. Where F1 finish is permitted, ties may be cut off flush with formed surface.

- The ties shall be constructed so that removal of the end or end of fasteners can be accomplished without causing appreciable spalling at the faces of the concrete. Recesses resulting from removal of the ends of he form ties shall be filled in accordance with the provision for repair of concrete as per para 3.15.

    - FORM, CENTERING AND TEMPORARY WORKS

- All centering, form work and temporary works shall be constructed according to the approved drawings and specifications. The IS : 883 : 1970 code of practice for design of structure timber in building shall be applicable for this work.

- As soon as practicable, after the acceptance of his tender, the contractor shall submit a scheme showing the order or procedure and method by which he proposes to carryout the work, together with such details as are necessary to demonstrate the adequacy, stability and safety of the methods.

- Necessary data for the general scheme of centering shall be obtained well in time.

- After approval of the general scheme, the contractor shall prepare detailed design and drawings for execution of the form work, centering and temporary works. These shall be forwarded to the Engineer-in- charge for approval. No work shall be carried out without prior approval of the Engineer-in-charge.

- Not withstanding the approval given to the design criteria and loading and the general scheme for the centering, the entire responsibility for the satisfactory execution of the centering and all temporary works shall rest with the contractor and he shall be liable to pay all claims and compensation arising from any loss or damage to life and property due to any deficiency, failure or malfunctioning of the centering or the temporary works.

- All centering and supports shall be properly braced and cross braced in 2 directions. The supports shall be strong enough to withstand the weight or pressure when considerable quantity of wet concrete is poured. When the centering posts rest on soft ground, their load shall be distributed by means of scantlings / planks of not less than 5 cms thickness / short piles. Wherever the stage of centering is more than 3 mtrs. Invariably steel centering shall be resorted to.

- Reuse of forms etc.

Forms required to be used more than once shall be maintained in serviceable condition and shall be thoroughly cleaned and repaired before reuse. Where metal sheets are used for lining forms, the sheets shall be placed and maintained in the forms without humps and other imperfections. All forms shall be checked for shape and strength before reuse.

    - CLEANING AND TREATMENT OF FORMS

At the time the concrete is placed in the forms, the surfaces of the forms shall be free from encrustations of mortar, grout or other foreign material. Before concrete is placed, the surfaces of the forms designated to produce F-1, F-2, F-3 and F-4 finishes shall be oiled with a commercial form oil, that will effectively prevent sticking and will not stain the concrete surface. For timber forms, form oil shall consist of pure, refined, pale paraffin mineral oil or other approved form oil. For steel forms form shall consist of refined mineral oil suitably compounded with one or more ingredients which are appropriate for the purpose. Care shall be taken to keep form oil out of contact with reinforcement. In the alternative the surfaces of the forms designated to produce formed surfaces shall be overlaid with LDPE film of 200 microns.

3.12.5.REMOVAL OF FORMS

- Except as otherwise provided in this Sub-Clause forms shall be removed as soon as the concrete has hardened sufficiently, thus facilitating satisfactory curing and earliest practicable repair of surface imperfections.

- Forms on upper sloping surfaces of concrete, such as forms on the water sides of wrapped transition, shall be removed as soon as the concrete has attained sufficient stiffness to prevent sagging. Any needed repair or treatment required on such sloping surface shall be performed at once and be followed immediately by the specified curing.

- In order to avoid excessive stresses in the concrete that might result from swelling of the forms, timber forms shall be loosened as soon as this can be accomplished without damage to the concrete.

- Subject to approval, forms on concrete surface close to excavated rock surface may be left in place provided that the distance between the concrete surface and the rock is less than 400 mm and that the forms are not exposed to view after completion of the works.

- Forms shall be removed with care so as to avoid damage to the concrete. Concrete damaged if any in form removal shall be repaired in accordance with the provisions for repair of concrete as per para 4.15.

- The following minimum intervals of time will generally be allowed when using ordinary Portland cement between placing concrete and striking form work, but the period shall be modified in case of wet weather and also as per direction of Engineer-in-charge.

  - Walls, columns and vertical faces	24 to 48 hours or as may be decided by the Engineer-in charge

  - Slabs	14 days

  - Beam Soffits	14 days

  - Slab spanning up to 6.0 mtrs.	14 days

  - Slab spanning over 6 mtrs.	21 days

NOTE : In normal circumstances, and where ordinary Portland cement is used forms may generally be removed after expiry of the above period. For other cements, the stripping time recommended for ordinary Portland cement may be suitably modified.

Where the shape of the element is such that the form work has re - entrant angles, the formwork shall be removed as soon as possible after the concrete has set, to avoid shrinkage cracking, occurring due to the restraint imposed.

##### FINISHES AND FINISHING OF CONCRETE SURFACES

    - FORMED SURFACES

- Allowable deviation from plumb or level and from the alignment profile, grades and dimensions shown on the drawings is defined as 'tolerance' and is to be distinguished from the irregularities in finishes as described herein. The tolerance in concrete construction is specified in para 4.21.

- The classes of finish and requirements for finishing of concrete surface shall be as shown on the drawing or as hereinafter specified. In the event of finishing not being definitely specified herein or on the drawings the finishes to be used shall be as directed by the Engineer-in-charge. Finishing of concrete surface shall be performed only by skilled workmen.

- Completed concrete surfaces will be tested where necessary to determine whether surface irregularities are within the limits hereinafter specified.

- Surface irregularities are classified as 'Abrupt' or 'gradual' offsets caused by displaced or misplaced form sheathing, or lining or form sections or by loose knots or otherwise defective timber form will be considered as abrupt irregularities and shall be tested by direct measurements. All other irregularities shall be considered as gradual irregularities and will be tested by use of template, consisting of a straight edge or the equivalent thereof for curved surfaces. The length of the template shall be 150 cms for testing of formed surfaces and 300 cms for testing unformed surfaces.

- The clauses of finish for formed concrete surface are designated by one of the symbols F1, F2, F3 and F4. The jute bags rubbing or sand blasting will not be required on formed surfaces and grinding will not be required on formed surfaces other than that necessary for the repair of surface imperfections. Unless otherwise specified or indicated on the drawings, the classes of finish which will apply are as follows :

  - FINISH F1

This finish applies to surfaces where roughness is not objectionable, such as those upon or against which fill material, masonry or concrete will be placed, the upstream face of the structure that will permanently be under water or surface that will otherwise be permanently concealed. The surface treatment shall be the repair of defective concrete, correction of surface depression deeper than 25 mm and filling of the tie rod holes. Form sheathing will not leak mortar when the concrete is vibrated. Forms may be built with a minimum of refinement.

  - FINISH F2

This finish is required on all permanently exposed surface for which other finishes are not specified, such as in Head Regulators, Cross Regulators, Drainage siphons, Bridges and Retaining Walls not prominently exposed to public view except wherein F1 finishes are permitted. Forms shall be built in a workmanlike manner to the required dimensions and alignment, without conspicuous offsets or bulge. Surface irregularities shall not exceed 5 mm for abrupt irregularities and 10 mm for gradual irregularities measured with 1.5 mtrs. template.

  - FINISH F3

This finish is designated for surface of structures prominently exposed to public view where appearance is also of special importance. This shall include inside of drainage barrels, piers of bridges and beams and slabs of cross regulators, siphons, aqueducts, drops, parapets, railings and decorative features on the structures and on the bridges. To meet with the requirements for the F3 finish forms shall be built in a skillful, workmanlike manner, accurately to dimensions. There should be no visible offsets, bulges, or misalignment of the concrete. At construction joints the forms shall be tightly set and securely anchored close to the joint. Abrupt irregularities shall not exceed 5 mm for irregularities parallel to the directions of flow and 2.5 mm for irregularities in other directions. Gradual irregularities shall not exceed 5 mm. Irregularities exceeding this limit shall be reduced by grinding on a bevel of 1 to 20 ratio of height to length.

  - FINISH F4

This finish is required for formed concrete surface at the cut and ease waters of the piers portions of outlets, draft tubs, high velocity flow surfaces of outlet work downstream from gates and spillway tunnels of dams and where evenness of surface is essential. The forms must be strong and held - rigidly and accurately to the prescribed alignment. For wrapped surface the forms shall be built up in section cut to make tight smooth form surfaces after which the form surfaces are dressed and sanded to the required curvature. Gradual irregularities shall not exceed 5 mm. Abrupt irregularities shall not be permitted. Formations of air holes on the surface of the concrete designated to receive finish shall be minimized and

where such air holes are found, they shall be repaired in accordance with the provisions of relevant paragraph.

    - UNFORMED SURFACES

- The classes of finish for unformed concrete surfaces are designated by the symbols, U1, U2, U3 and U4. Unless otherwise specified or indicated on the drawings, these classes of finish shall apply as follows :

  - FINISH U1

This finish applies to unformed surfaces that will be covered by fill material, masonry or concrete, or where a screeded surface meets the functional requirements. Finish U1 is also used as the first stage of finishes for U2 and U3. Finishing operations shall consists of sufficient leveling and screeding to produce an even uniform surface. Surface irregularities measured as described in this section, shall not exceed 10 mm.

  - FINISH U2

    - This is a floated finish, and used on all out door unformed surfaces not specified to receive finishes U1 and U3. It may be used for such surfaces as apron and floors of cross regulators and head regulators, drainage barrels, aqueducts and escapes and inside of slopping aqueduct troughs.

    - Finish U2 is also used as the second stage of finish for U3. Floating may be performed by hand or power driven equipment. Floating shall be started as soon as the screeded surface has stiffened sufficiently to prevent the formation of laitance and shall be the minimum necessary to produce a surface that is free from screed marks and is uniform in texture. If finish U3 is to be applied, floating shall be continued until a small amount of mortar without excess water is brought to the surface, so as to permit effective toweling. Surface irregularities measured as described in this section shall be removed as directed.

  - FINISH U3

This is a trowelled finish and may be specified for tops of parapets prominently exposed to view and conduit invert immediately downstream of regulating gates and valves. When the floated surface has hardened sufficiently to prevent excess of fine material from being drawn to the surface, steel troweling shall be started. Steel trowel ling shall be performed with firm pressure, that will flatten the sandy texture of the floated surface and produce a dense uniform surface free from blemishes and trowel marks. Surface irregularities, measured as described in relevant parts of this section, shall not exceed 5 mm where hard steel trowelled finish is specified, the regular U3 finish shall be trowelled again after the surface has nearly hardened using firm pressure and trowel ling until the surface is hard and has a slightly glossy appearance.

  - FINISH U4

    - This is a steel trowelled finish similar to finish U3 except that light surface pitting and light trowel marks such as obtained form the use of machine trowel ling or lining machine will be acceptable, provided the surface irregularities do not exceed the limits specified for finish U3.

    - Unformed surfaces which are nominally level shall be sloped for drainage as shown on the drawings or as directed, unless the use of other slopes or level surface is indicated on the drawing, narrow surface such as tops of parapets, tops of walls and kerbs shall be sloped approximately half centimeter per 30 cms of width.

    - Unformed surfaces which are nominally level shall be sloped for drainage as shown on the drawings or as directed, unless the use of other slopes or level surface is indicated on the drawing, narrow surface such as tops of parapets, tops of walls and kerbs shall be sloped approximately half centimeter per 30 cms of width.

For canal lining the finish U4 shall be adopted.

##### REPAIR OF CONCRETE

    - GENERAL

- Repair of concrete shall be performed by skilled workers and in the presence of an experienced Engineer. The Contractor shall correct imperfections on the concrete surfaces as necessary to produce surface that conform with requirements of the paragraph "finishes and finishing of concrete surfaces". Repairs on formed concrete shall be completed as soon as practicable after removal of forms and within 24 hrs after removal of forms. Concrete that is damaged from any cause and concrete that is honeycombed, fractured or otherwise defective and concrete which because of excessive surface depressions has to be excavated and built up to bring the surface to the prescribed lines shall be removed and replaced by dry pack mortar or concrete as hereinafter specified. Where bulges and abrupt irregularities protrude outside the limits specified in the paragraph 'finishes and finishing of concrete surfaces', the protrusions shall be reduced by bush hammering and grinding so that the surfaces are within the specified limits.

- Before repair is to commence, the methods proposed for the repair shall be approved by the Engineer –in charge. Routine curing should be interrupted only in the area of repair operations.

    - METHODS OF REPAIRS

For new works four methods are used as under :

- DRY PACK METHOD :

This method should be used for holes having a depth nearly equal to, or greater than the least surface dimensions, for cone bolt, she bolt and grout insert holes, and narrow bolts cut for the repair of cracks. Dry pack should not be used for relatively shallow depressions where lateral restraint cannot be obtained, for filling in back of considerable lengths of exposed reinforcement ; nor for filling holes which extend entirely through the wall, beam, etc.

- CONCRETE REPLACEMENT METHOD

Concrete replacement should be used when holes extend entirely though the concrete section, when holes in unreinforced concrete are more than 1,000 sq cms in area and 100 cms or more in depths and when holes in reinforced concrete are more than 500 sq cms in area and deeper than the reinforcement steel.

- MORTAR REPLACEMENT METHOD

This should be used for holes too wide to dry pack and too shallow for concrete replacement and for all comparatively shallow depressions, large or small, which extend no deeper than for side of the reinforcement bars nearest to surface.

- EPOXY METHOD

A thermosetting plastic known as epoxy can be used as a bonding medium whenever long time curing of conventional concrete cannot be assured. Also epoxy mortars of fine sand as well as plain epoxy are suitable for concrete repair work and should be used whenever very thin patches are to be placed or immediate reuse of the area is required or where moist curing cannot be effectively accomplished. Preparation for epoxy bonded repairs should in general be identical to that for other concrete repairs except that every efforts should be made to provide surfaces thoroughly dry. Drying of the immediate surface for at least 24 hrs. and warming to temperature between 18 degree C to 27 degree C. are essential for proper application of epoxy bonded repairs. Preparation for the use of epoxy mortars should include thorough cleaning and drying of the areas to be repaired. A wash of dilute 1:4 mercuric acid rinsing with clean water and subsequent drying is desirable, where feasible. If acid wash is not feasible, preparation may be accomplished as for other concrete repairs with final cleanup being by means of sandblast method, followed by air water jet washing and thorough drying, epoxy repairs shall be carried out only by a trained personnel. The type of epoxy to be used shall be got approved by the Engineer-in charge.

    - PREPARATION OF CONCRETE FOR REPAIRS

All concrete of questionable quality should be removed. It is better to remove too much concrete than too little because affected concrete generally continues to disintegrate and while the work is being done it costs but little more to excavate to ample depth. Moistening, cleaning, surface drying and complete curing are of utmost importance when making repairs which must be thoroughly bonded, watertight and permanent.

Surfaces within trimmed holes should be kept continuously wet for several hours, preferably overnight prior to placing new concrete. Immediately before placement of the filling, the holes should be cleaned so as to leave a surface completely free from chipping dust, dried grout and all other foreign materials. Preliminary washing as soon as the chipping and trimming are completed is desirable to remove loose material. Final cleaning of the surfaces to which the new concrete is to be bonded should be done by wet sandblasting followed by washing with air water jet for through cleaning and drying with an air jet. Care should be taken to remove any loose materials embedded in the surface by chisels during the trimming and to eliminate all shiny spots indicating free surface moisture. Cleaning of the steel if necessary should be accomplished by sand blasting. The prepared surface shall be approved by the Engineer-in-charge.

- DRY PACKING OF CONCRETE

For this method of repair, the holes should be sharp and square at the surface edges, but the corners within the holes should be rounded, especially when water tightness is required. The interior surfaces of holes left by cone bolts, she bolts etc. .. should be roughened to develop an effective bond. Other holes should be under-cut slightly in several places. Holes for dry pack should have minimum depth of 25 mm.

- CONCRETE REPLACEMENT

Preparation for this method should be as follows :

  - Holes should have minimum depth of 100 mm. in new concrete and the minimum area of repair should be 500 sq cms for reinforced and 1,000 sq cms for unreinforced concretes.

  - Reinforcement bars should not be left partially embedded. There should be a clearance of at least 25 mm around each exposed bar.

  - The top edge of the holes at the face of the structure should be cut to a fairly horizontal line. If the shape of the defect makes it advisable, the top of the cut may be stepped down and continued on a horizontal line. The top of the hole should be cut to 1 to 3 upward slope from the back towards the face of the wall or beam. It may be necessary to fill the hole from both sides, in which case the slope of the top of the cut should be modified accordingly.

  - The bottom and sides of the holes should be cut sharp and approximately square with the face of the wall when the hole goes entirely through concrete section, spalling or feather edges shall be avoided by having chippers worked from both faces. All interior corners should be rounded to a minimum radius of 25 mm.

- MORTAR REPLACEMENT

When mortar gun is used with this method , comparatively shallow holes should be flattered outwardly at about 1 to 1 slope to avoid inclusion of rebound. Corner within the holes should be rounded. Shallow imperfections in concrete may be repaired by mortar replacement if the work is done promptly after removal of the forms and while the concrete is still green, for instance when it is considered necessary to repair the peeled areas resulting from surface material sticking to steel forms the surfaces may be filled using mortar gum without further trimming or cutting. Whenever hand placed mortar replacement is used, edges of chipped out areas should be squared with the surface leaving no feather - edges.

- USE OF DRY PACK MORTAR

The surface after preparing should be thoroughly brushed with a stiff mortar or grout barely wet enough to thoroughly wet the surface after which the dry pack material should be immediately packed into place before the bonding grout has dried. The mix of bonding grout shall be 1 to 1 cement and fine sand mixed to a consistency like thick cream. Under no circumstance should bonding coat be wet enough or applied heavily enough to make the dry material more than very slightly rubbery. Dry pack is usually a mix (by dry volume or weight) of one part of cement to 1.50 parts of sand that will pass No. 16 ASTM Screen.

    - PROCEDURE OF REPLACEMENT OF CONCRETE, CURING OR REPAIRS ETC.

All procedures for replacement of concrete, mortar replacement , use of epoxies and curing of repairs shall according to the provisions laid down in chapter VII "Repairs and Maintenance of Concrete" Concrete Manual of the United States Bureau of Reclamation, Seventh Edition 1963.

##### CURING OF CONCRETE

    - GENERAL

- All equipment, material etc, needed for curing and protection of concrete shall be at hand and ready for installing before actual, concreting begins. Detailed plans, methods and procedures whereby the various phases of curing and protection shall firmly established,. shall be settled and got approved in writing from the Engineer-in-charge sufficiently in advance of the actual concreting. The equipment and method proposed to be utilized shall provide for adequate control and avoid interruption or damage to the work of other agencies.

- All Concrete shall be cured by water in a accordance with the requirement of sub-clause (3) of this Clause or membrane curing in accordance with the requirement of sub-clause (4) of this Clause. Concrete surfaces to be painted shall not be cured by membrane curing.

    - WATER CURING

- Uniform top surfaces of walls and piers shall be moistened by covering with water saturated material or by other effective means as soon as the concrete has hardened sufficiently to prevent damage

by water i.e. normally after 24 to 36 hrs of placement of concrete. Exposed finished surfaces of concrete shall be protected against heating and drying from the Sun for at least 72 hrs after placement in location. When finishing or repairs are involved, concrete shall not be disturbed by workmen walking on it or by storing materials on the surface or otherwise for at least 10 hours after placing. These surfaces and steeply sloping and vertical formed surfaces shall be kept completely and

- concrete cured with water shall be kept wet for at least 21 days immediately following placement of the concrete or until covered with fresh concrete by covering with water saturated material or by a system of perforated pipes, or mechanical sprinklers or porous hoses or by any other suitable method, which will keep all surfaces continuously (not periodically) wet. For uncovered portions curing should continue for specified period.

- The contractor shall make arrangements at work site for storing the water required for at least 3 days curing. The concrete work shall not be started until the water required for 3 days curing is stored in advance.

    - MEMBRANCE CURING

- Membrane curing shall be by application of a suitable type of white / pigmented curing compound which forms a water retaining membrane on the surface of concrete, provided that on concrete surfaces which will be permanently exposed to view clear curing compound may be required excepting canal lining as per para 3.5.10. Curing compound shall be applied to the concrete surfaces after demonstrating its effectiveness as per para 3.5.10 by spraying one coat to provide a continuous uniform membrane over all area, with a maximum coverage per gallon as prescribed by he manufacturer's instructions according to the roughness of the surface to be covered. If necessary to cover the surface adequately, a second coat of curing compound shall be applied by spraying at right angle to the direction at which the first coat was applied. Mortar encrustations and fines on surfaces for which finish F4 is specified shall be removed prior to application of curing compound. Curing compound shall be applied to all areas of concrete surface except that those areas with surface imperfections which shall be omitted until repaired.

- When curing compound is to be used for unformed concrete surfaces, application of the compound shall commence immediately after the finishing operations are completed.

- When curing compound is to be used on formed concrete surfaces, the surface shall be moistened with light spray of water immediately after the forms are removed and shall be kept wet until the surfaces do not absorb more moisture. As soon as the surface film of moisture disappears but while the surface still has a damp appearance, the curing compound shall be applied. There must be ample coverage with compound at edge, corners and rough spots of formed surface. After application of curing compound has

been completed and the coating is dry to the touch, any required repairs of concrete surfaces shall be performed. Each repair, after being finished, shall be moistened and coated with curing compound in accordance with the foregoing requirements.

- Traffic and other construction operation shall be such as to avoid damage to coating of curing compound for a period of not less than 28 days after application of the curing compound. Where it is impossible because of construction operations to avoid traffic over surfaces coated with curing compound, the membrane shall be protected by a covering of sand or earth not less than 25 mm in thickness or by other effective means. The protective covering shall not be placed until the sealing membrane is completely dry. Any sealing membrane, that is damaged or that peels from concrete surface within 28 days after application, shall be repaired without delay.

- Curing compound shall be of approved quality.

##### 3.16 REQUIREMENT OF CONCRETE CONSTRUCTION

    - GENERAL

All concrete construction shall conform to the permissible tolerance and technical provisions as described in this section and to the detailed requirement of the following paragraphs. All structures shall be build in a workmanlike manner or to the lines, grades and dimensions shown in the drawing or as prescribed by the Engineer-in-charge. The location of all the construction joint shall be subject to the approval of the Engineer-in-charge. The dimensions of each structure shown on the drawings are tentative and shall be subjects to such change as may be found necessary by the Engineer-in-charge due to design considerations.

    - CONCRETE IN VARIOUS COMPONENTS OF BRIDGES, DRAINAGE SYPHON AQUEDUCTS, ETC.,

- The items of the schedule B for concrete in aforesaid structures include all concrete in the various components of the structure and block outs.

- Expansion joints shall be constructed as shown on the drawing or as directed. Pre moulded bituminous fibre type expansion joint material shall be placed in the expansion joints. Lighting recesses shall be constructed in the parapets as directed by the Engineer-in-charge. Open joints or false joints shall be constructed as shown on the drawings or as directed by the Engineer-in-charge. Performed expansion joint filler shall be placed in the road way and side walls where shown on the drawing or as directed by the Engineer-in-charge.

    - CONCRETE IN BLOCKOUTS

- All concrete required to be placed in block outs to permit the installation and adjustment of mechanical and other equipments shall be included in the respective concrete as described above. The concrete surface of the blackouts shall be chipped and roughened as described hereinafter before the concrete is placed in block outs.

- Exceptional care shall be taken in placing the concrete in block outs in order to ensure satisfactory bond with the concrete previously placed and to secure complete contact with all metal work in the block outs.

- The roughening of the concrete surface of the block outs shall be performed by chipping or sand blasting as approved by the Engineer-in-charge and in such a manner as not to loosen, crack or shatter any part of the concrete beyond the roughened surface. After being roughened the surface of the concrete shall be cleaned thoroughly of loose fragment, dirt and other objectionable substances and shall be sound and hard to ensure good mechanical bond between the existing and new concrete. All concrete which is not hard, dense and durable shall be removed to the depth required to the satisfaction of the Engineer-in- charge.

    - EMBEDMENT IN CONCRETE

In some of the locations of structures as shown on the relevant drawings a few conduits or openings shall have to be provided through R.C.C. / P.C.C. / masonry work. Construction of the surface for either placement of concrete or for laying of masonry shall have to be suitably carried out as to meet with the placement of such conduits or openings. No extra claim for such construction shall be entertained.

##### CONSTRUCTION JOINTS IN UNREINFORCED CONCRETE WALLS

- Concreting shall be carried out continuously up to the construction joins, the position and details of which shall be as shown on approved Drawing or as directed by the Engineer-in-charge.

- For vertical construction joints stopping boards shall be fixed previously at a predetermined position and shall be properly stayed for sufficient lateral rigidity to prevent its displacement or bulging when concreting is completed against it. Concreting shall be continued right up to the board. The board shall not be removed before expiry of the specified period for removal of vertical forms.

- Before resuming work at any construction joints when concrete has not yet fully hardened, all laitance shall be removed thoroughly, care being taken to avoid dislodgement of coarse aggregates. The surface shall be thoroughly wetted and all free water removed from the surface shall then be coated with cement slurry. On this surface, layer of concrete not exceeding 150 mm in thickness shall first be placed

and shall be well rammed against old work particular attention being paid to corners and closed spots, work thereafter shall proceed in a normal way.

- When work has to be resumed on a surface, which has hardened, it shall be thoroughly raked, swept clean, wetted and covered with a layer of neat cement grout. The neat cement grout shall be followed by a 15 mm thick layer of mortar mixed on the same proportion as in concrete and concreting resumed immediately thereafter. The batch of concrete shall be rammed against the old work to avoid formation of any stone pockets, particular attention being paid to corners and close spots.

In all cases, the position and detailed arrangements of all construction joints shall be predetermined and got approved by the Engineer-in-charge.

##### TEST AND ACCEPTANCE CRITERIA.

GENERAL

Samples from fresh concrete shall be taken as per IS : 1199-1959 and Cubes shall be made, cured and tested at 28 days in accordance with IS : 516-1959

NOTE : For relatively small and isolated works in which quantity of concrete is less than 15 cum the strength tests may be waived by the Engineer-in-charge at his discretion.

In order to get a relatively quicker ideas of the quality of concrete, optional tests on eams for modulus of rupture at 72 + hrs. or at 7 days, or compressive strength tests at 7 days may be carried out in addition to 28 days compressive strength tests. For this purpose the values given in Table 5 may be taken for general guidance in the case of concrete made with ordinary Portland cement. In all cases, the 28 days compressive strength specified in Table 1 shall alone be the criteria for acceptance or rejection of the concrete. If however, from tests carried out in a particular job over a reasonably long period, it has been established to the satisfaction of the Engineer-in-charge that a suitable ratio between 28 days compressive strength at 7 days may be accepted, the Engineer-in-charge may suitably relax the frequency of 28 days compressive strength specified in 14.2 of IS : 456-1978 provided the expected strength values at the specified early age are consistently met.

TABLE - 5 OPTIONAL REQUIREMENT OF CONCRETE

(Clause 14.1.1 of IS : 456-1978)

Grade of	Compressive strength	Modules of Rupture by Beam Test

| Concrete | On 15 cms Cubes Min. At 7 days N/sq mm | Min. at 72+ hrs. N/sq mm. | Min at 7 days N/sq mm |
| --- | --- | --- | --- |
| 1 | 2 | 3 | 4 |
| M 10 | 7.0 | 1.2 | 1.7 |
| M 15 | 10.0 | 1.5 | 2.1 |
| M 20 | 13.5 | 1.7 | 2.4 |
| M 25 | 17.0 | 1.9 | 2.7 |
| M 30 | 20.0 | 2.1 | 3.0 |
| M 35 | 23.5 | 2.3 | 3.2 |
| M 40 | 27.0 | 2.5 | 3.4 |

FREQUENCY OF SAMPLING SAMPLING PROCEDURE :

A random sampling procedure shall be adopted to ensure that each concrete batch shall have a reasonable chance of being tested ; that is, the sampling should spread over the entire period of concreting and cover all mixing units.

FREQUENCY :

The minimum frequency of sampling of concrete of each grade shall be in accordance with the following :

Quantity of Concrete	Number of

in the work, Cum.	Samples

1 to 5	1

6 to 15	2

16 to 30	3

31 to 50	4

51 and above	4 plus one additional sample

for each additional 50 cum or

part thereof.

Note : At least one sample shall be taken from each shift.

TEST SPECIMEN :

Three test specimens shall be made from each sample for testing at 28 days. Additional cubes may be required for various purposes, such as to determine the strength of concrete at 7 days or at the time of striking the formwork, or to determine the duration of curing or to check the testing error. Additional cubes may also be required for testing cubes cured by accelerated methods as described in IS : 9013- 1978*. The specimen shall be tested as described in IS : 516-1959.

TEST STRENGTH OF SAMPLE :

The test strength of the sample shall be the average of the strength of three specimen. The individual variation should not be more than plus or minus 15 percent of the average.

STANDARD DEVIATION :

Provision made under para 3.7.5 shall apply.

ACCEPTANCE CRITERIA:

The provision made under para 3.7.6 shall apply.

CORE TEST

The locations at which cores are to be taken and the number of cores required shall be at the discretion of the Engineer-in-charge and shall be representative of the whole of concrete concerned. In no case, however, fewer than three cores shall be tested.

Cores shall be prepared and tested as described in IS : 516-1959*.

Concrete in the member represented by a core test shall be considered acceptable if the average equivalent cube strength of the cores is equal to at least 85 percent of the cube strength of the grade of concrete specified for the corresponding age and no individual core has a strength less than 75 percent.

In case the core test results do not satisfy the requirements of IS : 456-1978 or where such tests have not been done, load test (as per IS : 456-1978) may be resorted to.

HYDRAULIC TEST

After curing period of the water retaining structure is over, a hydraulic test shall be carried out. Water should be filled in the structure to the designed depth and maintained for a period of 7 days. Starting from the end of 7 days, observations of water level will be made for a period of 7 days. The drop in the water level observed should correspond to evaporation loss applicable to circumstances. There should also be no visible dampness or sweating on the exposed surfaces. In case of leakage, rectification work shall be

carried out to achieve the desired water tightness. After rectification is done hydraulic tests shall be repeated.

##### STEEL REINFORCEMENT

The provision made under Section No. V shall apply.

##### TOLERANCE IN CONCRETE CONSTRUCTION

    - GENERAL

- Permissible surface irregularities for the various classes of concrete surface finishes specified in he relevant portion of the paragraph of "Finishes and Finishing of Concrete Surfaces", are defined as "finishes" and are to be distinguished from "Tolerance" as described in this section. Deviation from the established lines, grades and dimensions shall be permitted to the extent set forth in this clause, provided that lesser tolerance than that set forth in this clause may be prescribed at site if such tolerances are considered to impair the structural action or operational action or operational function of the structure.

- Where tolerances are not stated in the specifications or drawings for any individual structure of feature thereof, permissible deviations shall be interpreted in conformity with the provisions of this Clause.

- Concrete work that exceeds the tolerance limits specified in this section shall be either remedied satisfactorily or removed.

    - TOLERANCE FOR CANAL STRUCTURE

Variation in alignment, grade and dimensions of the structures from the established alignment, grade and dimensions shown on the drawings shall be within the tolerances specified in Table below. Variation shall not be cumulative. Where the provisions of paragraph 4.14, "finishes and finishing of concrete surfaces", as specified herein before, would permit greater variations than those allowed in the table, provisions of the table given on the following page shall apply.

TABLE

- Pipe Culverts, float wells and similar structures

  - Departure from established alignment	25mm

  - Departure from established grade	25 mm

  - Variation from plumb or specified batter for

lines and surfaces of columns, piers and walls and for arises. When overall length of line or surface is :

3 mtrs or less	Exposed	10mm

Buried	20 mm

More than 3 mtrs. Exposed	12 mm Buried		25mm

  - For any two successive intermediate points on the line or surface separated by

3 mtrs or less	Exposed	10mm

Buried	20mm

More than 3 mtrs. Exposed	12mm Buried		25mm

- Variation from level or specified grades for slabs.

  - When overall length of line or surface is :

3 mtrs. or less	Exposed	10mm

Buried	20mm

More than 3 mtrs. Exposed	12mm Buried		25mm

  - For any two successive intermediate points on the line or surface separated by :

3 mtrs or less	Exposed	10mm

Buried	20mm

More than 3 mtrs	Exposed	12mm Buried		25mm

- Variation in cross-sectional dimensions of columns, beams, slabs, walls and similar members of

...................................................minus	6mm

...................................................plus	12mm

- Variation in sizes and locations from those specified for slab

and wall openings.	12mm

- Variation fom plumb or pipe erected vertically in any length of

.................................................3mtrs.	12mm

- Tolerances for bridges :

  - Departure from established

alignment..................................................	6mm

- Footings

  - Variation of dimensions

in plain ........................................................minus	12mm

..........................................................plus	50mm

  - Misplacement of eccentricity	2 percent of the footing width in the

direction of misplacement but not more than 50mm

  - Reduction in thickness...........	.	5 percent of specified thickness.

- Variation from plumb or specified batter for lines and surfaces of piers and walls.

- Exposed construction :

When overall height of line or surface is :

3 mtrs or less.	10mm

more than 3 mtrs.	12mm

for any two successive intermediate points on the line or surface separated by :

3 mtrs or less.	10mm

more than 3 mtrs.	12mm

- Buried construction	Twice the amounts

listed in h(I) above.

- Variation from level of specified grades for beams Horizontal grooves, railing off sets and diaphragms :

- Exposed Constructions :

When overall length of line or surface is :

3 mtrs or less.	10mm

more than 3 mtrs.....................................................	12mm

For any two successive intermediate points on the line or surface separated by :

3 mtrs or less.	10mm

more than 3 mtrs.	12mm

- For buried construction	Twice the amounts listed in 1(i) above

- Departure of bridge deck and rails from

specified grades.	6mm

- Variation in cross-sectional dimensions from those specified for piers, walls, beams and similar parts of bridge structures.

...............................................minus	6mm

................................................plus	12mm

- Variation from that specified in the

thickness of bridge slabs ............. minus	3mm

............. plus	6mm

    - a) GENERAL :

Bulges, Depressions and offsets are defined as concrete Surface irregularities. concrete surface irregularities are classified as "abrupt" or "gradual" & are measured relative to the actual concrete surface.

- ABRUPT SURFACE IRREGULARITIES:

Abrupt surface irregularities are defined herein as offsets such as those caused by misplaced or loose forms, loose knots in form member, or other similar forming faults. Abrupt surface irregularities are measured using a short straight edge, at least 15 cms. long held firmly against the concrete surface over the irregularity and the magnitude of the offset is determined by direct measurement.

- GRADUAL SURFACE IRREGULARITIES :

Gradual surface irregularities are defined herein as bulges and depressions resulting in gradual changes on the concrete surface. Gradual surface irregularities are measured using a template conforming to the design profile of the concrete surface being examined. Templates for measuring gradual surface irregularities shall be provided by the contractor, templates shall be at least 2.5 mtrs. in length. The magnitude of gradual surface irregularities is defined herein as a measure of the rate of change in slope of the concrete surface.

- The magnitude of gradual surface irregularities on concrete surfaces shall be checked by the contractor to ensure that the surface are within specified tolerances. The department will also make such checks of hardened concrete surfaces as determined necessary to ensure compliance with these specifications. Templates for these surface shall be furnished by the concrete free of change and shall be available for use by the department at all times.

##### UNACCEPTABLE WORK

All defective concreting work, including those due to honeycombing, under sizing, under-strength etc. shall be demolished and rebuilt by the contractor at his cost. In exceptional cases where such work is accepted by the Engineer-in-charge after the contractor has made specified repairs, all cost of repairs shall be borne by the contractor. Acceptance of such works will be in accordance with the provisions of IS : 456-1978. In the event of the work being accepted, allowing under sizing commensurate with higher materials strength and accepting materials not fully meeting the specifications etc. the contractor shall be paid for the work actually carried out by him at a reduced rate derived from the tendered rate as approved by the Engineer- in-charge.

##### MEASUREMENTS FOR PAYMENT

Payment as per payment schedule

##### SCOPE OF WORK

SECTION - IV REINFORCEMENT

The work includes supplying, cutting, bending, binding, welding and erecting in position high yield strength deformed (H.Y.S.D.) steel bars and mild steel (M.S.) bars as reinforcement for concrete of various components of drainage syphons, syphon aqueducts, road bridges, cross regulators, head regulators, escapes, lining and other structures.

##### INDIAN STANDARDS FOR REFERENCE

- IS : 226-1975	Structural steel (Standard Quality).

- IS : 280-1978	Mild steel wire for general Engineering purposes.

- IS : 432-1966	Mild steel and medium tensile bars and drawn stead

wire for concrete reinforcement

- IS : 432-1966(part-I)	Mild Steel and medium tensile steel bars.

- IS : 432-1996 (part-V) Hard drawn steel wire.

- IS : 814-1974	Covered electrodes for metal or welding of structural

steel.

- IS : 814-1974(part-I)	For welding products other than sheets.

- IS : 814-1974(part-II)	For welding sheets

- IS : 1139-1966	Hot rolled mild steel medium tensile steel and high

yield strength steel deformed bars for concrete

- IS : 1278-1972	Filler rods and wires for gas welding.

- IS : 1481-1970	Metric steel scales for Engineers.

- IS : 1521-1972	Method for tensile testing of steel wires.

- IS : 1566-1967	Hard drawn steel wire fabrics for concrete

reinforcement.

- IS : 1608-1972	Method for tensile testing of steel products.

- US : 1786-1979	Cold twisted steel bars for concrete reinforcement.

- IS : 2502-1963	Code of practice for bending and fixing of bars for

concrete reinforcement

- IS : 2751-1979	Code of practice for welding of mild steel bars used

for reinforced concrete construction.

- IS : 5525-1969	Recommendations for detailing of reinforcement in

reinforced concrete works.

- IS : 9417-1979	Recommendations for welding cold worked steel bars

for reinforced concrete construction

In addition to the above the relevant Indian Standard codes referred to in Section IV shall also apply.

##### STEEL REINFORCING BARS

    - GENERAL

- Steel reinforcing bars shall be placed in concrete where shown on the drawings or as directed by the Engineer-in-charge. The drawings issued with these specifications show only in part the requirement of reinforcement and further drawings shall be issued by the Engineer-in-charge during the course of the contract.

- As far as possible, high yield strength deformed bars conforming to IS : 1786-1979 shall be used as reinforcement. However, in case of Non-availability of such bars other steel bars conforming to IS : 432- 1966 and / or IS : 1139-1966 shall be used as per the directions of the Engineer-in-charge.

    - CUTTING, BENDING AND BINDING

- The contractor shall be responsible for the accuracy of the cutting, bending and placing of the reinforcement. Reinforcement shall be inspected for compliance with the requirement of grade, size, shape, length splicing and locations after it has been placed. No concreting shall be started unless the reinforcement as placed in the work is finally checked, recorded and certified by the Engineer-in-charge.

- Before the reinforcement is placed, the surface of the bars and the surfaces of any metal bar supports shall be cleaned of the rust, loose mill scale, dirt, grease and other objectionable foreign substances. After being placed, the reinforcing bars shall be maintained in a clean condition until they are completely embedded in the concrete.

- Reinforcing bars shall be accurately placed and secured in positions as shown in the drawing so that the bars and fabric shall not be displaced during the placing of concrete. The contractor shall also ensure that there is no disturbance of reinforcing bars already placed.

- Wire for binding reinforcement shall be of soft and annealed mild steel and shall conform to IS : 280- 1978. The binding wire shall have tensile strength of not less than 56kg/sqmm. The wire shall have minimum diameter of 1 mm. Chairs, hangers, spacers and other supports for reinforcement, may be of concrete, metal or other approved material. Where portions of such supports will be exposed on concrete surfaces designated to receive F2 or F3 finish, the exposed portion of support shall be galvanized or coated with other corrosion resistant material without which the concreting will not be permitted. Such supports shall not be exposed on surfaces of F4 finish unless otherwise shown on the drawings. The minimum allowable clearance between parallel round bars shall not be less than 1.50 times the diameter of the larger bars and for square bars shall not be less than twice the side dimensions of the larger bars. In no case the minimum clearance between the bars shall be less than 1.50 times the maximum size of aggregate irrespective of the shape of the reinforcing bar. Bars crossing each other where required shall be secured by binding wire in such a manner that they do not slip over each other at the time of fixing and concreting. Wire used for binding reinforcement shall not be measured for payment.

    - SPLICING

- Where it is necessary to splice reinforcement the splices shall be made by lapping, by welding or by mechanical means.

- Joints or splices in reinforcing bar shall generally be made at the locations where neither shear nor bending moment is maximum, but the contractor would be permitted to take joints or splices at other position provided that such positions are approved by the Engineer-in-charge and joints and splices in adjacent bars are staggered as directed by the Engineer-in-charge. Approval of such additional splices will generally be restricted to splices not closer than 9 mtrs. in horizontal bars and 4 mtrs. in vertical bars measured between midpoint of laps.

- If the contractor proposes to use welded splices in reinforcing bars the equipment, the material and all welding testing procedures shall be subject to the approval of the Engineer-in-charge. The contractor shall also carry out test welds as required by the Engineer-in-charge.

- For welded splices for reinforcing bars conforming to IS : 1786-1979, welding shall be done in accordance with IS : 9419-1979. For reinforcing bars conforming to IS: 432 (part-I) 1966 and IS : 1139- 1966 welding shall be done in accordance with IS : 2751-1966. Electrodes for manual metal arc welding shall confirm to IS : 814 (part-I) 1974 and IS : 814 (part-II) 1974, mild steel filler rods for oxyacetylene welding shall conform to IS : 1278-1972 provided they are capable of giving a minimum butt weld tensile strength of 41 kg / sq mm.

- Reinforcing bars 28mm in diameter and larger may be connected by butt welding, provided that lapped splices will be permitted if found to be more practicable than butt welding and if lapping does not encroach on cover limitation or hinder concrete or reinforcement placing.

- Reinforcing bars 25mm diameter and less may be either lapped or butt welded, whichever is most practicable.

- Butt welding of reinforcing bars shall be performed under cover from weather and may be performed either by the gas pressure or flash pressure welding process, or by the electric arc methods. The following requirements shall apply to all welding of reinforcing bars including butt welding and the preparation of welded reinforcement mats.

- Welded pieces of reinforcement shall be tested at the rate of 5% of total number of joints welded. Specimen shall be taken from the actual site of work. Strength of the weld provided shall be at least 25% higher than the strength of bar.

- If the contractor proposes to use mechanical couplings for reinforcing bars he shall submit samples of the proposed coupling to the Engineer-in-charge for approval not less than 60 days prior to their proposed use.

    - CARE OF PLACED REINFORCEMENT AND CONCRETE

Where reinforcement bars are bent aside at construction joints and afterwards bent back into their original position, care shall be taken to ensure that at no time the radius of the bend is less than 6 times the diameters for deformed bars and 4 times diameters for plain mild steel bars. Care shall also be taken, when bending such bars, to ensure that the concrete around the bars is not damaged.

LAPPED SPLICES

| Diameter of bar | Grade of Bar | Minimum length of overlap in straight splice |
| --- | --- | --- |
| 6mm | Structural Plain | 30 cm |
| 10mm | Structural Plain | 46 cm |
| 12 mm | Structural deformed | 38 cm |
| 16 mm | Structural deformed | 48 cm |
| 20 mm | Structural deformed | 58 cm |
| 22 mm | Structural deformed | 66 cm |
| 25 mm | Structural deformed | 86 cm |
| 30 mm | Structural deformed | 97 cm |
| 35 mm | Structural deformed | 107 cm |

##### SCOPE OF WORK

SECTION – V RUBBLE MASONRY

The work covered under this section consists of furnishing all material, equipment and labour for providing and laying uncoursed rubble masonry in substructure and superstructure and performing all functions necessary and ancillary thereto and including pointing of exposed surfaces and curing. This also includes dewatering if required.

##### INDIAN STANDARDS FOR REFERENCE

- IS : 1121 - 1974 Method	of	test	for	determination	of	strength	properties (All parts)of natural buildings stones

- IS : 1122 - 1974 Method of test for determination of true specific gravity of natural building stones.

- IS : 1123 - 1975 Method of identification of natural building stones

- IS : 1124 - 1974 Method of test for determination of water absorption, apparent specific

gravity and porosity of natural building stones.

- IS : 1125 - 1974 Method of test for determination of weathering of natural building stones.

- IS : 1126 - 1974 Method of test for determination of durability of natural building stnvs.

- ÉS : 1127 - 1970	Recommendations for dimentions and workman ship of natural

building stone for masonry work.

- IS : 1129 - 1972 Recommendations for dressing of natrual building stone

- IS : 1542 - 1977 Sand for plaster.

- IS : 1597 - 1967 Code of practice for construction of stone masonry

- IS : 1597 - 1967 Rubble stone massonry Part I

- IS : 1706 - 1972 Method of determination of resistance to wear by abrasion of natural

building stones.

- IS : 2116 - 1980 Sand for masonry mortars.

- IS : 2250 - 1981 Code of practice for preparation and use of masonry mortars.

- IS : 1401 - 1967	Stone facing	Part I

- IS : 4121 - 1967 Method of test for determination of water transimssion rate by capillary action through natural b|ilding stones.

- IS : 4122 - 1967 Method for the surface ³oftening of natural building stones by exposure to

acidic atmosphere

- IS : 4348 - 1973 Method of test for determination of permeability of natural building stones.

- IS : 5218 - 1969 Method of test for toughtness of natural building stones

- IS : 7779	Engineering properties of building stones

- IS : 8381 - 1977 Recommended practice for quarrying stones for construction purposes.

##### MATERIAL

    - CEMENT

The provisions of sub - para 3.5.1 shall apply.

    - WATER

The provisions of sub - para 3.5.4 shall apply.

    - SAND

      - Sand to be used in mortar shall conform to IS : 2116 - 1980 and the gradation limits given

below :

| I.S. sieve designation | Percentage by weight passing I.S. sieve |
| --- | --- |
| 4.75 mm | 100 |
| 2.36 mm | 90-100 |
| 1.18 mm | 70-100 |
| 600 Micron | 40-100 |
| 300 Micron | 5-70 |
| 150 Micron | 0-15 |

      - The provisions of sub-para 3.5.2 shall also apply

      - Before collecting the sand required for mortar for the masonry work, the contractor shall ensure that the sample of sand proposed to be used are supplied to the project laboratory for casting the mortar cubes, and material shall be collected only after ascertaining the results of the test on the mortar cubes. During the execution of the work sand collected at site shall also be tested for all specification requirements.

    - RUBBLE (STONES)

Stone shall be hard, sound free from cracks,decay and weathering. Stone shall be used from surplus usable excavated rubble or from the approved quarries, if required. Stone with round surface shall not be used. Stones when immersed in water for 24 hours shall not absorb water by more than one percent of their dry weight when tested in accordance with IS:1125 -1974.

The length of stone shall not exceed three times its height and the breadth on the base shall not be greater than three fourth of the thickness of wall and in any case not less than 15 cm. Minimum crushing strength of stones shall not be less than 600 Kg/Sqcm.

###### U.C.R. Masonry

    - MORTAR

The mortar shall consist of cement, sand and water thoroughly mixed in the proportion as specified. Proportion of cement and sand shall be on weight basis as specified in schedule -B. Due allowance shall be made for the moisture content in sand. Mixing water shall be added to achieve required workability.

    - MIXING

- The mortar shall be mixed in mechanical mixers of tilting type having calibrated water tank for storing water. The first batch of the mortar at the commencement of work with any mixer shall be made richer by adding 10 percent more cement over and above that required for the particular mix. In case of mechanical mixing, the mortar shall be mixed for at least 3 minutes after addition of water. Hand mixing shall not be allowed. However, in exceptional circumstances such as mechanical break down of mixer, work in remote areas or when the quantity of work is very small, mixing in hand operated mixers shall be permitted.

- All ingredients shall be fed to the mixer simultaneously. The quantity of water to achieve the required consistency shall be predetermind by trial mixes, and proportion of water from 5 to 10 percent shall precede and lthe like quantity shall follow the introduction of other materials. The remainder of water quantity shall be added during mixing operation.

- The wet mortar shall be used within 30 minutes of mixing, mortar remaining unused, after above time shall be rejected and shall not be allowed to be used.

    - MODE OF LAYING

- The dressing of stone shall conform to the general requirements covered in IS : 1129-1972. Stone shall be sufficiently wetted before laying to prevent absorption of water from mortar. All stones shall be laid full in mortar both in bed and in vertical joints and settled carefully in place with a wooden mallet immediately on placement so that it is firmly bedded in before the same has set. Clean chips and spalls shall be wedged into the mortar joints and beds wherever necessary to avoid thick beds or joints of mortar. Whenever foundation masonry is laid directly on rock, the face stones of the first course shall be dressed to fit into the rock snughly when pressed down in the mortar bedding over the rock. No dry or hollow space shall be left anywhere in the masonry and each stone shall have all the embedded faces completely covered with mortar. Vertical joints shall be staggered. Transverse bond shall be provided by the use of bond stones extending from the front to the back of the masonry. In case of thick walls beyond 60 cm,

bond stones shall overlap each other in their arangement. Overlap shall not be less than 15 cms. Bell shaped bond stones or headers shall not be used.

Bond stone shall be stacked separately and marked to distinguish it from other stones. Masonry work shall be started after sufficient number of bond stones are collected on site as directed by the Engineer-in- charge. Bond stones shall be inserted at the rate of one per square meter and shall be staggered.

- At all angular junctions, stones at each alternate course shall be well bonded into the respective course of the adjacent wall. All connected masonry in sturctures shall be carried up at one uniform level throughout as far as possible, but when breaks are unavoidable the masonry shall be in sufficient long steps to facilitate jointing of new work with old. Stepping shall not be more than 45 degrees with the horizontal. Masonry work shall be carried out to truly plumb or to the specified batter. Face work and hearting shall be brought up evenly. The top of each course, however, shall not be levelled up by use of flat chips. Chips and spalls of stones may be used wherever necessary to avoid thick mortar beds or joints and it shall also be ensured that not hollow spaces are left anywhere in the masonry. Chips shall not be used below hearting stones to bring these up to level of face stones. Use of chips shall be restricted to filling of interstices between the adjacent stones in hearting and they shall not exceed 20 percent of the quantity of stone masonry.

- Hearting or interior filling of water face shall consist of rubble stones, not less than 15 cm. in any direction carefully laid, hammered down with a wooden mallet into position and firmly bedded in mortar. Hearting should be laid nearly level with facing and backing.

- The joint shall not be more than 25 mm thick but shall be sufficiently thick to prevent stone to stone contact and shall be completely filled with mortar. The total content of mortar in masonry shall not be less than 40% and not more than 48% of the volume of masonry.

- When fresh masonry is to be placed against existing surface of structure, the old surface shall be cleaned of all loose material, roughened and wetted as directed by the Engineer-in-charge so as to achieve a good bond with the new work.

- The scaffoliding shall be sound and strong to withstand all loads likely to come upon it. The holes which provide resting space for horizontal members shall not be left in masonry. The holes left in the masonry work for supporting the scaffolding shall be filled.

- Green work shall be protected from rain by suitable cover. Mansory work in cement mortar shall be kept consistently moist on all faces for a minimum period of twenty one days after 24 hours of construction and continuous for 21 days. Watering should be done carefully so as not to washout the mortar, joints or disturb the masonry in any manner. During hot weather all finished or partly completed work shall be covered or wetten in such a manner as to prevent drying. The raking of joints where necessary shall be done at the end of day's work when mortar is green.

    - MEASUREMENT AND PAYMENT

Payment as per payment schedule.

##### POINTING

    - GENERAL

- For a surface, which is to be subsequently pointed, the joints shall be squarely raked out to a depth of 20 mm. While the mortar is still green. The raked joints shall be well brushed to remove dust and loose particles and the surface shall be thoroughly washed and cleaned.

- Mortar required for pointing shall be prepared in accordance with the provisions of para No. 7.4.1 and 7.4.2. The cement and sand shall be used in proportion as specified in the respective items or as directed by the Engineer-in-charge.

- For pointing, mortar shall be filled and pressed into the raked out joints before giving the required finish. Superfluous mortar shall be cut off from the edges of the lines and the surface of the masonry shall also cleared of all mortar.

- Curing shall be started as soon as the mortar used for finishing has hardened sufficiently not to be damaged when watered. It shall be kept wet for a period of atleast 21 days. During this period it shall be suitably protected from all damages.

    - MEASUREMENT AND PAYMENT

Payment as per payment schedule.

##### TEST FOR MORTAR FOR CONSTRUCTION OF MASONRY

- At least one set of test cubes of cement mortar used shall be taken for each day's work and it shall be tested for 28 days strength.

- From the design mortar mix, cubes using the material shall be cast in the laboratory at suitable intervals and their strength be determined. This strength shall deemed as the standard strength for that mortar. The strength of the test cubes shall be found out and shall not be less than 80% of the standard strength mentioned above. For acceptance, the 28 days strength of test cubes shall be the the criteria, 80 percent of the test cubes should satisfy the above criteria. All laboratory testing work shall be carried out by

the department as per relevant Indian standards and the contractor shall be permitted to watch the test if he so desires.

##### SECTION - VI REVETMENT AND PITCHING

  - The bed or slope to receive the pitching or revetment shall be prepared true to line and grade and shall be moistened and well rammed so as to present a clear uniform compact surface.

  - The stones shall be hard, sound and durable and as regular in shape as possible and with length not less than specified. Each stone shall not be less in size than 0.015 cum unless otherwise specified or ordered by the Engineer-in-charge, having regard to nature of the stone obtainable in the approved source. For revetment only the size stones shall be used.

  - The stones shall be laid closely in position on the prepared bed and firmly set with their narrowest end downwards and level with the finished surface of the pitching. The stones shall be laid breaking joint as far as possible, in the direction of flow of water. The stones are to be placed perpendicular to the finished surface. i.e. perpendicular to the slope for revetments and to the specified thickness.

  - The interstices between adjacent stones shall be filled in with stone spalls of the, proper size, well driven in with crowbars to ensure tight packing and complete filling of all interstices. Such filling shall be carried on simultaneously with the placing in position of the large stones and shall in no case be permitted to fall behind. The final wedging shall be done only after obtaining the orders of the Engineer-in-charge. The final wedging shall be done with the largest sized chips practicable, each chip being well driven with a hammer so that no chip is possible at being picked up or removed by hand.

  - Profiles of string and pegs are to be put up to ensure that the pitching is done true, straight, and to the proper slope throughout and revetments in all cases are to be built up from the foot of the bank to be revetted.

  - On completion, the surface presented by the apron or revetment shall be even throughout, free from irregularities, to the required length, breadth and slope specified as shown in the drawings.

  - When use of rubble of canal spoils is specified, rubble required for the work shall be issued at the nearest available stacks of the excavated materials of the canal in the reach concerned or in any of the adjoining reaches if available. The contractor shall sort out useful rubble, hammer dress to the required size shape and convey the same to the work spot at his cost.

  - MEASUREMENT AND PAYMENT

Payment as per payment schedule.

SECTION – VII

SUPPLYING AND LAYING PERFORATED PRESSURE RELIEF PIPES

  - Pipes of specified classes shall be procured by the contractor at the site of work. No pipe shall be placed in position until the foundations have been approved by the Engineer-in-charge

  - The laying of pressure relief pipes within the sub structure shall start from the outlet proceed towards the inlet and shall be completed to the specified lines and grades. The pipes shall be fitted and matched.

  - Any pipe found defective or damaged during laying shall be removed and replaced by the contractor at his cost.

  - MEASUREMENTS AND PAYMENTS

Payment as per payment schedule.

  - The amount quoted shall include the cost of pipes transportatin, handling, storing, laying in position and jointing pipes and also the cost of preparing specified bedding.

SECTION - VIII

SUPPLYING AND LAYING PIPES FOR DRAINAGE SPOUTS

  - Drainage Spouts of specified classes shall be procured by the contractor at the site of work.

  - The laying of Drainage Spouts within the deck slab shall start from the outlet proceed towards the inlet and shall be completed to the specified lines and grades.

  - Any Drainage Spouts found defective or damaged during laying shall be removed and replaced by the contractor at his cost.

  - MEASUREMENTS AND PAYMENTS

Payment as per payment schedule.

  - The amount quoted shall include the cost of transportatin, handling, storing, laying in position.

SECTION - IX

ELASTOMERIC BEARING

  - General

Elastomeric bearing conforming to IRC - 83 (part II) section-I and as per the MOST specification 2005 is to be used.

  - Placing

Elastomeric bearing pads of required size shall be fixed in position true to Line and lEVEL AS directed by Engineer - incharge. It includes cost and conveyance of all materials, labour and fabrication machinering inputs, gascutting, straightening, mixing neoprene with respect with respect to nodules with chemicals, vulcanising of Elastomeric compound with reinforcement plates etc. as per drawing and as directed by Engineer-incharge.

  - Testing

The cost per cubic centimetrers shall be inclusive of one extra bearing for Testing, For Which no separate payment will be made and also for testing.

  - Measurement and payment

Measurement and Payment as per payment schedule.

SECTION – X

WATER STOPPER

  - Water bars are performed strips of impermeable material which are to be embedded in the concrete during construction so as to span across the joint and provide a permanent watertight seal during the whole range of joint movement. The most useful forms of water bars are strip with a central longitudinal corrugation and a central longitudinal hollow tube with thin walls with stiff wings. The material used for the water bar are synthetic rubbers and plastics have very considerable advantage in handling, splicing and in making intersections.

With all water bars, it is important to ensure proper compaction of the concrete. The bar should have such shape and width that the water path through the concrete round the bar should not be unduly short. The water bar should either be placed centrally in the thickness of the wall or its distances from either side of the wall should not be less than half the width of the bar. The full concrete cover to all reinforcement should be maintained.

  - Joint sealing compound: Joint sealing compounds are impermeable ductile materials which are required to provide a watertight seal by adhesion to the concrete throughout the range of joint movement. The commonly used materials are based on asphalt, bitumen, or coal tar pitch with or without filters, such as lime stone or slate dust, asbestos fibre, chopped hemp, rubber or other suitable material. These are usually supplied after construction or just before the reservoir/delivery chamber are put into service by pouring in the hot or cold state. These may also be applied during construction such as by packing round the corrugation of water bar. For detailed specification refer IS 3370 (Part-I) – 1965.

  - MEASUREMENT AND PAYMENT

Measurement and Payment as per payment schedule.

SECTION-XI

G.I.PIPE HAND RAILS

  - G.I.Pipes of approved quality, confirming to the relevant IS code of 40mm dia. in three rows shall be fixed to RCC posts of CC M-15 grade of size 100mm x 100mm at top and 150mm x 150mm at bottom placed at a distance of 2 mtr. intervals at a height of 750mm. including curing, finishing etc.

Hand rails shall be properly jointed and installed and painted with two coats of paint as approved by Engineer-in-charge.

  - MEASUREMENT AND PAYMENT

Measurement and Payment as per payment schedule.

##### SECTION - XII

FLEXIBLE PAVEMENT

Site Clearance Clearing and Grubbing

  - Scope

This work shall consist of cutting, removing and disposing of all materials such as trees, bushes, shrubs, stumps, roots, grass, weeds, top organic soil not exceeding 150 mm in thickness, rubbish etc., which in the opinion of the Engineer are unsuitable for incorporation in the works, from the area of road land containing embankment, drains, cross-drainage structures and such other areas as may be specified on the drawings or by the Engineer. It shall include necessary excavation, back-filling of pits resulting from uprooting of trees and stumps to required compaction, handling, salvaging and disposal of cleared materials. Clearing and grubbing shall be performed in advance of earthwork operations and in accordance with the requirements of these Specifications.

  - Preservation of Property/Amenities

Trees, shrubs, any other plants, pole line, fences, signs, monuments, buildings, pipelines, sewers and all other facilities within or adjacent to the project site which are not to be disturbed shall be protected from injury or damage. The Contractor shall provide and install at his own expense, suitable safeguards approved by the Engineer for this purpose.

During clearing and grubbing, the Contractor shall take all adequate precautions against soil erosion, water pollution, etc., and where required, undertake additional works to that effect vide Clause 306 of MoRT&H. Before start of operations, the Contractor shall submit to the Engineer for approval, his work plan including the procedure to be followed for disposal of waste materials, etc., and the schedules for carrying out temporary and permanent erosion control.

  - Methods, Tools and Equipments

Only such methods, tools and equipment as are approved by the Engineer and which will not affect the property to be preserved shall be adopted for the work. If the area has thick vegetation/roots/trees, a crawler or pneumatic tyre dozer of adequate capacity may be used for clearance purposes. The dozer shall have ripper attachments for removal of tree stumps. All trees, stump such as roots, under-growth, grass and other deleterious matter unsuitable for incorporation in the embankment/subgrade shall be removed between fill lines to the satisfaction of the Engineer. On areas beyond these limits, trees and stumps

required to be removed as directed by the Engineer shall be cut down to 1 m below ground level so that these do not present an unsightly appearance.

All excavations below the general ground level arising out of the removal of trees, stumps, etc., shall be filled with suitable material and compacted thoroughly so as to make the surface at these points conform to the surrounding area.

Ant-hills both above and below the ground, as are liable to collapse and obstruct free subsoil water flow shall be removed and their workings, which may extend to several metres, shall be suitably treated.

  - Disposal of Materials

All materials arising from clearing and grubbing operations shall be the property of Department and shall be disposed of by the Contractor as hereinafter provided or directed by the Engineer.

Trunks, branches and stumps of trees shall be cleaned of limbs and roots and stacked. Also boulders, stones and other materials usable in road construction shall be neatly stacked as directed by the Engineer. Stacking of stumps, boulders, stones etc., shall be done at specified spots with all lifts and upto a lead of 1000 m.

All products of clearing and grubbing which, in the opinion of the Engineer, cannot be used or auctioned shall be cleared away from the project site in a manner as directed by the Engineer. Care shall be taken to see that unsuitable waste materials are disposed of in such a manner that there is no likelihood of these getting mixed up with the materials meant for embankment, sub grade and road construction.

  - Measurements for Payment

Clearing and grubbing for road embankment, drains and cross-drainage structures shall be measured on area basis in terms of hectares. Clearing and grubbing of borrow areas shall be deemed to be a part of works preparatory to embankment construction and shall be deemed to have been included in the rates quoted for the embankment construction item and no separate payment shall be made for the same. Cutting of trees upto 300 mm in girth including removal of stumps and roots, and trimming of branches of trees extending above the project area shall be considered incidental to the clearing and grubbing operations. Removal of stumps left over after trees have been cut by any other agency shall also be considered incidental to the clearing and grubbing operations.

Cutting, including removal of stumps and roots of trees of girth above 300 mm and backfilling to required compaction shall be measured in terms of number according to the sizes given below: -

- Above 300 mm to 600 mm

- Above 600 mm to 900 mm

- Above 900 mm to 1800 mm

- Above 1800 mm

For this purpose, the girth shall be measured at a height of 1 metre above ground or at the top of the stump if the height of the stump is less than one metre from the ground.

##### DISMANTLING CULVERTS, BRIDGES AND OTHER STRUCTURES / PAVEMENTS

  - Scope

This work shall consist of removing, as hereinafter set forth, existing culverts, bridges, pavements, kerbs and other structures like guard-rails, fences, utility services, manholes, catch basins, inlets, etc., which are in place but interfere with the new construction or are not suitable to remain in place, and of salvaging and disposing of the resulting materials and back filling the resulting trenches and pits.

Existing culverts, bridges, pavements and other structures which are within the highway and which are designated for removal, shall be removed upto the limits and extent specified in the drawings or as indicated by the Engineer.

Dismantling and removal operations shall be carried out with such equipment and in such a manner as to leave undisturbed, adjacent pavement, structures and any other work to be left in place.

All operations necessary for the removal of any existing structure which might endanger new construction shall be completed prior to the start of new work.

  - Dismantling Culverts and Bridges

The structures shall be dismantled carefully and the resulting materials so removed as not to cause any damage to the serviceable materials to be salvaged, the part of the structure to be retained and any other properties or structures nearby.

Unless otherwise specified, the superstructure portion of culverts/ bridges shall be entirely removed and other parts removed below the ground level or as necessary depending upon the interference they cause to the new construction. Removal of overlying or adjacent material, if required in connection with the dismantling of the structures, shall be incidental to this item.

Where existing culverts/bridges are to be extended or otherwise incorporated in the new work, only such part or parts of the existing structure shall be removed as are necessary and directed by the Engineer to provide a proper connection to the new work. The connecting edges shall be cut, chipped and trimmed to the required lines and grades without weakening or damaging any part of the structure to be retained. Due care should be taken to ensure that reinforcing bars which are to be left in place so as to project into the new work as dowels or ties are not injured during removal of concrete.

Pipe culverts shall be carefully removed in such a manner as to avoid damage to the pipes.

Steel structures shall, unless otherwise provided, be carefully dismantled in such a manner as to avoid damage to members thereof. If specified in the drawings or directed by the Engineer that the, structure is to be removed in a condition suitable for re-erection, all members shall be match-marked by the Contractor with white lead paint before dismantling; end pins, nuts, loose plates, etc., shall be similarly marked to indicate their proper location; all pins, pin holes and machined surfaces shall be painted with a mixture of white lead and tallow and all loose parts shall be securely wired to adjacent members or packed in boxes. Timber structures shall be removed in such a manner as to avoid damage to such timber or lumber as is designated by the Engineer to be salvaged.

  - Dismantling Pavements and Other Structures

In removing pavements, kerbs, gutters, and other structures like guard-rails, fences, manholes, catch basins, inlets, etc., where portions of the existing construction are to be left in the finished work, the same shall be removed to an existing joint or cut and chipped to a true line with a face perpendicular to the surface of the existing structure, Sufficient removal shall be made to provide for proper grades and connections with the new work as directed by the Engineer, All concrete pavements, base courses in carriageway and shoulders etc., designated for removal shall be broken to pieces whose volume shall not exceed 0.02 cu. m. and stockpiled at designated locations if the material is to be used later or otherwise arranged for disposal as directed (see Clause 202.5).

  - Back-filling

Holes and depressions caused by dismantling operations shall be backfilled with excavated or other approved materials and compacted to required density as directed by the Engineer.

  - Disposal of Materials

All materials obtained by dismantling shall be the property of Government. Unless otherwise specified, materials having any salvage value shall be placed in neat stacks of like materials within the right of way, as directed by the Engineer with all lifts and upto a lead of 1000 m.

Pipe culverts that are removed shall be cleaned and neatly piled on the right -of-way at points designated by the Engineer with all lifts and lead upto 1000 m.

Structural steel removed from old structures shall, unless otherwise specified or directed, be stored in a neat and presentable manner on blocks in locations suitable for loading. Structures or portions (hereof which are specified in the Contract for re -erection shall be stored in separate piles.

Timber or lumber from old structures which is designated by the Engineer as materials to be salvaged shall have all nails and bolts removed therefrom and shall be stored in neat piles in locations suitable for loading. All materials obtained from dismantling operations which, in the opinion of the Engineer, cannot be^ used or auctioned shall be disposed of as directed by the Engineer with all lifts and upto a lead of 1000 m.

  - Measurements for Payment

The work of dismantling structures shall be paid for in units indicated below by taking measurements before and after, as applicable:

- Dismantling brick/stone masonry/

concrete (plain and reinforced)	cu. m.

- Dismantling flexible and

cement concrete pavement	cu. m.

- Dismantling steel structures	tonne

- Dismantling limber structures	cu. m.

- Dismantling pipes, guard rails, kerbs, gutters and

fencing	linear m.

- Utility services	Nos.

- Earthwork, Erosion Control and Drainage

##### EXCAVATION FOR ROADWAY AND DRAINS

  - Scope

This work shall consist of excavation, removal and satisfactory disposal of all materials necessary for the construction of roadway, side drains and waterways in accordance with requirements of these Specifications and the lines, grades and cross-sections shown in the drawings or as indicated by the Engineer, It shall include the hauling and stacking of or hauling to sites of embankment and subgrade construction, suitable cut materials as required, as also the disposal of unsuitable cut materials in specified manner, trimming and finishing of the road to specified dimensions or as directed by the Engineer.

  - Classification of Excavated Materials

    - Classification:

All materials involved in excavation shall be classified by the Engineer in the following manner:

- Soil

This shall comprise topsoil, turf, land, sill, loon, day, mud, peat. Mack cotton toil, loft shale or loose moorum, a mixture of these and similar material which yields to the ordinary application of pick, spade and/or shovel, rake or other ordinary digging implement. Removal of gravel or any other nodular material having dimension in any one direction not exceeding 75 mm occurring in such strata shall be deemed to be covered under mil category.

- Ordinary Rock (not requiring blasting)

  - rock types such as lalerites, shales and conglomerates, varieties of limestone and sandstone etc., which may be quarried or split with crow ban, also including any rock which in dry state may be hard, requiring- blasting but which, when wet, becomes soft and manageable by means other than blasting;

  - macadam surfaces such as water bound and bitumen Air bound; soling of roads, paths etc. and hard core; compact' moorum or stabilized soil requiring grafting tool or pick or both and shovel, closely applied; gravel and cobble stone having maximum dimension in any one direction between 75 and 300 mm;

  - lime concrete, stone masonry in lime mortar and brick work in lime/cement mortar below ground level, reinforced cement concrete which may be broken up with crow bars or picks and stone masonry in cement mortar below ground level; and

  - boulders which do not require blasting having maximum dimension in any direction of more than 300 mm, found lying loose on (he surface or embedded in river bed, soil, talus, slope wash and terrace material of dissimilar origin.

- Hard Rock (requiring blasting)

This shall comprise:

  - any rock or cement concrete for the excavation of which the use of mechanical plant and/or blasting is required;

  - reinforced cement concrete (reinforcement cut through but not separated from the concrete) below ground level; and

  - boulders requiring blasting.

- Hard Rock (blasting prohibited)

Hard rock requiring blasting as described under (c) but where blasting is prohibited for any reason and excavation has to be carried out by chiselling, wedging or any other agreed method.

- Marshy Soil

This shall include soils like soft clays and peats excavated below the original ground level of marshes and swamps and soil) excavated from other areas requiring continuous pumping or bailing out of water.

    - Authority for classification:

The classification of excavation shall be decided by the Engineer and his decision shall be final and binding on the Contractor. Merely the use of explosives in excavation will not be considered as a reason for higher classification unless blasting is necessary in the opinion of the Engineer.

  - Construction Operations.

    - Setting out:

After the site has been cleared as per clause 201 the limits of excavation shall be set out true to lines, curves, slopes, grades and sections as shown on the drawings or as directed by the Engineer. The contractor shall provide all labour, survey instruments and materials such as strings, pegs, nails, bamboos, stones, line, mortar, concrete etc. required in connection with the settings out of works and the

establishment of bench marks. The contractor shall be responsible for the maintenance of bench marks and other marks and stakes as long as in the opinion of the Engineer they are required for the work.

    - Stripping and storing top soil:

When so directed by the Engineer, the top soil existing over the sites of excavation shall be stripped to specified depths and stored at designated locations for re-use in covering embankment slopes, cut slopes, berms and other disturbed areas where re-vegetation is desired. Prior to stripping the topsoil, all trees, shrubs etc. shall be removed along with their roots, with approval of the Engineer.

    - Excavation General:

All excavations shall be carried out in confirmity with directions laid herein under and in a manner approved by the Engineer. The work shall be so done that the suitable materials available from excavation are satisfactorily utilized as decided upon beforehand.

While planning or executing excavations, the Contractor shall make all adequate precautions against soil erosion, water pollution etc., vide clause 306 and take appropriate drainage measures to keep the site free of water in accordance with Clause 311.

The excavations shall conform to the lines, grades, side slopes and levels shown on the drawings or directed by the Engineer. The contractor shall not excavate outside the slopes or below the established grades or loosen any material outside the limits of excavation. Subject to the permitted tolerances, any excess depth excavate below the specified levels on the road shall be made good at the cost of the contractor with suitable material of similar characteristics to that removed and compacted to the requirements of clause 305.

All debris and loose material on the slope of cutting shall be allowed to obtain required slopes excepting that when boulders or soft material are encouraged in cut slopes these shall be excavated to approved depth on instructions of the Engineer and the resulting cavities filled with suitable material and thoroughly compacted in an approved manner.

After excavation the sides of excavated areas shall be trimmed and the area contoured to minimize erosion and ponding, allowing for material drainage to take place. If trees were removed new trees shall be planted as directed by the Engineer. The cost of planting new trees shall be damaged to be incidental to the works.

    - Methods, tools and equipment’s:

Only such method, tools and equipment’s as approved by the Engineer shall be adopted/ used in the work. II so desired by the Engineer, the contractor shall demonstrate the efficacy of the type of equipment to be used before the commencement of work.

    - Rock excavation:

Rock, when encountered in road excavation, shall be removed upto the formation level or as otherwise indicated on the drawings. Where, however, unstable shales or other unsuitable materials are encountered at the formation level, these shall be excavated to the extent of 500 mm below the formation level or as otherwise specified. In all cases, 'the excavation operations shall be so carried out that at no point on cut formation the rock protrudes above the specified levels. Rocks and large boulders which are likely to cause differential settlement and also local drainage problems should be removed to the extent of 500 mm below the formation level in full formation width including drains and cut through the side drains.

Where excavation is done to levels lower than those specified, the excess excavation shall be made good as per Clauses 301.3.3 and 301.6 to the satisfaction of the Engineer.

Slopes in rock cutting shall be finished to uniform lines corresponding to slope lines shown on the drawings or as directed by the Engineer. Notwithstanding the foregoing, all loose pieces of rock on excavated slope surface which move when pierced by a crowbar shall be removed.

Where blasting is to be resorted to, the same shall be carried out to Clause 302 and all precautions indicated therein observed.

Where presplitting is prescribed to be done for the establishment of a specified slope in rock excavation, the same shall be carried out to Clause 303.

    - Marsh Excavation:

The excavation of marshes / swamps shall be carried out as per the programme laid down by the Engineer. Excavation of marshes shall begin at one end and proceed in one direction across the entire marsh immediately ahead of backfilling. The method and sequence of excavating and backfilling shall be such as to assure, to the extent practicable, the complete removal or displacement of ail muck from within the lateral limits called for on the drawings or as stacked by the Engineer, and to the bottom of the marsh, firm support or levels indicated.

    - Excavation of road shoulders/verge/median for widening of pavement or providing treated shoulders:

In works involving widening of existing pavements or providing treated shoulders, unless otherwise specified, the shoulder/verge/median shall be removed to their full width and to levels shown on drawings or as indicated by the Engineer. White doing so, care shall be taken to see that no portion of the existing pavement designated for retention is loosened or disturbed. If the existing pavement gets disturbed or loosened, it shall be dismantled and cut to a regular shape with sides vertical and the disturbed/loosened portion removed completely and relaid as directed by the Engineer, at the cost of the Contractor.

    - Excavation for surface/sub-surface drains:

Where the Contract provides for construction of surface/sub-surface drains to Clause 309, excavation for these shall be carried out in proper sequence with other works as approved by the Engineer.

    - Slides:

If slips, slides, over-breaks or subsidence occur in cuttings during the process of construction, they shall be removed at the cost of the Contractor as ordered by the Engineer. Adequate precautions shall be taken to ensure that during construction, the slopes are not rendered unstable or give rise to recurrent slides after construction. If finished slopes slide into the roadway subsequently, such slides shall be removed and paid for at the Contract rate for the class of excavation involved, provided the slides are not due to any negligence on the part of the Contractor. The classification of the debris material from the slips, slides etc. shall conform to its condition at the time of removal and payment made accordingly regardless of its condition earlier.

    - Dewatering:

If water is met with in the excavations due to springs, seepage, rain or other causes, it shall be removed by suitable diversions, pumping or bailing out and the excavation kept dry whenever so required or directed by the Engineer. Care shall be taken to discharge the drained water into suitable outlets as not to cause damage to the works, crops or any other property. Due to any negligence on the part of the Contractor, if any such damage is caused, it shall be the sole responsibility of the Contractor to repair/restore to the original condition at his own cost or compensate for the damage.

    - Disposal of excavated materials:

All the excavated materials shall be the property of the Employer. The material obtained from the excavation of roadway, shoulders, verges, drains, cross drainage works etc., shall be used for filling up of

(i) roadway embankment, (ii) the existing pits in the right -of-way and (iii) for landscaping of the road as directed by the Engineer, including levelling and spreading with all lifts and lead upto 1000 m and no extra payment shall be made for the same.

All hard materials such as hard moorum, rubble, etc., not intended for use as above shall be stacked neatly on specified land as directed by the Engineer with all lifts and lead upto 1000 m.

Unsuitable and surplus material not intended for use within the lead specified above shall also, if necessary, be transported with all lifts and lead beyond initial 1000 m, disposed of or used as directed by the Engineer.

    - Backfilling:

Backfilling of masonry /concrete/ hume pipe drain excavation shall be done with approved material after concrete/ masonry/hume pipe is fully set and carried out in such a way as not to cause undue thrust on any part of the structure and/or not to cause differential settlement. All space between the drain walls and the

side of the excavation shall be refilled to the original surface making due allowance for settlement, in layers generally not exceeding 150 mm compacted thickness to the required density, using suitable compaction equipment such as mechanical tamper, rammer or plate compactor as directed by the Engineer.

  - Plying of Construction Traffic

Construction traffic shall not use the cut formation and finished subgrade without the prior permission of the Engineer. Any damage arising out of such use shall be made good by the Contractor at his own expense.

  - Preservation of Property

The Contractor shall undertake all reasonable precautions for the protection and preservation of any or all existing roadside trees, drains, sewers or other sub -surface drains, pipes, conduits and any other structures under or above ground, which may be affected by construction operations and which, in the opinion of the Engineer, shall be continued in use without any change. Safety measures taken by the Contractor in this respect, shall be got approved from the Engineer. However, if any of these objects is damaged by reason of the Contractor's negligence, it shall be replaced or restored to the original condition at his expense. If the Contractor fails to do so, within the required time as directed-by the Engineer or if, in the opinion of the Engineer, the actions initiated by 'the Contractor to replace/restore the damaged objects are not satisfactory, the Engineer shall arrange the replacement/ restoration directly through any other agency at the risk and cost of the Contractor after issuing a prior notice to the effect,

  - Preparation of Cut Formation

The cut formation, which serves as a subgrade, shall be prepared to receive the" sub-base/base course as directed by the Engineer. Where the material in the subgrade (that is within 500 mm from the lowest level of the pavement) has a density less than specified in Table 300-2, the same shall be loosened to a depth of 500 mm and compacted in layers in accordance with the requirements of Clause 305.

Any unsuitable material encountered in the subgrade level shall be removed as directed by the Engineer and replaced with suitable material compacted in accordance with Clause 305.

In rocky formations, the surface irregularities shall be corrected and the levels brought up to the specified elevation with granular base material as directed by the Engineer, laid and compacted in accordance with the respective Specifications for these materials. The unsuitable material shall be disposed of in accordance with Clause 301.3.11. After satisfying the density requirements, the cut formation shall be prepared to receive the subbase/base course in accordance with Clauses 310 and 311 to receive the sub- base/base course.

  - Finishing Operations

Finishing operations shall include the work of properly shaping and dressing all excavated surfaces.

When completed, no point on the slopes shall vary from the designated slopes by more than 150 mm measured at right angles to the slope, except where excavation is in rock (hard or soft) where no point shall vary more than 300 mm from the designated slope. In no case shall any portion of the slope encroach on the roadway.

The finished cut formation shall satisfy the surface tolerances described in Clause 902.

Where directed, 'the topsoil removed earlier and conserved (Clauses 301.3.2 and 305.3.3) shall be spread over cut slopes, where feasible, berms and other disturbed areas. Slopes may be roughened and moistened slightly, prior to the application of topsoil, in order to provide satisfactory bond. The depth of topsoil shall be sufficient to sustain plant growth, the usual thickness being from 75 mm to 100 mm.

  - Measurements for Payment

Excavation for roadway shall be measured by taking cross – sections at suitable intervals in the original position before the work starts and after its completion and computing the volumes in cu. m. by the method of average end areas for each class of material encountered. Where it is not feasible to compute volumes by this method because of erratic location of isolated deposits, the volumes shall be computed by other accepted methods.

At the option of the Engineer, the Contractor shall leave depth indicators during excavations of such shape and size and in such positions as directed so as to indicate the original ground level as accurately as possible. The Contractor shall see that these remain intact till the final measurements are taken.

For rock excavation, the overburden shall be removed first so that necessary cross-sections could be taken for measurement. Where cross sectional measurements could not be taken due to irregular configuration or where the rock is admixed with other classes of materials, the volumes shall be computed on the basis of stacks of excavated rubble after making 35 per cent deduction therefrom. When volumes are calculated in this manner for excavated material other than rock, deduction made will be to the extent of 16 per cent of stacked volumes.Works involved in 'the preparation of cut formation shall be measured in units indicated below:

- Loosening and re compacting the	... cu. m. loosened material at subgrade

- Loosening and removal of unsuitable	... cu. m. material and replacing with a

suitable material and compacting to required density

- Preparing rocky subgrade	... sq. m,

- Stripping including storing and	... cu. m.

reapplication of topsoil

- Disposal of surplus material	... cu. m, beyond initial 1000 m lead

##### EXCAVATION FOR STRUCTURES

  - Scope

Excavation for structures shall consist of the removal of material for the construction of foundations of bridges, culverts retaining walls, head walls cut off walls, pipe culverts and other similar structures, in accordance with the requirements of these Specifications and the lines and dimensions shown on the drawings or as indicated by the Engineer. The work shall include constructions of the necessary cofferdams and cribs and their subsequent removal; all necessary sheeting, shoring, bracing draining and pumping the removal of all logs, slumps, grubs and other deleterious matter and obstructions necessary for placing the foundations; trimming bottoms of excavations; backfilling and clearing up the site and the disposal of all surplus materials.

  - Classification of Excavation

All materials involved in excavation shall be classified in accordance with clause 301.2.

  - Construction Operations

    - Setting out:

After the site has been cleared to Clause 201, the limits of excavation shall be -set out true to lines curves and slopes to Clause 301.3.1.

    - Excavation:

Excavation shall be taken to the width of the lowest step of the footing and the sides shall be left plumb where the nature of roil allows it. Where the nature of the soil or the depth of the trench does not permit vertical sides, the contractor at his own expense shall put up the necessary shoring, strutting and planking or cut slopes to a safer angle or both with due regard to the safety of personnel and works and to the satisfaction of the Engineer.

The depth to which the excavation is to be carried out shall be as shown on the drawings, unless the type of material encountered is such as to require changes, in which case the depth shall be as ordered by the Engineer. Propping shall be "undertaken when any foundation or stressed zone from an adjoining structure is within a line of 1 vertical to 2 horizontal from the bottom of the excavation.

Where blasting is to be resorted to the same shall be carried out to Clause 302 and all precautions indicated therein observed. Where blasting is likely to endanger adjoining foundations or other structures,

necessary precautions such as controlled blasting, providing rubber mat cover to prevent flying of debris etc. shall be taken to prevent any damage.

    - Dewatering and protection:

Where water is met within excavation due, to stream flow, seepage, spring, rain or other reasons, the contractor shall betake adequate measures such as bailing, pumping, constructing diversion channels, drainage channels bunds, cofferdams and other necessary works to keep the foundation trenches dry when so required and to protect the green concrete/masonry against damage by erosion or sudden rising of water level. The methods to be adopted in this regard and other details thereof shall be left lo the choice of the contractor but subject to approval of the Engineer. Approval of the Engineer shall however, not relieve the contractor of the responsibility or the adequacy of dewatering and protection arrangements and for the quality and safety of the works.

Where cofferdams are required, these shall be carried out to adequate depths and heights, be safely designed and constructed and be made as watertight as is necessary for facilitating construction to be carried out inside them. The interior dimensions of the cofferdams shall be such as lo give sufficient clearance for the construction and inspection and to permit installation of pumping equipment’s etc. inside the enclosed area.

If it is determined beforehand that the foundations cannot be laid dry or the situation is found that the percolation is too heavy for keeping the foundation dry, the foundation concrete shall be laid under water by tremic pipe only. In case of flowing water or artesian springs, the flow shall be stopped or reduced as far as possible at the time of placing the concrete.

Pumping from the interior of any foundation enclosure shall be done in such a manner as to preclude the possibility of the movement of water thorough any fresh concrete. No pumping shall be permitted during the placing of concrete or for a period of atleast 24 hours thereafter, unless it is done from a suitable pump sump separated from the concrete work by a watertight wall or other similar means.

At the discretion of the contractor, cement grouting or other approved methods may be used to prevent or reduce seepage and to protect the excavation area.

The contractor shall take all precautions in diverting channels and in discharging the drain water as not to cause damage to the works, crops or.-to any other property.

    - Preparation of foundation:

The bottom of the foundation shall be leveled, both longitudinally and transversely or stepped as directed by the Engineer. Before footing is laid, the surface shall be slightly watered and rammed. In the event of excavation having been made deeper than that shown on the drawings or as otherwise ordered by the

Engineer the extra depth shall be made up with concrete or masonry of the foundation grade at the cost of the contractor. Ordinary filling shall not be used for the purpose to bring the foundation to level.

When rock or other hard strata is encountered, it shall be deed of all soft and loose material, cleaned and cut to a firm surface either level, stepped or serrated as directed by the Engineer. All seems shall be cleaned out and filled with cement mortar or grout to the satisfaction of the Engineer. In the case of excavation in rock, annular space around footing shall be filled with lean concrete (1:3:6nominal mix) upto the top level of rock.

If the depth of the fill required is more than 1.5m above the top of the footing, filling upto 1.5m above top of

footing shall be done with lean concrete (1:3:6 nominal mix) followed by boulder’s grouted with cement. When foundation piles are used, the excavation of each pit shall be substantially completed before beginning pile-driving operations therein. After pile-driving operations in a given pit are completed, all loose and displaced materials therein shall be removed to the elevation of the bottom of the footings.

    - Slips and slip - outs: If there are any slips or blows in the excavation, these shall be removed by the contractor at his own cost.

    - Public Safety: Near towns, villages and all frequented places, trenches and foundations pits shall be securely fenced, provided with proper caution signs and marked with red lights at night to avoid accidents. The contractor shall take proper adequate protective measures to see that the excavation operations do not affect or damage adjoining structures. For safety precautions, guidance may be taken from IS: 3764.

    - Backfilling: Backfilling shall be done with approved material after concrete or masonry is fully set and carried out in such a way as not to cause undue thrust on any part of the structure. All space between foundation masonry or concrete and the sides of excavation shall be refilled to the original surface in layers not exceeding 150 mm compacted thicknesses. The compaction shall be done with the help of suitable equipment such as mechanical tamper, rammer, plate vibrators, after necessary watering, so as to achieve a density not less than the field density before excavation.

  - Measurements for Payment

Excavation for structures shall be measured in cu. m. for each class of material encountered, limited to the dimensions shown on the drawings or as directed by the Engineer. Excavation over increased with, cutting of slopes, shoring, shuttering and planking shall be deemed as convenience for the Contractor in executing the work and shall not be measured and paid for separately.

Preparation of rock foundation shall be measured in square metres. Foundation sealing, dewatering, including pumping shall be deemed to be incidental to the work unless separate provision is made for in the Contract. In the letter case, payment shall be on lump sum basis as provided in the Bill of Quantities.

##### EMBANKMENT CONSTRUCTION

  - General

    - Description: These Specifications shall apply to the construction of embankments including subgrades, earthen shoulders and miscellaneous backfills with approved material obtained from roadway and drain excavation, borrow pits or other sources. All embankments, subgrades, earthen shoulders and miscellaneous backfills shall be constructed in accordance with the requirements of these Specifications and in conformity with the lines, grades, and cross-sections shown on the drawings or as directed by the Engineer.

  - Materials and General Requirements

    - Physical requirements:

      - The materials used in embankments, subgrades, earthen shoulders and miscellaneous backfills shall be soil, moorum, gravel, a mixture of these or any other material approved by the Engineer. Such materials shall be free of logs, stumps, roots, rubbish or any other ingredient likely to deteriorate or affect the stability of the embankment/ subgrade.

The following types of material shall be considered unsuitable for embankment:

- Materials from swamps, marshes and bogs;

- Peat, log, stump and perishable material: any soil that, classifies as OL, OI, OH or Pt in accordance with IS: 1498.

- Materials susceptible to spontaneous combustion;

- Materials in a frozen condition;

- Clay having liquid limit exceeding 70 and plasticity index exceeding 45; and

- Materials with sails resulting in leaching in the embankment.

      - Expansive clay exhibiting marked swell and shrinkage properties ("free swelling index" exceeding 50 per cent when tested as per IS: 2720 - Part 40} shall not be used as a fill material. Where expansive clay with acceptable "free swelling index" value is used as a fill material, subgrade and top 500 mm portion of the embankment just below subgrade shall be non-expansive in nature.

      - Any fill material with a soluble sulphate consent exceeding 1.9 grams of sulphate (expressed as SO3) per litre when tested in accordance with BS: 1377 Test 10, but using a 2:1 water-soil ratio shall not be deposited within 500 mm or other distance described in the Contract, of concrete, cement bound materials or other cementitious materials forming part of the Permanent Works.

Materials with a total sulphate content (expressed as SO3) exceeding 0.5 per cent by mass, when tested in accordance with BS: 1377 Test 9 shall not be deposited within 500 mm, or other distances described in the

Contract, of metallic items forming part of the Permanent Works.

      - The size of the coarse material in the mixture of earth shall ordinarily not exceed 75 mm when being placed in the embankment and 50 mm when placed in the subgrade. However, the Engineer may at his discretion permit the use of material coarser than this also if he is satisfied that the same will not present any difficulty as regards the placement of fill material and its compaction to the requirements of these Specifications. The maximum particle, size shall not be more than two-thirds of the compacted layer thickness.

      - Ordinarily, only the materials satisfying the density requirements given in Table 300-1 shall be employed for the construction of the embankment and the subgrade.

TABLE 1.1 DENSITY REQUIREMENTS OF EMBANKMENT AND SUBGRADE MATERIALS

Notes: (1) This Table is not applicable for lightweight fill material e.g. cinder, fly ash etc.

- The Engineer may relax these requirements at his discretion taking into account the availability of materials for construction and other relevant factors.

- The material to be used in subgrade should also satisfy design CBR at the dry unit weight applicable as per Table 300-1.

    - General requirements:

      - The materials for embankment shall be obtained from approved sources with preference given to materials becoming available from nearby roadway excavation or any other excavation under the same Contract.

The work shall be so planned and executed that the best available materials -are saved for the subgrade and the embankment portion just below the subgrade.

      - Borrow materials: Where the materials are to be obtained from designated borrow areas, the location, size and shape of these areas shall be as indicated by the Engineer and the same shall not be opened without his written permission. Where specific borrow areas are not designated by the Employer/the Engineer, arrangement for locating the source of supply of material for embankment and

subgrade as well as compliance to environmental requirements in respect of excavation and borrow areas

as stipulated, from time to time by the Ministry of Environment and Forests, Government of India and the local bodies, as applicable, shall be the sole responsibility of the Contractor.

Borrowpits along the road shall be discouraged. If permitted by the Engineer, these shall not be dug continuously. Ridges of not less than 8 m width should be left at intervals not exceeding 300 m. Small drains shall be cut through the ridges to facilitate drainage. The depth of the pits shall be so regulated that their bottom does not cut an imaginary line having a slope of 1 vertical to 4 horizontal projected from the edge of the final section of the bank, the maximum depth in any case being limited-to 1.5 m. Also, no pit shall be dug within the offset width from the toe of the embankment required as per the consideration of stability with a minimum width of 10 m.

Haulage of material to embankments or other areas of fill shall proceed only when sufficient spreading and compaction plant is operating at the place of deposition.

No excavated acceptable material other than surplus to requirements of the Contract shall be removed- from the site. Should the Contractor be permitted to remove acceptable material from the site to suit his operational procedure, then he shall make good any consequent deficit of material arising therefrom.

Where the excavation reveals a combination of acceptable and un -acceptable materials, the Contractor shall, unless otherwise agreed by the Engineer, carry out the excavation in such a manner that the acceptable materials are excavated separately for use in the permanent works without contamination by the unacceptable materials. The acceptable materials shall be stockpiled separately.

The Contractor shall ensure that he does not adversely affect the stability of excavation or fills by the methods of stockpiling materials, use of plants or siting of temporary buildings or structures.

The Contractor shall obtain representative samples from each of the identified borrow areas and have these tested at the site laboratory following a testing programme approved by the Engineer. It shall been ensured that the subgrade material when compacted to the density requirements as in Table 300-2 shall yield the design CBR value of the subgrade.

TABLE 1.2. COMPACTION REQUIREMENTS FOR EMBANKMENT AND SUBGRADE

The Contractor shall at least 7 working days before commencement of compaction submit the following to the Engineer for approval:

- The values of maximum dry density and optimum moisture content obtained in accordance with IS: 2720 (Part 7) or (Part 8), as the case may be, appropriate for each of the fill materials he intends to use.

- A graph of density plotted against moisture content from which each of the values in (i) above of maximum dry density and optimum moisture content were determined.

- The Dry density-moisture content -CBR relationships for light, intermediate and heavy compactive efforts (light corresponding to IS: 2720 (Part 7), heavy corresponding to IS: 2720 (Part 8) and intermediate in-between the two) for each of the fill materials he intends to use in the subgrade.

Once the above information has been approved by the Engineer, it shall form the basis for compaction.

  - Construction Operations

    - Setting out: After the site has been cleared to Clause 201, the work shall be set out to Clause

301.3.1. The limits of embankment/subgrade shall be marked by fixing batter pegs on both sides at regular intervals as guides before commencing the earthwork. The embankment/subgrade shall be built sufficiently wider than the design dimension so that surplus material may be trimmed, ensuring that the remaining material is to the desired density and in position specified and conforms to the specified side slopes.

    - Dewatering: If the foundation of the embankment is in an area with stagnant water, and in the opinion of the Engineer it is feasible to remove it, the same shall be removed by bailing out or pumping, as directed by the Engineer and the area of the embankment foundation shall be kept dry. Care shall be taken to discharge the drained water so as not to cause damage to the works, crops or any other property. Due to any negligence on the part of the Contractor, if any such damage is caused, it shall be the sole responsibility of the Contractor to repair/restore it to original condition or compensate the damage at his own cost.

If the embankment is to be constructed under water, Clause 305.4.6 shall apply.

    - Stripping and storing topsoil: In localities where most of the available embankment materials are not conducive to plant growth, or when so directed by the Engineer, the topsoil from all areas of cutting and from all areas to be covered by embankment foundation shall be stripped to specified depths not exceeding 150 mm and stored in stockpiles of height not exceeding 2 m for covering embankment slopes, cut slopes and other disturbed areas where re-vegetation is desired. Topsoil shall not be unnecessarily trafficked either before stripping or when in a stockpile. Stockpiles shall not be surcharged or otherwise loaded and multiple handling shall be kept to a minimum.

    - Compacting ground supporting embankment/subgrade:

Where necessary, the original ground shall be levelled to facilitate placement of first layer of embankment, scarified, mixed with water and then compacted by rolling so as to achieve minimum dry density as given in Table 300-2.

In case where the difference between the subgrade level (top of the subgrade on which pavement rests) and ground level is less than 0.5 m and the ground does not have 97 per cent relative compaction with respect to the dry density as given in Table 300-2, the ground shall be loosened upto a level 0.5 m below the subgrade level, watered and compacted in layers in accordance with Clauses 305.3,5 and 305.3.6 to not less than 97 per cent of dry density as given in Table 300-2.

Where so directed by the Engineer, any unsuitable material occurring in the embankment foundation shall be removed and replaced by approved materials laid in layers to the required degree of compaction.

Embankment or subgrade work shall not proceed until the foundations for embankment/subgrade have been inspected by the Engineer for satisfactory condition and approved.

Any foundation treatment specified for embankments especially high embankments, resting on suspect foundations as revealed by borehole logs shall be carried out in a manner and to the depth as desired by the Engineer. Where the ground on which an embankment is to be built has any of the material types (a) to

(f) in Clause 305.2.1, at least 500 mm of such material must be removed and replaced by acceptable fill material before embankment construction commences.

    - Spreading material in layers and bringing to appropriate moisture content

      - The embankment and subgrade material shall be spread in layers of uniform thickness not exceeding 200 mm compacted thickness over the entire width of embankment by mechanical means, finished by a motor grader and compacted as per Clause 305.3.6. The motor grader blade shall have hydraulic control suitable for initial adjustment and maintain the same so as to achieve the specific slope and grade. Successive layers shall not be p laced until the layer under construction has been thoroughly compacted to the specified requirements as in Table 300-2 and got approved by the Engineer. Each compacted layer shall be finished parallel to the final cross-section of the embankment.

      - . Moisture content of the material shall be checked at the site of placement prior to commencement of compaction; if found to be out of agreed limits, the same shall be made good. Where water is required to be added in such constructions, water shall be sprinkled from a water tanker fitted with sprinkler capable of applying water uniformly with a controllable rate of flow to variable widths of surface but without any flooding. The water shall be added uniformly and thoroughly mixed in soil by blading, discing or harrowing until uniform moisture content is obtained throughout the depth of the layer.

If the material delivered to the roadbed is too wet, it shall be dried, by aeration and exposure to the sun till the moisture content is acceptable for compaction. Should circumstances arise, where owing to wet

weather, the moisture content cannot be reduced to the required amount by the above procedure, compaction work shall be suspended.

Moisture content of each layer of soil shall be checked in accordance with IS: 2720 (Part 2), and unless otherwise mentioned, shall be so adjusted, making due allowance for evaporation losses, that at the time of compaction it is in the range of 1 per cent above to 2 per cent below the optimum moisture content determined in accordance with IS: 2720 (Part 7) or IS: 2720 (Part 8) as the case may be. Expansive clays shall, however, be compacted at moisture content corresponding to the specified dry density, but on the wet side of the optimum moisture content obtained from the laboratory compaction curve.

After adding the required amount of water, the soil shall be processed by means of graders, harrows, rotary mixers or as otherwise approved by the Engineer until the layer is uniformly wet.

Clods or hard lumps of earth shall be broken to have a maximum size of 75 mm when being placed in the embankment and a maximum size of 50 mm when being placed in the subgrade.

      - . Embankment and other areas of fill shall, unless otherwise required in the Contract or permitted by the Engineer, be constructed evenly over their full width and their fullest possible extent and the Contractor shall control and direct construction plant and other vehicular traffic uniformly over them. Damage by construction plant and other vehicular traffic shall be made good by the Contractor with material having the same characteristics and strength as the material had before it was damaged. Embankments and other areas of unsupported fills shall not be constructed with steeper side slopes, or to greater widths than those shown in the Contract, except to permit adequate compaction at the edges before trimming back, or to obtain the final profile following any settlement of the fill and the underlying material.

Whenever fill is to be deposited against the face of a natural slope, or sloping earthworks face including embankments, cuttings, other fills and excavations steeper than 1 vertical on 4 horizontal, such faces shall be benched as per Clause 305.4.1 immediately before placing the subsequent fill.

All permanent faces of side slopes of embankments and other areas of fill formed shall, subsequent to any trimming operations, be reworked and sealed to the satisfaction of the Engineer by tracking a tracked vehicle, considered suitable by the Engineer, on the slope or any other method approved by the Engineer.

    - . Compaction: Only the compaction equipment approved by the Engineer shall be employed to compact the different material types encountered during construction. Smooth wheeled, vibratory, pneumatic tyred, sheepsfoot or pad foot rollers, etc. of suitable size and capacity as approved by the Engineer, but used for the different types and grades of materials required to be compacted either individually or in suitable combinations.

The compaction shall be done with the help of vibratory roller of 80 to 100 kN static weight with plain or pad foot drum or heavy pneumatic tyred roller of adequate capacity capable of achieving required compaction. The Contractor shall demonstrate the efficacy of the equipment he intends to use by carrying out compaction trials. The procedure to be adopted for these site trials shall first be submitted to the Engineer for approval.

Earthmoving plant shall not be accepted as compaction equipment nor shall the use of a lighter category of plant to provide any preliminary compaction to assist the use of heavier plant be taken into account.

Each layer of the material shall be thoroughly compacted to the densities specified in Table 300-2. Subsequent layers shall be placed only after the finished layer has been tested according to Clause

903.2.2 and accepted by the Engineer. The Engineer may permit measurement, of field dry density by a nuclear moisture/density gauge used in accordance with agreed procedure and the gauge is calibrated to provide results identical to that obtained from tests in accordance with IS: 2720 (Part 28), A record of the same shall be maintained by the Contractor.

When density measurements reveal any soft areas in the embankment/ subgrade/earthen shoulders, further compaction shall be carried out as directed by the Engineer. If inspite of that the specified compaction is not achieved, the material in the soft areas shall be removed and replaced by approved material, compacted to the density requirements and satisfaction of the Engineer.

    - . Drainage: The surface of the embankment/subgrade at all times during construction shall be maintained at such a cross fall (not flatter than that required for effective drainage of an earthen surface) as will shed water and prevent ponding.

    - . Repairing of damages caused by rain/spillage of water:

The soil in the affected portion shall be removed in such areas as directed by the Engineer before next layer is laid and refilled in layers and compacted using appropriate mechanical means such as small vibratory roller, plate compactor or power rammer to achieve the required density in accordance with Clause 305.3.6. If the cut is not sufficiently wide for use of required mechanical means for compaction, the same shall be widened suitably to permit their use for proper compaction. Tests shall be carried out as directed by the Engineer to ascertain the density requirements of the repaired area. The work of repairing the damages including widening of the cut, if any, shall be carried out by the Contractor at his own cost, including the arranging of machinery/equipment for the purpose.

    - . Finishing operations: Finishing operations shall include the work of shaping and dressing the shoulders/verge/roadbed and side slopes to conform to the alignment, levels, cross-sections and dimensions shown on the drawings or as directed by the Engineer subject to .the surface tolerance

described in Clause 902. Both the upper and lower ends of the side slopes shall be rounded off to improve appearance and to merge the embankment with the adjacent terrain.

The topsoil, removed and conserved carrier (Clause 301.3.2 and 305.3.3) shall be spread over the fill slopes as per directions of the Engineer to facilitate the growth of vegetation. Slopes shall be roughened and moistened slightly prior to the application of the topsoil in order to provide satisfactory bond. The depth of the topsoil shall be sufficient to sustain plant growth, the usual thickness being from 75 mm to 150 mm. When earthwork operations have been substantially completed, the road area shall be cleared of all debris, and ugly scars in the construction area responsible for objectionable appearance eliminated.

  - Construction of Embankment and Subgrade under Special Conditions

    - Earthwork for widening existing road embankment:

When an existing embankment and/or subgrade is to be widened and its slopes are steeper than 1 vertical on 4 horizontal, continuous horizontal benches, each at least 300 mm wide, shall be cut into the old slope for ensuring adequate bond with the fresh embankment/subgrade material to be added. The material obtained from cutting of benches could be utilized in the widening of the embankment/subgrade. However, when -the existing slope against which the fresh material is to be placed is flatter than 1 vertical on 4 horizontal, the slope surface may only be ploughed or scarified instead of resorting to benching.

Where the width of the widened portions is insufficient to permit the use of conventional rollers, compaction shall be carried out with the help of small vibratory rollers/plate compactors/power rammers or any other appropriate equipment approved by the Engineer. End dumping of material from trucks for widening operations shall be avoided except in difficult circumstances when the extra width is too narrow to permit the movement of any other types of hauling equipment.

    - Earthwork for embankment and subgrade to be placed against sloping ground: Where an embankment/subgrade is to beplaced against sloping ground, the latter shall be appropriately benchedor ploughed/scarified as required in Clause 305.4.1 before placing theembankment/subgrade material. Extra earthwork involved in benching ordue to ploughing/scarifying etc. shall be considered incidental to the work. For wet conditions, benches with slightly inward fall and subsoil drains at the lowest point shall be provided as per the drawings, before the fill is placed against sloping ground.

Where the Contract requires construction of transverse subsurface drain at the cut-fill interface, work on the same shall be carried out to Clause 309 in proper sequence with the embankment and subgrade work as approved by the Engineer.

    - Earthwork over existing road surface: Where the embankment is to be placed over an existing road surface, the work shall be carried out as indicated below:

- If the existing road surface is of granular or bituminous type and lies within 1 m of the new subgrade level, the same shall be scarified to a depth of 50 mm or more if specified, so as to provide ample bond between the old and new material ensuring that at least 500 mm portion below the top of new subgrade level is compacted to the desired density.

- If the existing road surface is of cement concrete type and lies within 1 m of the new subgrade level the same shall be removed completely.

- If the level difference between the existing road surface and the new formation level is more than 1m, the existing surface shall be permitted to stay in place without any modification.

    - . Embankment and subgrade around structures: To avoid interference with the construction of abutments, wing walls or return walls of culvert/bridge structures, the Contractor shall, at points to be determined by the Engineer suspend work on embankment forming approaches to such structures, until such time as the construction of the latter is sufficiently advanced to permit die completion of approaches without the risk of damage to the structure.

Unless directed otherwise, the filling around culverts, bridges and other structures upto a distance twice the height of the road from the back of die abutment shall be carried out independent of the work on the main embankment. The fill material shall not be placed against any abutment or wing wall, unless permission has been given by the Engineer but in any case not until the concrete or masonry has been in position for 14 days. The embankment and subgrade shall be brought up simultaneously in equal layers on each side of die structure to avoid displacement and unequal pressure. The sequence of work in this regard shall be got approved from the Engineer.

The material used for backfill shall not be an organic soil or highly plastic clay having plasticity index and liquid limit more than 20 and 40 respectively when tested according to 15:2720 (Part 5). Filling behind abutments and wing, walls for ail structures shall conform to the general guidelines given in Appendix 6 of IRC: 78 (Standard Specifications and Code of Practice Road Bridges-Section VII) in respect of the type of material, the extent of backfill, its laying and Compaction etc. The fill material shall be deposited in horizontal layers in loose thickness and compacted thoroughly to the requirements of Table 300-2.

Where the provision of any filter medium is specified behind the abutment, the same shall be laid in layers simultaneously with the laying of fill material. The material used for filter shall conform to the requirements for filter medium spelt out in Clause 2502/309.3.2 (B) unless otherwise specified in the Contract.

Where it may be impracticable to use conventional rollers, the compaction shall be carried out by appropriate mechanical means such as small vibratory roller, plate compactor or power rammer. Care shall be taken to see that the compaction equipment does not hit or come too close to any structural member so as to cause any damage to them or excessive pressure against the structure.

    - . Construction of embankment over ground incapable of supporting construction equipment: Where embankment is to be constructed across ground which will not support the weight of repeated heavy loads of construction equipment, the first layer of the fill may be constructed by placing successive loads of material in a uniformly distributed layer of a minimum thickness required to support the construction equipment as permitted by the Engineer. The Contractor, if so desired by him, may also use suitable geosynthetic material to increase the bearing capacity of the foundation. This exception to normal procedure will not be permitted where, in the opinion of the Engineer, the embankments could be constructed in the approved manner over such ground by the use of lighter or modified equipment after proper ditching and drainage have been provided. Where this exception is permitted, the selection of the material and the construction procedure to obtain an acceptable layer shall be the responsibility of the Contractor. The cost of providing suitable traffic conditions for construction equipment over any area of the Contract will be the responsibility of the Contractor and no extra payment will be made to him. The remainder of the embankment shall be constructed as specified in Clause 305.3.

    - . Embankment construction under water: Where filling or backfilling is to be placed under water, only acceptable granular material or rock shall be used unless otherwise approved by the Engineer. Acceptable granular material shall consist of graded, hard durable particles with maximum particle size not exceeding 75 mm. The material should be non-plastic having uniformity coefficient of not less than 10. The material placed in open water shall be deposited by end tipping without compaction.

    - . Earthwork for high embankment: In the case of high embankments, the Contractor shall normally use the material from the specified borrow area. In case he desires to use different material for his own convenience, he shall have to carry out necessary soil investigations and redesign the high embankment at his own cost. The Contractor shall then furnish the soil test data and design of high embankment for approval of the Engineer, who reserves the right to accept or reject it.

If necessary, stage construction of fills and any controlled rates of filling shall be carried out in accordance with the Contract including installation of instruments and its monitoring.

Where required, the Contractor shall surcharge embankments or other areas of fill with approved material for the periods specified in the Contract. If settlement of surcharged fill, results in any surcharging material, which is unacceptable for use in the fill being surcharged, lying below formation level, the Contractor shall remove the unacceptable material and dispose it as per direction of the Engineer. He shall then bring the resultant level up to formation level with acceptable material.

    - . Settlement period: Where settlement period is specified in the Contract, the embankment shall remain in place for the required settlement period before excavating for abutment, wingwall, retaining wall,

footings, etc., or driving foundation piles. The duration of the required settlement period at each location shall be as provided for in the Contract or as directed by the Engineer.

  - Plying of Traffic

Construction and other vehicular traffic shall not use the prepared surface of the embankment and/or subgrade without the prior permission of the Engineer, Any damage arising out of such use shall, however, be made good by the Contractor at his own expense as directed by the Engineer.

  - Surface Finish and Quality Control of Work

The surface finish of construction of subgrade shall conform to the requirements of Clause 902. Control on the quality of materials and works shall be exercised in accordance with Clause 903.

  - Subgrade Strength

    - It shall be ensured prior to actual execution that the borrow area material to be used in the subgrade satisfies the requirements of design CBR.

    - Subgrade shall be compacted and finished to the design strength consistent with other physical requirements. The actual laboratory CBR values of constructed subgrade shall be determined on undisturbed samples cut out from the compacted sub grade in CBR mould fitted with cutting shoe or on remoulded samples, compacted to the field density at the field moisture content.

  - Measurements for Payment

Earth embankment/subgrade construction shall be measured separately by taking cross sections at intervals in the original position before the work starts and after its completion and computing the volumes of earthwork in cubic metres by the method of average end areas.

The measurement of fill material from borrow areas shall be the difference between the net quantities of compacted fill and the net quantities of suitable material brought from roadway and drainage excavation. For this purpose, it shall be assumed that one cum of suitable material brought to site from road and drainage excavation forms one cum of compacted fill and all bulking or shrinkage shall be ignored.

Construction of embankment under water shall be measured in cum.

Construction of high embankment with specified material and in specified manner shall be measured in cu.m.

Stripping including storing and reapplication of topsoil shall be measured in cu.m.

Work involving loosening and recompacting of ground supporting embankment/subgrade shall be measured in cum.

Removal of unsuitable material at embankment/subgrade foundation and replacement with suitable material shall be measured in cum.

Scarifying existing granular/bituminous road surface shall be measured in square metres.

Dismantling and removal of existing cement concrete pavement shall be measured vide Clause 202.6. Filter medium and backfill material behind abutments, wing walls and other retaining structures shall be measured as finished work in position in cum.

##### SURFACE/SUB-SURFACE DRAINS

  - Scope

This work shall consist of constructing surface and/or sub-surface drains in accordance with the requirements of these Specifications and to the lines, grades, dimensions and other particulars shown on the drawings or as directed by the Engineer. Schedule of work shall be so arranged that the drains are completed in proper sequence with road works to ensure that no excavation of the completed road works is necessary subsequently or any damage is caused to these works due to lack of drainage.

  - Surface Drains

Surface drains shall be excavated to the specified lines, grades, levels and dimensions to the requirements of Clause 301. The excavated material shall be removed from the area adjoining the drains and if found suitable, utilised in embankment/subgrade construction. All unsuitable material shall be disposed of as directed.

The excavated bed and sides of the drains shall be dressed to bring these in close conformity with the specified dimensions, levels and slopes.

Where so indicated, drains shall, be lined or turfed with suitable materials in accordance with details shown on the drawings.

All works on drain construction shall be planned and executed in proper sequence with other works as approved by the Engineer, with a view to ensuring adequate drainage for the area and minimising erosion/ sedimentation.

  - Sub-surface Drains

    - Scope: Sub -surface drains shall be of close -jointed perforated pipes, open-jointed unperforated pipes, surrounded by granular material laid in a trench or aggregate drains to drain the pavement courses. Sub-surface drains designed using geosynthetics and approved by the Engineer can also be used.

    - Materials

- Pipe: Perforated pipes for the drains may be of metal/asbestos cement/cement concrete/PVC, and unperforated pipes of vitrified clay/cement concrete/ asbestos cement. The type, size and grade of the pip: 10 be used shall be specified in the Contract In no case, however, shall the internal diameter of the pipe be less than 100 mm. Holes for perforated pipes shall be on one half of the circumference only and conform to the spacing indicated on the drawings. Size of the holes shall not ordinarily be greater than half of D85 size

of the material surrounding the pipe, subject to being minimum 3 mm and maximum 6 mm, DM stands for the size of the sieve that allows 85 per cent of the material to pass through it.

- Backfill material: Backfill material shall consist of sound, tough, hard, durable particles of free draining sand-gravel material or crushed stone and shall be free of organic material, clay balls or other deleterious matter. Unless the Contract specifies any particular grading for the backfill material or requires these to be designed on inverted filter criteria for filtration and permeability to the approval of the Engineer, the backfill material shall be provided on the following lines:

  - Where the soil met with in the trench is of fine grained type (e.g. silt, clay or a mixture thereof) the backfill material shall conform to Class I grading set out in-Table 300-3,

  - Where the soil met with in the trench is of coarse silt to medium sand or sandy type, the backfill material shall correspond 10 Class II grading of Table 300-3.

  - Where soil met with in the trench is gravelly sand, the backfill material shall correspond to Class 111 grading of Table 300-3.

Thickness of backfill material around the pipe shall be as shown on the drawings subject to being at least 150 mm alround in all cases.

Table 300.3. GRADING REQUIREMENTS FOR FILTER MATERIAL

    - . Trench excavation: Trench for sub-surface drain shall be excavated to the specified lines, grades and dimensions shown in the drawings provided that width of trench at pip e level shall not be less than 450 mm. The excavation shall begin at the outlet end of the drain and proceed towards the upper end. Where unsuitable material is met with at the trench bed, the same shall be removed to such depth as directed by the Engineer and backfilled with approved material which shall be thoroughly compacted to the specified degree.

    - . Laying of pipe and backfilling: Laying of pipe in the trench shall be started at the outlet end and proceed towards the upper end, true to the lines and grades specified. Unless otherwise provided, longitudinal gradient of the pipe shall not be less than 1 in 100.

Before placing the pipe, backfill material of the required grading(s) shall be laid for full width of the trench bed and comp acted to a minimum thickness of 150 mm or as shown on the drawings. The pipe shall then be embedded firmly on the bed.

Perforated pipes, unless otherwise specified, shall be placed with their perforations down to minimise clogging. The pipe sections shall be joined securely with appropriate coupling fittings or bands.

Non-perforated pipes shall be laid with joints as close as possible with the open joints wrapped with suitable pervious material (like double layer of hessian, suitable Geosynthetics or some other material of not less than 150 mm width) to permit entry of water but prevent fines entering the pipes. In the case of non

-perforated pipes with bell end, the bell shall face upgrade.

Upgrade end sections of the pipe installation shall be tightly closed by means of concrete plugs or plugs fabricated from the same material as the pipe and securely held in place to prevent entry of soil materials. After the pipe installation has been completed and approved, backfill material of the required grading(s) (see Clause 309.3.2B) shall be placed over the pipe to the required level in horizontal layers not exceeding 150 mm in thickness and thoroughly compacted. The minimum thickness of material above the top of the pipe shall be 300 mm.

Unless otherwise provided, sub-surface drains not located below the road pavement shall be sealed at die top by means of 150 mm thick layer of compacted clay so as to prevent percolation of surface water.

    - . Use of geosynthetic in laying of pipe and backfilling:

After excavating the trench for subsurface drain, the filter fabric shall be placed, ihe pipe installed and the trench backfilled with permeable material according to dimensions and details shown on the plans. Surfaces to receive filter fabric prior to placing shall be free of loose or extraneous material and sharp objects that may damage the filter fabric during installation. Adjacent rolls of the fabric shall be overlapped a minimum of 450 mm. The preceding roll shall overlap the following roll in the direction the material is being spread.

Damage to the fabric resulting from Contractor's vehicles, equipment or operations shall be replaced or repaired by the Contractor at his expense.

    - . Drain outlet: The outlet for a sub-drain shall not be under water or plugged with debris but should be a free outlet discharging into a stream, culvert or open ditch. The bottom of the pipe shall be kept above high water in the ditch and the end protected with a grate or screen. For a length of 500 mm from the outlet end, the trench for pipe shall not be provided with granular material but backfilled with excavated soil and

thoroughly compacted so as to stop water directly percolating - from the backfill material around the pipe. The pipe in this section shall not have any perforations.

    - . Aggregate drains: Aggregate drains snail be placed within the verge/shoulders after completion of the pavement. Depth, thickness and spacing of the aggregate drains shall be as shown on the plan. Trenches for aggregate drains shall be excavated to a minimum width of 300 mm and to the depth shown on the plans or ordered by the Engineer. The bottom of the trench shall be sloped to drain and shall be free from loose particles of soil. The trench shall be excavated so as to expose clearly the granular pavement courses to be drained.

Aggregate for the drains shall be durable gravel, stone or slag and shall be free from vegetable matter and other deleterious substances. The grading requirements are given at Table 300-4. Type B grading may be used only where the drain is designed to intercept surface water flowing to the pipe and is likely to get slowly blocked. Type A grading allows a much wider range.

TABLE 300-4. GRADING REQUIREMENTS FOR AGGREGATE DRAINS

  - . Measurements for Payment

Measurement for surface and sub -surface drains shall be per running metre length of the drain. Disposal of surplus material beyond 1000 m shall be measured in cu. m.

- Sub-Bases, Bases (Non - Bituminous)

##### GRANULAR SUB-BASE

  - Scope

This work shall consist of laying and compacting well-graded material on prepared subgrade in accordance with the requirements of these Specifications. The material shall be laid in one or more layers as sub-base or lower sub-base and upper sub-base (termed as sub-base hereinafter)as necessary according to lines, grades and cross -sections shown on the drawings or as directed by the Engineer.

  - . Materials

    - . The material to be used for the work shall be natural sand, moorum, gravel, crushed stone, or combination thereof depending upon the grading required. Materials like crushed slag, crushed concrete, brick metal and kankar may be allowed only with the specific approval of the Engineer. The material shall be free from organic or other deleterious constituents and conform to one of the three gradings given in Table400-1.

While the gradings in Table 400-1 are in respect of close-graded granular sub-base materials, one each for maximum particle size of 75mm, 53 mm and 26.5 mm, the corresponding gradings for the coarse graded materials for each of the three maximum particle sixes are given at Table 400-2. The grading to be adopted for a project shall be as specified in the Contract.

    - . Physical requirements: The material shall have a 10 per cent fines value of 50 kN or more (for sample in soaked condition)when tested in compliance with BS:812 (Part 111). The water absorption value of the coarse aggregate shall be determined as per IS: 2386 (Pan3); if this value is greater than 2 per cent, the soundness test shall be carried out on the material delivered to site as per IS: 383.For Grading II and III materials, the CBR shall be determined at the density and moisture content likely to be developed in equilibrium conditions which shall be taken as being the density relating to a uniform air voids content of 5 per cent.

TABLE 400-1. GRADING FOR CLOSE-GRADED GRANULAR SUB-BASE MATERIALS

TABLE 400-2. GRADING FOR COARSE GRADED GRANULAR SUB –BASK MATERIALS

Note: The material passing 425 micron (0.425 mm) sieve for all the three gradings when vested according to IS : 2720 (Pan 5) shall have liquid limit and plasticity index not more than 25 and 6 per cent respectively.

  - Strength of sub-base

It shall be ensured prior to actual execution that the material to be used in the sub-base satisfies the requirements of CBR and other physical requirements when compacted and finished.

When directed by the Engineer, this shall be verified by performing CBR tests in the laboratory as required on specimens remoulded at field dry density and moisture content and any other tests for the "quality" of materials, as may be necessary.

  - Construction Operations

    - Preparation of subgrade : Immediately prior to the laying of sub-base, the subgrade already finished to Clause 301 or 305 as applicable shall be prepared by removing all vegetation and other extraneous matter, lightly sprinkled with water if necessary and rolled with two passes of 80 -100 kN smooth wheeled roller.

    - . Spreading and compacting: The sub-base material of grading specified in the Contract shall be spread on the prepared subgrade with the help of a motor grader of adequate capacity, its blade having hydraulic controls suitable for initial adjustment and for maintaining the required slope and grade during the operation or other means as approved by the Engineer.

When the sub-base material consists of combination of materials mentioned in Clause 401.2.1, mixing shall be done mechanically by the mix in-place method.

Manual mixing shall be permitted only where the width of laying is not adequate for mechanical operations, as in small-sized jobs. The equipment used for mix-in -place construction shall be a rotavator or similar approved equipment capable of mixing the material to the desired degree. If so desired by the Engineer, trial runs with the equipment shall be carried out to establish its suitability for the work.

Moisture content of the loose material shall be checked in accordance with 15:2720 (Part 2) and suitably adjusted by sprinkling additional water from a truck mounted or trailer mounted

water tank and suitable for applying water uniformly and at controlled quantities to variable widths of surface or other means approved by the Engineer so that, at the time of compaction, it is from 1 per cent above to 2 per cent below the optimum moisture content corresponding to IS: 2720 (Part 8). While adding water, due allowance shall be made for evaporation losses. After water has been added, the material shall be processed by mechanical or other approved means like disc harrows, rotavators until the layer is uniformly wet.

Immediately thereafter, rolling shall start. If the thickness of the compacted layer does not exceed 100 mm, a smooth wheeled roller of 80 to 100 KN weight may be used. For a compacted single layer upto 225 mm the compaction shall be done with the help of a vibratory roller of minimum 80 to 100 kN static weight with plain drum or pad foot drum or heavy pneumatic tyred roller of minimum 200 to 300 kN weight having a minimum tyre pressure of 0.7 MN/m2 or equivalent capacity roller capable of achieving the required compaction. Rolling shall commence at the lower edge and proceed towards the upper edge longitudinally for portions having unidirectional cross fall and super-elevation and shall commence at the edges and progress towards the centre for portions having cross fall on both sides.

Each pass of the roller shall uniformly overlap not less than one third of the track made in the preceding pass. During rolling, the grade and cross fall (camber) shall be checked and any high spots or depressions, which become apparent, corrected by removing or adding fresh material.

The speed of the roller shall not exceed 5 km per hour. Rolling shall be continued all the density achieved is at least 98per cent of the maximum dry density for the material determined as per IS: 2720 (Part 8). The surface of any layer of material on completion of compaction shall be well closed, free from movement under compaction equipment and from compaction planes, ridges, cracks or loose material. All loose, segregated or otherwise defective areas shall be made good to the full thickness of layer and re - compacted.

  - . Surface Finish and Quality Control of Work

The surface finish of construction shall conform to the requirements of Clause 902.

Control on the quality of materials and works shall be exercised by the Engineer in accordance with Section 900.

  - .Arrangements for Traffic

During the period of construction, arrangement of traffic shall be maintained in accordance with Clause 112.

  - Measurements for Payment

Granular sub -base shall be measured as finished work in position in cubic metres.

The protection of edges of granular sub-base extended over the full formation as shown in the drawing shall be considered incidental to the work of providing granular sub-base and as such no extra payment shall be made for the same.

##### WET MIX MACADAM SUB -BASE/BASE

  - . Scope

This work shall consist of laying and compacting clean, crushed, graded aggregate and granular material, premixed with water, to a dense mass on a prepared subgrade/sub -base/base or existing pavement as the case may be in accordance with the requirements of these Specifications. The material shall be laid in one or more layers as necessary to lines, grades and cross -sections shown on the approved drawings or as directed by the Engineer.

The thickness of a single compacted Wet Mix Macadam layer shall not be less than 75 mm. When vibrating or other approved types of compacting equipment arc used, the compacted depth of a single layer of the sub-base course may be increased to 200 mm upon approval of the Engineer.

  - Materials

    - . Aggregates

      - Physical requirements: Coarse aggregates .shall be crushed stone. If crushed gravel/shingle is used, not less than 90 per cent by weight of the gravel/shingle pieces retained on 4,75 mm sieve shall have-at least two fractured faces. The aggregates shall conform to the physical requirements set forth in Table 400 -10 below,

Table 400-10. PHYSICAL REQUIREMENTS OF COARSE AGGREGATES FOR WET MIX MACADAM FOR SUB-BASE/BASE COURSES

* Aggregate may satisfy requirements of either of the two tests.

If the water absorption value of the coarse aggregate is greater than 2 per cent, the soundness test shall be carried out on the material delivered to site as per IS: 2386 (Part-5).

      - Grading requirements: The aggregate shall conform to the grading given in Table 400-11.

Table 400-11. GRADING REQUIREMNTS OF AGGREGATES FOR WET MIX MACADAM

Materials finer than 425 micron shall have Plasticity Index (PI) not exceeding 6.

The final gradation approved within these limits shall be well graded from coarse to fin and shall not vary from the low limit on one sieve to the high limit on the adjacent sieve or vice versa.

  - Construction Operations

    - . Preparation of base: Clause 404.3.1 shall apply.

    - Provision of lateral confinement of aggregates: While constructing wet mix macadam, arrangement shall be made for the lateral confinement of wet mix. This shall be done by laying materials in adjoining shoulders along with that of wet mix macadam layer and following the sequence of operations described in Clause 407.4.1.

    - . Preparation of mix: Wet Mix Macadam shall be prepared in an approved mixing plant of suitable capacity having provision for controlled addition of water and forced/positive mixing arrangement like pug mill or pan type mixer of concrete batching plant. For small quantity of wet mix work, the Engineer may permit the mixing to be done in concrete mixers.

Optimum moisture for mixing shall be determined in accordance with IS:2720 (Part -8) after replacing the aggregate fraction retained on_22A mm sieve with material of 4.75 mm to 22.4 mm size. While adding water, dup allowance should be made for evaporation losses. However, at the time of compaction, water in the wet mix should not vary from the optimum value by more than agreed limits. The mixed material should be uniformly wet and no segregation should be permitted.

    - Spreading of mix: Immediately after mixing, the aggregates shall be spread uniformly and evenly upon the prepared subgrade/sub- base/base in required quantities. In no case should these be dumped in heaps directly on the area where these are to be laid nor shall their hauling over a partly completed stretch be permitted.

The mix may be spread either by a payer finisher or motor grader. For portions where mechanical means cannot be used, manual means as approved by the Engineer shall be used. The motor grader shall be capable of spreading the material uniformly all over the surface. Its blade shall have hydraulic control

suitable for initial adjustments and maintaining the same so as to achieve the specified slope and grade. The paver finisher shall be self-propelled, having the following features:

- Loading hoppers and suitable distribution mechanism

- The screed shall have lamping and vibrating arrangement for initial compaction to the layer as it is spread without rutting or otherwise marring the surface profile.

- The paver shall be equipped with necessary control mechanism so as to ensure that the finished surface is free from surface blemishes.

The surface of the aggregate shall be carefully checked with templates and all high or low spots remedied by removing or adding aggregate as may be required. The layer may be tested by depth blocks during construction. No segregation of larger and fine particles should be allowed. The aggregates as spread should be of uniform gradation with no pockets of fine materials.

    - Compaction: After the mix has been laid to the required thickness, grade and crossfall/camber the same shall be uniformly compacted, to the full depth with suitable roller. If the thickNess of single compacted layer does not exceed 100 mm, a smooth wheel roller of 80 to 100 kN weight may be used. For a compacted single layer upto 200 mm, the compaction shall be done with the help of vibratory roller of minimum static weight of 80 to 100 kN or equivalent capacity roller. The speed of the roller shall not exceed 5 km/h.

In portions having unidirectional cross fall/superelevation, rolling shall commence from the lower edge and progress gradually towards the upper edge. Thereafter, roller should progress parallel to the centre line of the road, uniformly over- lapping each preceding track by at least one third width until the entire surface has been rolled. Alternate trips of the roller shall be terminated in stops at least 1 m away from any preceding stop.

In portions in camber, rolling should begin at the edge with the roller running forward and backward until the edges have been firmly compacted. The roller shall then progress gradually towards the centre parallel to the centre line of the road uniformly overlapping each of the preceding track by at least one-third width until the entire surface has been rolled.

Any displacement occurring as a result of reversing of the direction of a roller or from any other cause shall be corrected" at once as specified and/or removed and made good.

Along forms, kerbs, walls or other places not accessible to the roller, the mixture shall be thoroughly compacted with mechanical tampers or a plate compactor. Skin patching of an area without scarifying the surface to permit proper bonding of the added material shall not be permitted.

Rolling should not be done when the subgrade is soft or yielding or when it causes a wave-like motion m the sub-base/base course or subgrade. If irregularities develop during rolling which exceed 12 mm when

tested with a 3 metre straight edge, the surface should be loosened and premixed material added or removed as required before rolling again so as to achieve a uniform surface conforming to the desired grade and crossfall. In no case should the use of unmixed material be permitted to make up the depressions.

Rolling shall be continued till the density achieved is at least 98 per cent of the maximum dry density for the material as determined by the method outlined in IS: 2720 (Part -8)

After completion, the surface of any finished layer shall be well closed, free from movement under compaction equipment or any compaction planes, ridges, cracks and loose material. All loose, segregated or otherwise defective areas shall be made good to the full thickness of the layer and recompacted.

    - Setting and drying: After final compaction of wet mix macadam course, the road shall be allowed to dry for 24 hours.

  - Opening to Traffic

Preferably no vehicular traffic of any kind should be allowed on the finished wet mix macadam surface till it has dried and the wearing course laid.

  - Surface Finish and Quality Control of Work

    - Surface evenness: The surface finish of construction shall conform to the requirements of Clause 902,

    - . Quality control: Control on the quality of materials and works shall be exercised by the Engineer in accordance with Section 900.

  - . Rectification of Surface Irregularity

Where the surface irregularity of the wet mix macadam course exceeds the permissible tolerances or where the course is otherwise defective due to subgrade soil getting mixed with the aggregates, the full thickness of the layer shall be scarified over the affected area, re - shaped with added premised material or removed and replaced with fresh premixed material as applicable and recompacted in accordance with Clause 406.3. The area treated in the aforesaid manner shall not be less than 5 m long and 2 m wide. In no case shall depressions be filled up with unmixed and ungraded material or fines,

  - Arrangement for Traffic

During the period of construction, arrangement of traffic shall be done as per Clause 112,

  - . Measurements for Payment

Wet mix macadam shall be measured as finished work in position in cubic metres.

- Base and Surface Courses (Bituminous)

##### GENERAL REQUIREMENTS FOR BITUMINOUS PAVEMENT LAYERS

  - General

Bituminous pavement courses shall be made using the materials described in the following Specifications. The use of machinery and equipment mentioned in various Clauses of these Specifications is mandatory. Details of the machinery and equipment are available in the Manual for Construction and Supervision of Bituminous Works. Equipment mandatory for any particular project shall be in accordance with the Contract Specification for that project.

  - Materials

    - Binder: The binder shall be an appropriate type of bituminous material complying with the relevant Indian Standard (IS), as defined in the appropriate Clauses of these Specifications, or as otherwise specified herein. The choice of binder shall be stipulated in the Contract or by the Engineer. Where penetration grades of bitumen are specified, they are referred to by a single- figure designation in accordance with IS:73. Thus bitumen grade 35 refers to bitumen in the penetration range 30 to 40. Where Modified Binder is specified, the Clause 521 of these Specifications shall apply.

    - Coarse Aggregates: The coarse aggregates shall consist of crushed rock, crushed gravel or other hard material retained on the 2.36 mm sieve. They shall be clean, hard, durable of cubical shape, free from dust and soft or friable matter, organic or other deleterious matter. Where the Contractor's selected sources of aggregates have poor affinity for bitumen, as a condition for the approval of that source, the bitumen shall be treated with approved anti-stripping agents, as per the manufacturer's recommendations, without additional payment. Before approval of the source the aggregates shall be tested for stripping.

The aggregates shall satisfy the physical requirements set forth in the individual relevant clause for the material in question.

Where crushed gravel is proposed for use as aggregate, not less than 90% by weight of the crushed material retained on the 4.75 mm sieve shall have at least two fractured faces.

    - Fine Aggregates: Fine aggregates shall consist of crushed or naturally occurring material, or a combination of the two, passing 2.36mm sieve and retained on the 75 micron sieve. They shall be clean, hard, durable, dry and free from dust, and soft or friable matter, organic or other deleterious matter.

    - Source of material: The source of all materials to be used on the project must be tested to the satisfaction of and be expressly approved by the Engineer. The Engineer may from time to time withdraw approval of a specific source, or attach conditions to the existing approval. Any change in aggregate source for bituminous mixes, will require a new mix design, and laying trials, where the mix is based on a job mix

design. Stockpiled from different sources, approved or otherwise, shall be kept separate, such that there is no contamination between one material and another. Each source submitted for approval shall contain sufficient material for at least 5 days work.

  - Mixing

Pre-mixed bituminous materials, including bituminous macadam, dense bituminous macadam, semi-dense bituminous concrete and bituminous concrete, shall be prepared in a hot mix plant of adequate capacity and capable of yielding a mix of proper and uniform quality with thoroughly coated aggregates. Appropriate mixing temperatures can be found in Table 500-5 of these Specifications; the difference in temperature between the binder and aggregate should at no time exceed 14°C. In order to ensure uniform quality of the mix and better coating of aggregates, the hot mix plant shall be calibrated from time to time.

If a continuous mixing-plant is to be used for mixing the bituminous bound macadam; the Contractor must demonstrate by laboratory analysis that the cold feed combined grading is within the grading limits specified for that bituminous bound material. In the case of a designed job mix, the bitumen and filler content shall be derived using this combined grading. Further details are available in the Manual for Construction and Supervision of Bituminous Works.

  - Transporting

Bituminous materials shall be transported in clean insulated vehicles, and unless otherwise agreed by the Engineer, shall be covered while in transit or awaiting tipping. Subject to the approval of the Engineer, a thin coating of diesel or lubricating oil may be applied to the interior of the vehicle to prevent sticking and to facilitate discharge of the material.

  - Laying

    - Weather and seasonal limitations: Laying shall be suspended while free-standing water is present on the surface to be covered, or during rain, fog and dust storms. After rain, the bituminous surface, prime or tack coat shall be blown off with a high pressure air jet to remove excess moisture, or the surface left to dry before laying shall start. Laying of bituminous mixtures shall not be carried out when the air temperature at the surface on which it is to be laid is below 10°C or when the wind speed at any temperature exceeds 40 km/h at 2m height unless specifically approved by the Engineer.

    - Cleaning of surface: The surface on which the bituminous work is to be laid shall be cleaned of all loose and extraneous matter by means of a mechanical broom or any other approved equipment / method as specified in the contract. The use of a high pressure air jet from a compressor to remove dust or loose matter shall be available full time on the site, unless otherwise specified in the Contract.

    - Spreading: Except in areas where a mechanical paver cannot access, bituminous materials shall be spread, levelled and tamped by an approved self-propelled paving machine. As soon as possible after arrival at site, the materials shall be supplied continuously to the paver and laid without delay.

The rate of delivery of material to the paver shall be regulated to enable the paver to operate continuously. The travel rate of the paver, and its method of operations, shall be adjusted to ensure an even and uniform flow of bituminous material across the screed, free from dragging, tearing and segregation of the material. In areas with restricted space where a mechanical pave r cannot be used, the material shall be spread, raked and levelled with suitable hand tools by experienced staff, and compacted to the satisfaction of the Engineer.

The minimum thickness of material laid in each paver pass shall be in accordance with the minimum values given in the relevant parts of these Specifications. When laying binder course or wearing course approaching an expansion joint of a structure, machine laying shall stop 300mm short of the joint. The remainder of the pavement up to the joint, and the corresponding area beyond it, shall be laid by hand, and the joint or joint cavity shall be kept clear of surfacing material.

Bituminous material, with a temperature greater than 145°C, shall p not be laid or, deposited on bridge deck waterproofing systems, unless precautions against heat damage have been approved by the Engineer.

Hand placing of pre -mixed bituminous materials shall only be permitted in the following circumstances:

- For laying regulating courses of irregular shape and varying thickness.

- In confined spaces where it is impracticable for a paver to operate.

- For footways.

- At the approaches to expansion joints at bridges, viaducts or other structures.

- For laying mastic asphalt in accordance with Clause 515.

- For filling of potholes.

- Where directed by the Engineer.

Manual spreading of pre - mixed wearing course material or the addition of such material by hand- spreading to the paved area, for adjustment of level, shall only be permitted in the following circumstances:

- At the edges of the layers of material and at gullies and manholes.

- At the approaches to expansion joints at bridges, viaducts or other structures.

- As directed by the Engineer.

    - Cleanliness and overlaying: Bituminous material shall be kept clean and uncontaminated. The only traffic permitted to run on bituminous material to be overlaid shall be that engaged in laying and compacting the next course or, where a binder course is to be sealed or surface dressed, that engaged on

such surface treatment. Should any bituminous material become contaminated the Contractor shall make it good to the satisfaction of the Engineer, in compliance with Clause 501.8.

Binder course material shall not remain uncovered by either the wearing course or surface treatment, whichever is specified in the Contract, for more than three consecutive days after being laid. The Engineer may extend this period, by the minimum amount of time necessary, because of weather conditions or for any other reason. If the surface of the base course is subjected to traffic, or not covered within three days, a tack coat shall be applied, as directed by the Engineer.

  - Compaction

Bituminous materials shall be laid and compacted in layers which enable the specified thickness, surface level, regularity requirements and compaction to be achieved.

Compaction of bituminous materials shall commence as soon as possible after laying. Compaction shall be substantially completed before the temperature falls below the minimum rolling temperatures stated in the relevant part of these Specifications. Rolling of the longitudinal joints shall be done immediately behind the paving operation. After this, rolling shall commence at the edges and progress towards the centre longitudinally except that on super elevated and unidirectional cambered portions, it shall progress from the lower to the upper edge parallel to the centre line of the pavement. Rolling shall continue until all roller marks have been removed from the surface. All deficiencies in the surface after laying shall be made good by the attendants behind the paver, before initial rolling is commenced. The initial or breakdown rolling shall be done with 8-10 tonnes dead weight smooth-wheeled rollers. The intermediate rolling shall be done with 8-10 tonnes dead weight or vibratory roller or with a pneumatic tyred roller of 12 to 15 tonnes weight having nine wheels, with a tyre pressure of at least 5.6 kg/sqcm. The finish rolling shall be done with 6 to 8 tonnes smooth wheeled tandem rollers.

Where compaction is to be determined by density of cores the requirements to prove the performance of rollers shall apply in order to demonstrate that the specified density can be achieved. In such cases the Contractor shall nominate the plant, and the method by which he intends to achieve the specified level of compaction and finish at temperatures above the minimum specified rolling temperature. Laying trials shall then demonstrate the acceptability of the plant and method used.

Bituminous materials shall be rolled in a longitudinal direction, with the driven rolls nearest the paver. The roller shall first compact material adjacent to joints and then work from the lower to the upper side of the layer, overlapping on successive passes by at least one-third of the width of the rear roll or, in the case of a pneumatic -tyred roller, at least the nominal width of 300mm

In portions with super-elevated and unidirectional camber, after the edge has been rolled, the roller shall progress from the lower to the upper edge.

Rollers should move at a speed of not more than 5 km per hour. The roller shall not be permitted to stand on pavement which has not been fully compacted, and necessary precautions shall be taken to prevent dropping of oil, grease, petrol or other foreign matter on the pavement either when the rollers are operating or standing. The wheels of rollers shall be kept moist with water, and the spray system provided with the machine shall be in good working order, to prevent the mixture from adhering to the wheels. Only sufficient moisture to prevent adhesion between the wheels of rollers and the mixture should be used. Surplus water shall not be allowed to stand on the partially compacted pavement.

  - Joints

Where longitudinal joints are made in pre-mixed bituminous materials, the materials shall be fully compacted and the joint made flush in one of the following ways; only method (iii) shall be used for transverse joints:

- by heating the joints with an approved joint beater when the adjacent width is being laid, but without cutting back or coating with binder. The heater shall raise the temperature of the full depth of material, to within the specified range of minimum rolling temperature and maximum temperature at any stage for the material, for a width not less, Am 75 mm, The Contractor shall have equipment available, for use in the event of a beater breakdown, to form joints by method (iii);

- by using two or more pavers operating in echelon, where this is practicable, and in sufficient proximity for adjacent widths to be fully compacted by continuous rolling;

- bycuttmgbaeklbeexposedjou<,foradistanceequaltothespecifiedlayerthickness, to vertical face, discarding all loosened material and coating the vertical face completely, with 80/100 penetration grade hot bitumen, or cold-applied bitumen, or polymer modified adhesive bitumen tape with a minimum thickness of 2 mm, before the adjacent width is laid.

All joints shall be offset at least 300 mm from parallel joints in the layer beneath or as directed, and in a layout approved by the Engineer. Joints in the wearing course shall coincide with either the lane edge or the lane marking, whichever is appropriate. Longitudinal joints shall not be situated in wheel track zones.

  - Preparation of Surface

    - Scope: This work shall consist of preparing an existing granular or black-topped surface bituminous course. The work shall be performed on such widths and lengths as shown on the drawings or as instructed by the Engineer. The existing surface shall be firm and clean, and treated with Prime or Tack coat as shown on the drawings as otherwise stated in the Contract.

    - Materials

25.8.2.1 For scarifying and re -laying the granular surface: The material used shall be coarse aggregate salvaged from the scarification of the existing granular base course supplemented by fresh

coarse aggregate and screenings so that aggregates and screenings thus supplemented correspond to Clause 404: Water Bound Macadam or Clause 406: Wet Mix Macadam of the Ministry's Specification for Road and Bridge Works (third revision) 1995.

    - Construction Operations

      - Preparing existing granular surface: Where the existing surface is granular, all loose materials shall be removed, and the surface lightly watered where the profile corrective course to be provided as a separate layer is also granular. Where the profile corrective course of bituminous material is to be laid over the existing granular surface, the latter shall, after removal of all loose material, be primed in accordance with Clause 502.

The surface finish of all granular layers on which bituminous works are to be placed, shall, unless otherwise specifically instructed by the Engineer, be free from dust. All such layers must be capable of being swept, after the removal of any non- integral loose material, by means of a mechanical broom, without shedding significant quantities of material and dust removed by air jet, washing, or other means approved by the Engineer.

After cleaning the surface shall be correct to line and level, within the tolerances specified for base course.

      - Scarifying existing bituminous surface: Where specified or shown on the drawings, the existing bituminous layer in the specified width shall be removed with care and without causing undue disturbance to the underlying layer, by a suitable method approved by the Engineer. After removal, all loose and disintegrated material, the underlying layers which might have been disturbed should be suitably reworked and compacted to line and level. After supplementing the base material as necessary with suitable fresh stone, the compacted finished surface shall be primed in accordance with Clause 502. Reusable materials shall be stacked as directed by the Engineer within 1000 m of their origin.

    - Surface finish and quality control of work: The relevantprovisions of Section 900 shall apply.

    - Arrangements for traffic: During construction operations, arrangements for traffic shall be made in accordance with the provisions of Clause 112 of the Ministry's Specification for Road and Bridge Works (third revision) 1995.

    - Environmental protection: The provisions of Clause 111 of the Ministry's Specification for Road and Bridge Works (third revision) 1995 and the provision of Annexure A to Clause 501shall apply.

    - Measurement for payment

##### PRIME COAT OVER GRANULAR BASE

  - Scope

This work shall consist of the application of a single coat of low viscosity liquid bituminous material to a porous granular surface preparatory to the superimposition of bituminous treatment or mix.

  - Materials

    - Primer: The choice of a bituminous primer shall depend upon the porosity characteristics of the surface to be primed as classified in IRC: 16.These are:

- Surfaces of low porosity; such as wet mix macadam and water bound macadam,

- Surfaces of medium porosity; such as cement stabilised soil base,

- Surfaces of high porosity; such as a gravel base.

    - Primer viscosity: The type and viscosity of the primer shall comply with the requirements of IS 8887, as sampled and tested for bituminous primer in accordance with these standards. Guidance on viscosity and rate of spray is given in Table 500-1.

TABLE 500-1. VISCOSITY REQUIREMENT AND QUANTITY OF LIQUID BITUMINOUS PRIMER

    - Choice of primer: The primer shall be bitumen emulsion, complying with IS 8887 of a type and grade as specified in the Contract or as directed by the Engineer. The use of medium curing cutback as per IS 217 shall be restricted only for sites at sub-zero temperatures or for emergency applications as directed by the Engineer.

  - Weather and Seasonal Limitations

Bituminous primer shall not be applied to a wet surface (see 502.4.2) or during a dust storm or when the weather is foggy, rainy or windy or when the temperature in the shade is less than 10°C. Surfaces which are to receive emulsion primer should be damp, but no free or standing water shall be present.

  - Construction

    - Equipment: The primer distributor shall be a self-propelled pi or towed bitumen pressure sprayer equipped for spraying the material uniformly at specified rates and temperatures. Hand spraying of small & areas, inaccessible to the distributor, or in narrow strips shall be sprayed with a pressure hand sprayer, or as directed by the Engineer.

    - Preparation of road surface: The surface to be primed shall be prepared in accordance with Clauses 501.8 and 902 as appropriated. Immediately prior to applying the primer the surface shall be carefully swept clean of dust and loose particles, care being taken not to disturb the interlocked aggregate.

This is best achieved when the surface layer is slightly moist (lightly sprayed with water and the surface allowed to dry) and the surface should be kept moist until the primer is applied.

    - Application of bituminous primer: The viscosity and rate of application of the primer shall be as specified in the Contract, or as determined by site trials carried out as directed by the Engineer. Where a geosynthetic is proposed for use, the requirements of Clauses 704.3.2 and 704.4 of the Ministry's Specification for Road and Bridge Works (third revision) 1995 shall apply. The bituminous primer shall be sprayed uniformly in accordance with Clause 501.The method for application of the primer will depend on the type of equipment to be used, size of nozzles, pressure at the spray bar and speed of forward movement. The Contractor shall demonstrate at a spraying trial, that the equipment and method to be used is capable of producing a uniform spray, within the tolerances specified.

    - Curing of primer and opening to traffic: A primed surface shall be allowed to cure for at least 24 hours or such other period as is found to be necessary to allow all the volatiles to evaporate before any subsequent surface treatment or mix is laid. Any unabsorbed primer shall first be blotted with an application of sand, using the minimum quantity possible. A primed surface shall not be opened to traffic other than that necessary to lay the next course. A very thin layer of clean sand may be applied to the surface of the primer, to prevent the primer picking up under the wheels of the paver and the trucks delivering bituminous material to the paver.

    - Tack coat: Over the primed surface, a tack coat should be applied in accordance with Clause 503.

  - Quality Control of Work

For control of the quality of materials supplied and the works carried out, the relevant provisions of Section 900 shall apply.

  - Arrangements for Traffic

During construction operations, arrangements for traffic shall be made in accordance with the provisions of Clause 112 of the Ministry's Specification for Road and Bridge Works (third revision) 1995.

  - Measurement for Payment

Prime coat shall be measured in terms of surface area of application in square metres.

##### TACK COAT

  - Scope

This work shall consist of the application of a single coat of low viscosity liquid bituminous material to an existing bituminous road surface preparatory to the superimposition of a bituminous mix, when specified in the Contract or instructed by the Engineer.

  - Materials

    - Binder: The binder used for tack coat shall be bitumen emulsion complying with IS 8887 of a type and grade as specified in the Contract or as directed by the Engineer. The use of cutback bitumen as per IS 217 shall be restricted only for sites at sub-zero temperatures or for emergency applications as directed by the Engineer.

  - Weather and Seasonal Limitations

Bituminous material shall not be applied to a wet surface or during a dust storm or when the weather is foggy, rainy or windy or when the temperature in the shade is less than 10°C. Where the tack coat consists of emulsion, (he surface shall be slightly damp, but not wet. Where the tack coat is of cutback bitumen, the surface shall be dry.

  - Construction

    - .Equipment: The tack coat distributor shall be a self-propelled or towed bitumen pressure sprayer, equipped for spraying the material uniformly at a specified rate. Hand spraying of small areas, inaccessible to the distributor, or in narrow strips, shall be sprayed with a pressure hand sprayer, or as directed by the Engineer.

    - Preparation of base: The surface on which the tack coat is to be Applied shall be clean and free from dust, dirt, and any extraneous material, and be otherwise prepared in accordance with the requirements of Clauses 501.8 and 902 as appropriate. Immediately before the application of the tack coat, the surface shall be swept clean with a mechanical broom, and high pressure air jet, or by other means as directed by the Engineer.

    - Application of tack coat: The application of tack coat shall be at the rate specified in the Contract, and shall be applied uniformly. If rate of application of Tack Coat is not specified in the contract then it shall be at the rate specified in Table 500-2. The normal range of spraying temperature for a bituminous emulsion shall be 20°C to 70°C and for a cutback, 50°C to 80°C if RC-70/MC-70 is used. Where a geosynthetic is proposed for use, the provisions of Clauses 704.3.2 and 704.4.4 of the Ministry's Specification for Road and Bridge Works (third revision) 1995 shall apply. The method of application of the tack coat will depend on the type of equipment to be used, size of nozzles, pressure at the spray bar, and speed of forward movement. The Contractor shall demonstrate at a spraying trial, that the equipment and method to be used is capable of producing a uniform spray, within the tolerances specified. Where the material to receive an overlay is a freshly laid bituminous layer, that has not been subjected to traffic, or contaminated by dust, a tack coat is not mandatory where the overlay is completed within two days.

TABLE 500-2. RATE OF APPLICATION OF TACK COAT

    - Curing of tack coat: The tack coat shall be left to cure until all the volatiles have evaporated before any subsequent construction is started. No plant or vehicles shall be allowed on the tack coat other than those essential for the construction.

  - Quality Control of Work

For control of the quality of materials supplied and the works carried out, the relevant provisions of Section 900 shall apply.

  - Arrangements for Traffic

During the period of construction, arrangements for traffic shall be made in accordance with the provisions of Clause 112 of the Ministry's Specification for Road and Bridge Works (third revision) 1995.

  - Measurement for Payment

Tack coat shall be measured in terms of surface area of application in square metres.

##### DENSE GRADED BITUMINOUS MACADAM

  - Scope

This clause specifies the construction of Dense Graded Bituminous Macadam, (DBM), for use mainly, but not exclusively, in base/binder and profile corrective courses. DBM is also intended for use as road base material. This work shall consist of construction in a single or multiple layers of DBM on a previously prepared base or sub-base. The thickness of a single layer shall be 50mm to 100mm.

  - Materials

    - Bitumen: The bitumen shall be paving bitumen of Penetration Grade complying with Indian Standard Specifications for "Paving Bitumen" IS: 73, and of the penetration indicated in Table 500- 10 for dense bitumen macadam, or this bitumen as modified by one of the methods specified in Clause 521, or as otherwise specified in the Contract. Guidance on the selection of an appropriate grade of bitumen is given in The Manual for Construction and Supervision of Bituminous Works.

    - Coarse aggregates: The coarse aggregates shall consist of crushed rock, crushed gravel or other hard material retained on the 2.36 mm sieve. They shall be clean, hard, durable, of cubical shape, free from dust and soft or friable matter, organic or other deleterious substances. Where the Contractor's selected source of aggregates have poor affinity for bitumen, as a condition for the approval of that source,

the bitumen shall be treated with an approved anti-stripping agent, as per the manufacturer's recommendations, without additional payment. Before approval of the source, the aggregates shall be tested for stripping. The aggregates shall satisfy the physical requirements specified in Table 500- 8, for dense bituminous macadam.

Where crushed gravel is proposed for use as aggregate, not less than 90% by weight of the crushed material retained on the 4.75 mm sieve shall have at least two fractured faces.

    - Fine aggregates: Fine aggregates shall consist of crushed or naturally occurring mineral material or a combination of the two, passing the 2.36mm sieve and retained on the 75 micron sieve. They shall be clean, hard, durable, dry and free from dust, and soft or friable matter, organic or other deleterious matter. The plasticity index of the fraction passing the 0.425 mm sieve shall not exceed 4. when tested in accordance with IS: 2720 (Part 5)

TABLE 500-8. PHYSICAL REQUIREMENTS FOR COARSE AGGREGATE FOR DENSE GRADED BITUMINOUS MACADAM

Notes: 1. IS: 2386Part I

- IS: 2386 Part I

- IS: 2386 Part 4*

- IS: 2386Part4*

- IS: 2386Part5

- IS: 2386 Part 3 (the elongation test to be done only on non-flaky aggregates in the sample)

- IS: 6241

- AASHTOT283**

* Aggregate may satisfy requirements of either of these two tests.

** The water sensitivity test is only required if the minimum retained coating in the stripping lest is less than 95%.

    - Filler: Filler shall consist of finely divided mineral matter such as rock dust, hydrated lime or cement approved by the Engineer.

TABLE 500-9. GRADING REQUIREMENTS FOR MINERAL FILLER

The filler shall be graded within the limits indicated in Table 500-9. by weight of total aggregate, shall be Portland cement or hydrated lime and the percentage of fine aggregate reduced accordingly. Cement or hydrated lime is not required when the limestone aggregate is used. Where the aggregates fail to meet the

requirements of the water sensitivity test in Table 500-8, then 2 per cent by total weight of aggregate, of hydrated lime shall be added without additional cost.

    - Aggregate grading and binder content:

When tested in accordance with IS:2386 Part 1 (wet sieving method), the combined grading of the coarse and fine aggregates and added filler for the particular mixture shall fall within the limits shown in Table 500- 10, for dense bituminous macadam grading 1 or 2 as specified in the Contract. The type and quantity of bitumen, and appropriate thickness, are also indicated for each mixture type.

Table 500-10. Composition of Dense Graded Bituminous Macadam Pavement Layers

Notes: 1. The combined aggregate grading shall not vary from the low limit on one sieve to the high limit on the adjacent sieve.

- Determined by the Marshall method.

  - Mixture Design

    - Requirement for the mixture: Apart from conformity with the grading and quality requirements for individual ingredients, the mixture shall meet the requirements set out in Table 500-11.

TABLE 500-11. REQUIREMENTS FOR DENSE GRADED BITUMINOUS MACADAM

The requirements for minimum per cent voids in mineral aggregate (VMA) are set out in Table 500-12.

TABLE 500-12. MINIMUM PER CENT VOIDS IN MINERAL AGGREGATE (VMA)

Notes: 1. The nominal maximum particle size is one size larger than the first sieve to retain more than: 10'per cent.

- Interpolate minimum voids in the mineral aggregate (VMA) for design air voids values between those listed.

    - . Binder content: The binder content shall be optimised to achieve the requirements of the mixture set out in Table 500-11 and the traffic volume specified in the Contract. The Marshall method for determining the optimum binder content shall be adopted as described in The Asphalt Institute Manual MS- 2, replacing the aggregates retained on the 26.5 mm sieve by the aggregates passing the 26.5 mm sieve and retained on the 22.4 mm sieve, where approved by the Engineer.

Where 40 mm dense bituminous macadam mixture is specified, the modified Marshall method described in MS-2 shall be used. This method requires modified equipment and procedures; particularly the minimum stability values in Table 500-11 shall be multiplied by 2.25 and the minimum flow shall be 3 mm.

    - Job mix formula: The Contractor shall inform the Engineer in writing, at least 20 days before the start of the work, of the job mix formula proposed for use in the works, and shall give the following details:

- Source and location of all materials;

- Proportions of all materials expressed as follows where each is applicable:

  - Binder type, and percentage by weight of total mixture.

  - Coarse aggregate/Fine aggregate/Mineral filler as percentage by weight of total aggregate including mineral filler;

- A single definite percentage passing each sieve for the mixed aggregate;

- The individual gradings of the individual aggregate fractions, and the proportion of each in the combined grading.

- The results of tests enumerated in Table 500-11 as obtained by the Contractor;

- Where the mixer is a batch mixer, the individual weights of each type of aggregate, and binder per batch,

- Test results of physical characteristics of aggregates to be used;

- Mixing temperature and compacting temperature.

While establishing the job mix formula, the Contractor shall ensure that it is based on a correct and truly representative sample of the materials that will actually be used in the work and that the mixture and its different ingredients satisfy the physical and strength requirements of these Specifications.

Approval of the job mix formula shall be based on independent testing by the Engineer for which samples of all ingredients of the mix shall be furnished by the Contractor as required by the Engineer.

The approved job mix formula shall remain effective unless and until a revised Job Mix Formula is approved. Should a change in the source of materials be proposed, a new job mix formula shall be forwarded to the Engineer for approval before the placing of the material.

    - Plant trials - permissible variation in job mix formula:

Once the laboratory job mix formula is approved, the Contractor shall carry out plant trials at the mixer to establish that the plant can be set up to produce a uniform mix conforming to the approved job mix formula. The permissible variations of the individual percentages of the various ingredients in the actual mix from the job mix formula to be used shall be within the limits as specified in Table 500- 13. These variations are intended to apply to individual specimens taken for quality control tests in accordance with Section 900.

TABLE 500-13. PERMISSIBLE VARIATIONS FROM THE JOB MIX FORMULA

Once the plant trials have demonstrated the capability of the plant, and the trials are approved, the laying operation may commence. Over the period of the first month of production for laying on the works, the Engineer shall require additional testing of the product to establish the reliability and consistency of the plant.

    - Laving Trials: Once the plant trials have been successfully completed and approved, the Contractor shall carry out laying trials, to demonstrate that the proposed mix can be successfully laid, and compacted all in accordance with Clause SO 1. The laying trial shall be carried out on a suitable area which is not to form part of the works, unless specifically approved in writing, by the Engineer. The area of the laying trials shall be a minimum of 100 sq. m. of construction similar to that of the project road, and it shall be in all respects, particularly compaction, the same as the project construction, on which the bituminous material is to be laid.

The Contractor .shall previously inform the Engineer of the proposed method for laying and compacting the material. The plant trials shall then establish if the proposed laying plant, compaction plant, and methodology is capable of producing satisfactory results. The density of the finished paving layer shall be determined by taking cores, no sooner than 24 hours after laying, or by other approved method.

Once the laying trials have been approved, the same plant and methodology shall be applied to the laying of the material on the project, and no variation of either shall be acceptable, unless approved in writing by the Engineer, who may at his discretion require further laying trials.

  - Construction Operations

    - Weather and seasonal limitations: The provisions of Clause 501.5.1 shall apply.

    - . Preparation of base: The base on which Dense Graded Bituminous Material is to be laid shall be prepared in accordance with Clauses 501 and 902 as appropriate, or as directed by the Engineer. The surface shall be thoroughly swept clean by a mechanical broom, and the dust removed by compressed air. In locations where-mechanical broom cannot access, other approved methods shall be used as directed by the Engineer.

    - Geosynthetics: Where Geosynthetics are specified in the Contract this shall be in accordance with the requirements stated in Clause 704 of the Ministry's Specification for Road and Bridge Works (third revision) 1995.

    - . Stress absorbing layer: Where a stress absorbing layer is specified in the Contract, this shall be applied in accordance with the requirements of Clause 522.

    - Prime coat: Where the material on which the dense bituminous macadam is to be laid is other than a bitumen bound layer, a prime coat shall be applied, as specified, in accordance with the provisions of Clause 502, or as directed by the Engineer.

    - . Tack coat: Where the material on which the dense bituminous macadam is to be placed is bitumen bound surface, a tack coat shall be applied as specified, in accordance with the provisions of Clause 503, or as directed by the Engineer.

    - . Mixing and transportation of the mixture: The provisions as specified in Clauses 501.3 and

501.4 shall apply.

    - . Spreading: The provisions of Clauses 501.5.3 and 501.5.4 shall apply.

    - Rolling: The general provisions of Clauses 501.6 and 501.7 shall apply, as modified by the approved laying trials. The compaction process shall be carried out by the same plant, and using the same method, as approved in the laying trials, which may be varied only with the express approval of the Engineer in writing.

  - Opening to Traffic

The newly laid surface shall not be open to traffic for at least 24 hours after laying and completion of compaction, without the express approval of the Engineer in writing.

  - Surface Finish and Quality Control of Work

The surface finish; of the completed construction shall conform to the requirements of Clause 902. All materials and workmanship shall comply with the provisions set out in Section 900 of this Specification.

  - Arrangements for Traffic

During the period of construction, arrangements for traffic shall be made in accordance with the provisions of Clause 112 of the Ministry's Specification for Road and Bridge Works (third revision) 1995.

  - Measurement for Payment

Dense Graded Bituminous Materials shall be measured as finished work either in cubic metres, tons or by the square metre at a specified thickness as detailed on the Contract drawings, or documents, or as directed by the Engineer.

##### BITUMINOUS CONCRETE

  - Scope

This clause specifies the construction of Bituminous Concrete, for use in wearing and profile corrective courses. This work shall consist of construction in a single or multiple layers of bituminous concrete on a previously prepared bituminous bound surface. A single layer shall be 25mm to 100mm in thickness.

  - Materials

    - Bitumen: The bitumen shall be paving bitumen of Penetration grade complying with Indian Standard Specification for Paving Bitumen, IS: 73 and of the penetration indicated in Table 500-18, for bituminous concrete, or this bitumen as modified by one of the methods specified in Clause 521, or as otherwise specified in the Contract. Guidance on the selection of an appropriate grade of bitumen is given in The Manual for Construction and Supervision of Bituminous Works.

    - . Coarse aggregates: The coarse aggregates shall be generally as specified in Clause 507.2.2, except that the aggregates shall satisfy the physical requirements of Table 500-17.

    - Fine aggregates: The fine aggregates shall be all as specified in Clause 507.2.3.

    - . Filler: Filler shall be generally as specified in Clause 507.2.4. Where the aggregates fail to meet the requirements of the water sensitivity test in Table 500-17 then 2 per cent by total weight of aggregate, of hydrated lime shall be added without additional cost.

    - Aggregate grading and binder content: When tested in accordance with IS:2386 Part 1 (Wet grading method), the combined grading-of the coarse and fine aggregates and added filler shall fall within the limits shown in Table 500-18 for gradings 1 or 2 as specified in the Contract.

  - . Mixture Design

    - Requirements for the mixture: Apart from conformity with the grading and quality requirements for individual ingredients, the mixture shall meet the requirements set out in Table 500-19. The requirements for minimum per cent voids in mineral aggregate (VMA) are set out in Table 500-12.

    - Binder content: The binder content shall be optimised to achieve the requirements of the mixture set out in Table 500-19 and the traffic volume as specified in the Contract. The Marshall method for determining the optimum binder content shall be adopted as described in the Asphalt Institute Manual MS- 2, replacing the aggregates retained on the 26.5mm sieve and retained on the 22.4mm sieve, where approved by the Engineer.

TABLE 500-17. PHYSICAL REQUIREMENTS FOR COARSE AGGREGATE FOR BITUMINOUS CONCRETE PAVEMENT LAYERS

Notes: 1. IS: 2386 Part 1	6. IS: 2386 Part 5

- IS: 2386 Part 1	7. IS: 2386 Part 3

(the elongation test may be done only on non-flaky aggregates in the sample)

- IS: 2386 Part 4*	8. AASHTOT283**

- IS: 2386 Part 4*	9. IS: 6241

- BS: 812 Part 114

* Aggregate may satisfy requirements of either of these two tests.

** The water sensitivity test is only required if the minimum retained coating in the stripping test is ` lessthan 95%.

    - Job mix formula: The procedure for formulating the job mix formula shall be generally as specified in Clause 507.3.3 and the results of tests enumerated in Table 500-19 as obtained by the Contractors.

    - . Plant trials - permissible variation in job mix formula:

The requirements for plant trials shall be all as specified in Clause 507.3.4,and permissible limits for variation as shown in Table 500-13.

    - Laving trials: The requirements for laying trials shall be all as specified in Clause 507.3.5.

  - . Construction Operations

    - . Weather and seasonal limitations: The provisions of Clause 501.5.1 shall apply.

TABLE 500-18. COMPOSITION OF BITUMINOUS CONCRETE PAVEMENT LAYERS

Notes: 1. The combined aggregate grading shall not vary from the low limit on one sieve to the high limit on the adjacent sieve.

2.  Determined by the Marshall method.

TABLE 500 -19. REQUIREMENTS FOR BITUMINOUS PAVEMENT LAYERS

    - Preparation of base: The surface on which the bituminous concrete is to be laid shall be prepared in accordance with Clauses 501 and 902 as appropriate, or as directed by the Engineer. The surface shall be thoroughly swept clean by mechanical broom and dust removed by compressed air. In locations where a mechanical broom cannot access, other approved methods shall be used as directed by the Engineer.

    - Geosynthetics: Where Geosynthetics are specified in the Contract this shall be in accordance with the requirements stated in Clause 704 of the Ministry's Specification for Road and Bridge Works (third revision) 1995.

    - Stress absorbing layer. Where a stress absorbing layer is specified in the Contract, this shall be applied in accordance- with the requirements of Clause 522.

    - Tack coat: Where specified in the Contract, or otherwise required by the Engineer, a tack coat shall be applied in accordance with the requirements of Clause 503.

    - Mixing and transportation of the mixture: The provisions as specified in Clauses 501.3 and

501.4 shall apply.

    - Spreading: The general provisions of clauses 501.5.3 and 501.5.4 shall apply.

    - Rolling: The general provisions of clauses 501.6 and 501.7 shall apply, as modified by the approved laying trials.

  - Opening to Traffic

The newly laid surface shall not be open to traffic for at least 24 hours after laying and the completion of compaction, without the express approval of the Engineer in writing.

  - Surface Finish and Quality Control

The surface finish of the completed construction shall conform to the requirements of Clause 902. All materials and workmanship shall comply with the provisions set out in Section 900 of this Specification.

  - Arrangements for Traffic

During the period of construction, arrangements for traffic shall be made in accordance with the provisions of Clause 112 of the Ministry's Specification for Road and Bridge Works (third revision) 1995.

  - Measurement for Payment

The measurement shall be all as specified in Clause 507.8.

##### SHOULDERS, ISLANDS AND MEDIAN

  - Scope

The work shall consist of constructing shoulder (hard/paved/ earthen with brick or stone block edging) on either side of the pavement, median in the road dividing the carriageway into separate lanes and islands for channelising the traffic at junctions in accordance with the requirements of these Specifications and in conformity with the lines, grades and cross-sections shown on the drawings or as directed by the Engineer.

  - Materials

Shoulder on either side of the road may be of selected earth/ granular material/ paved conforming to the requirements of Clause 305/401 and the median may be of selected each conforming to the requirements of Clause 305.

Median/Traffic islands shall be raised and kerbed at the perimeter and the enclosed area filled with earth and suitably covered with grass turf/shrubs as per Clause 307 and/or paved as per Clause 409.3.4 or 409.3.5.

Paved shoulders shall consist of sub-base, base and surfacing courses, as shown in the drawings and materials for the same shall conform to relevant Specifications of the corresponding items. Where paved or hard shoulders are not provided, the pavement shall be provided with brick/stone block edgings as shown in the drawings. The bricks shall conform to Clause 1003 of these Specifications. Stone blocks shall conform to Clause 1004 of these Specifications and shall be of size 225 mm x 33 mm x 75 mm.

  - Size of Shoulders/Median/Islands

Shoulder (earthen/hard/paved) /median/traffic island dimensions shall be as shown on the drawings or as directed by the Engineer.

  - Construction Operations

    - Shoulder: The sequence of operations shall be such that the construction of paved shoulder is done in layers each matching the thickNess of adjoining pavement layer. Only after a layer of pavement and corresponding layers in paved and earth shoulder portion have been laid and compacted, the construction of next layer of pavement and shoulder shall be taken up.

Where the materials in adjacent layers are different, these shall be laid together and the pavement layer shall be compacted first. The corresponding layer in paved shoulder portion shall be compacted thereafter, which shall be followed by compaction of earth shoulder layer. The adjacent layers having same material shall be laid and compacted together.

In all cases where paved shoulders have to be provided alongside of existing carriageway, the existing shoulders shall be excavated in full width and to the required depth as per Clause 301.3.7. Under no circumstances, box cutting shall be done for construction of shoulders.

Compaction requirement of earthen shoulder shall be as per Table 300-2. In the case of bituminous courses, work on shoulder (earthen/hard/paved), shall start only after the pavement course has been laid and compacted.

During all stages of shoulder (earthen/hard/paved) construction, the required crossfall shall be maintained to drain off surface water.

Regardless of the method of laying, all shoulder construction material shall be placed directly on the shoulder. Any spilled material dragged on to the pavement surface shall be immediately removed, without damage to the pavement, and the area so affected thoroughly cleaned,

    - Median and Islands: Median and Islands shall be constructed in a manner similar to shoulder up to the road level. Thereafter the median and islands, if raised, shall be raised at least 300 mm by using kerb stones of approved material and dimensions and suitably finished and painted as directed by the Engineer. If not raised, the median and islands shall be differentiated from the shoulder/ pavement as the case may be, as directed by the Engineer. The confined area of the median and islands shall be filled with local earth or granular material or any other approved material and compacted by plate compactor/power rammer. The confined area alter filling with earth shall be turfed with grass or planted with shrubs and in case of granular fill it can be finished with tiles/slabs as directed by the Engineer.

    - Brick/stone block edging: The bricks/stones blocks shall be laid on edge, with the length parallel to the transverse direction of rolled into position by a light roller and made flush with the finished level of the pavement.

  - Surface Finish and Quality Control of works

The surface finish of construction shall conform to the requirements of Clause 902. Control on the quality of materials and works shall be exercised by the engineer in accordance with Section 900.

  - 407.6. Measurement for Payment

Shoulder (earthen /hard/paved), island and median construction shall be measured as finished work in position as below:

- For excavation in cu. m.

- For earthwork/granular fill in cu. m.

- For sub-base, base, surfacing courses in units as for respective items.

- For kerb in running metres.

- For turfing and tile/slab finish in sq. m.

- For Brick/stone block edging in se. m.

##### TRAFFIC SIGNS

  - General

    - The colour, configuration, size and location of all traffic signs for highways other than Expressways shall be in accordance with the Code of Practice for Road Signs, IRC: 67 or as shown on the drawings. For Expressways, the size of the signs, letters and their placement shall be as specified in the Contract

drawings and relevant Specifications. In the absence of any details or for any missing details, the signs shall be provided as directed by the Engineer.

    - The signs shall be either reflectorised or non-reflectorised as shown on the drawings or as directed by the Engineer. When they are of reflectorised type, they shall be of retro-reflectorized type and made of encapsulated lens type reflective sheeting vide Clause 801.3, fixed over aluminium sheeting as per these Specifications.

    - In general, cautionary and mandatory signs shall be fabricated through process of screen printing. In regard to informatory signs with inscriptions, either the message could be printed over the reflective sheeting, or cut letters of non-reflective black sheeting used for the purpose which must be bonded well on the base sheeting as directed by the Engineer.

  - Materials

The various materials and fabrication of the traffic signs shall conform to the following requirements:

    - Concrete: Concrete shall be of the grade shown on the Contract drawings or otherwise as directed by the Engineer.

    - Reinforcing steel: Reinforcing steel shall conform to the requirement of IS: 1786 unless otherwise shown on the drawing.

    - Bolts, nuts, washers: High strength bolts shall conform to IS: 1367 whereas precision bolts, nuts, etc., shall conform to IS: 1364.

    - Plates and supports: Plates and support sections for the sign posts shall conform to IS: 226 and IS: 2062 or any other relevant IS Specifications.

    - Aluminium: Aluminium sheets used for sign boards shall be of smooth, hard and corrosion resistant aluminium alloy conforming to IS: 736-Material designation 24345 or 1900.

    - Signs with a maximum side dimension not exceeding 600 mm shall not be less than 1.5 mm thick. All others shall be at least 2 mm thick. The thickness of the sheet shall be related to the size of the sign and its support and shall be such that it does not bend or deform under the prevailing wind and other loads.

    - In respect of sign sizes not covered by IRC67, the structural details (thickness, etc.) shall be as per the approved drawings.

  - Traffic Signs Having Retro -reflective Sheeting

    - General requirements: The retro-reflective sheeting used on the sign shall consist of the white or coloured sheeting having a smooth outer surface which has the property of retro-reflection over its entire surface. It shall be weather-resistant and show colour fastness. It shall be new and unused and shall show no evidence of cracking, scaling, pitting, blistering, edge lifting or curling and shall have negligible shrinkage or expansion. A certificate of having tested the sheeting for these properties in an unprotected

outdoor exposure facing the sun for two years and its having passed these tests shall be obtained from a reputed laboratory, by the manufacturer of the sheeting. The reflective sheeting shall be either of Engineering Grade material with enclosed lens or of High Intensity Grade with encapsulated lens. The type of the sheeting to be used would depend upon the type, functional hierarchy and importance of the road.

    - High intensity grade sheeting: This sheeting shall be of encapsulated lens type consisting of spherical glass lens, elements adhered to a synthetic resin and encapsulated by a flexible, transparent water-proof plastic having a smooth surface. The retro-reflective surface after cleaning with soap and water and in dry condition shall have the minimum co-efficient of retro-reflection (determined in accordance with ASTM Standard E: 810) as indicated in Table 800-1.

TABLE 800-1. ACCEPTABLE MINIMUM COEFFICIENT OK RETROREFLECTION FOR HIGH INTENSITY GRADE SHEETING (CANDELAS PER LUX PER SQUARE METRE)

When totally wet, the sheeting shall not show less than 90 per cent of the values of retro-reflectance indicated in Table 800-1. At the end of 7 years, the sheeting shall retain at least 75 per cent of its original retro-reflectance.

    - Engineering grade sheeting: This sheeting shall be of enclosed lens type consisting of microscopic lens elements embedded beneath the surface of a smooth, flexible, transparent, water-proof plastic, resulting in a non-exposed lens optical reflecting system. The retro reflective surface after cleaning with soap and water and in dry condition shall have the minimum coefficient of retro-reflection (determined in accordance with ASTM Standard: E 830) as indicated in Table 800-2.

TABLE 800-2. ACCEPTABLE MINIMUM COEFFICIENT OF RETROREFLECTION FOR ENGINEERING GRADE SHEETING (CANDELAS PER LUX PER SQUARE MFJTRE)

When totally wet, the sheeting shall not show less than 90 per cent of the values, of retro-reflection indicated in Table 800-2. At the end of 5 years, the sheeting shall retain at least 50 per cent of its original retro-reflectance.

    - Messages/borders: The messages (legends, letters, numerals etc.) and borders shall either be screen-printed or of cut-outs. Screen printing shall be processed and finished with materials and in a manner specified by the sheeting manufacturer. Cut-outs shall be of materials as specified by the sheeting manufacturer and shall be bonded with the sheeting in the manner specified by the manufacturer.

    - For screen-printed transparent coloured areas on white sheeting, the co-efficient of retro-reflection shall not be less than 50 per cent of the values of corresponding colour in Tables 800-1 and 800-2, as applicable.

    - . Cut-out messages and borders, wherever used, shall be made out of retro-reflective sheeting (as per Clause 801.3.2 or 801.3.3 as applicable), except those in black which shall be of non-reflective sheeting.

    - Colour: Unless otherwise specified, the general colour scheme shall be as stipulated in IS: 5 "Colour for Ready Mixed Paints", viz.

Blue	-	IS Colour	No. 166: French Blue Red	-	IS Colour	No. 537: Signal Red Green -	IS Colour	No. 284: India Green Orange.-	IS Colour	No. 591: Deep Orange

The Colours shall be durable and uniform in acceptable hue when viewed in day light or under normal headlights at night.

    - Adhesives: The sheeting shall either have a pressure sensitive adhesive of the aggressive-tack type requiring no heat, solvent or other preparation for adhesion to a smooth clean surface, or a lack free adhesive activated by heat, applied in a heat-vacuum applicator, in a manner recommended by the sheeting manufacturer. The adhesive shall be protected by an easily removable liner (removable by peeling without soaking in water or other solvent) and shall be suitable for the type of material of the base plate used for the sign. The adhesive shall form a durable bond to smooth, corrosion and weather resistant surface of the base plate such that it shall not be possible to remove the sheeting from the sign base in one piece by use of sharp instrument. In case of pressure-sensitive adhesive sheeting, the sheeting shall be applied in accordance with the manufacturer's Specifications. Sheeting with adhesives requiring use of solvents or other preparation for adhesive shall be applied strictly in accordance with the manufacturer's instructions.

    - Refurbishment: Where existing signs are specified for refurbishment, the sheeting shall have a semi-rigid aluminium backing pre-coated with aggressive-tack type pressure sensitive adhesive. The adhesive shall be suitable for the type of material used for the sign and should thoroughly bond with that material.

    - Fabrication:

      - Surface to be reflectorised shall be effectively prepared to receive the retro-reflective sheeting. The aluminium sheeting shall be de-greased either by acid or hot alkaline etching and all scale/dust removed to obtain a smooth plain surface before the application of retro reflective sheeting. If the surface is rough, approved surface primer may be used. After cleaning, metal shall not be handled, except by suitable device or clean canvas gloves, between all cleaning and preparation operation and application of reflective sheeting/primer. There shall be no opportunity for metal to come in contact with grease, oil or other contaminants prior to the application of retro-reflective sheeting.

      - Complete sheets of the material shall be used on the signs except where it is unavoidable; at splices; sheeting with pressure sensitive adhesives shall be overlapped not less than 5 mm. Sheeting with heat-activated adhesives may be spliced with an overlap not less than 5 mm or butted with a gap not exceeding 0.75 mm. Where screen printing with transparent colours is proposed, only butt jointing shall be used. The material shall cover the sign surface evenly and shall be free from twists, cracks and folds. Cut- outs to produce legends and borders shall be bonded with the sheeting in the manner specified by the manufacturer.

    - Warranty and durability: The Contractor shall obtain from the manufacturer a seven-year warranty for satisfactory field performance including stipulated retro-reflectance of the retro-reflective sheeting of high intensity grade and a five year warranty for the adhesive sheeting of engineering grade, and submit the same to the Engineer. In addition, a seven year and a five year warranty for satisfactory in- field performance of the finished sign with retro-reflective sheeting of high intensity grade and engineering grade respectively, inclusive-of the screen printed or cut out letters/ legends arid their bonding to the retro- reflective sheeting shall be obtained from the Contractor/supplier and passed onto the Engineer, The Contractor/supplier shall also furnish a certification that the signs and materials supplied against the assigned work meets all the stipulated requirements and carry the stipulated warranty.

Processed and applied in accordance with recommended procedures, the reflective material shall be weather resistant and, following cleaning, shall show no appreciable discolouration, cracking, blistering or dimensional change and shall not have less than 50 per cent of the specified minimum reflective intensity values (Tables 800-1 and 800-2) when subjected to accelerated weathering for 1000 hours, using type E or EH Weatherometer (AASHTO Designation M 268).

  - Installation

    - Sign posts, their foundations and sign mountings shall be so constructed as to hold these in a proper and permanent position against the normal storm wind toads or displacement by vandalism. Normally, signs with an area upto 0.9 sq. m. shall be mounted on a single post, and for greater area two or more supports shall be provided. Sign supports may be of mild steel, reinforced concrete or galvanised iron (G.I). Post- end(s) shall be firmly fixed to the ground by means of property designed foundation. The work of foundation shall conform to relevant Specifications as specified.

    - All components of signs and supports, other than the reflective portion and G.I. posts shall be thoroughly descaled, cleaned, primed and painted with two coats of epoxy paint. Any part of mild steel (M.S.) post below ground shall be painted with three coats of red lead paint.

    - The signs shall be fixed to the posts by welding in the case of steel posts and by bolts and washers of suitable size in the case of reinforced concrete or G.I. posts. After the nuts have been tightened, the tails of the bolts shall be furred over with a hammer to prevent removal.

  - Measurements for Payment

The measurement of standard cautionary, mandatory and information signs shall be in numbers of different types of signs supplied and fixed, while for direction and place identification signs, these shall be measured by area in square metres.

##### OVERHEAD SIGNS

a.   General

    - Overhead signs may be used in lieu of, or as an adjunct to, ground signs where the situation so warrants for proper information and guidance of the road user .The following conditions may be considered while deciding about the provision of overhead signs:

- Traffic volume at or near capacity

- Complex interchange design

- Three or more lines in each direction

- Restricted sight distance

- Closely spaced interchanges

- Multi-lane exits

- Large percentage of commercial vehicles

- High speed traffic

- Consistency of sign message location through a series of interchanges

- Insufficient space for ground mounted signs

- Background of street lighting

- Distances of important places enroute highways at suitable intervals,

    - From safety and aesthetic standpoints, overhead signs shall be mounted on overhead bridge structures wherever possible. Where these are required to be provided at some other locations, the support system should be properly designed based on sound engineering principles, to safely sustain the dead load, live load and wind load on the completed sign system. For this purpose, the overhead signs shall be designed to withstand a wind loading of 150 kg/m1 normal to the face of the sign and 30 kg/m1 transverse to the face of the sign. In addition to the dead load of the structure, walkway loading of 250 kg concentrated live load shall also be considered for the design of the overhead sign structure.

- Height

Overhead signs shall provide a vertical clearance of not less than 5.5 m over the entire width of the pavement and shoulders except where a lesser vertical clearance is used for the design of other structures. The vertical clearance to overhead sign structures or supports need not be greater than 300 mm in excess of the minimum design clearance of other structures.

- Lateral Clearance

    - The minimum clearance outside the usable roadway shoulder for expressway signs mounted at the road side or for overhead sign supports either to the right or left side of the roadway shall be 1.80 m. This minimum clearance of 1.80 m shall also apply outside of an uncountable kerb. Where practicable, a sign should not be less than 3 m from the edge of the nearest traffic lane. Large guide signs should be farther removed preferably 9 m or more from the nearest traffic lane, unless otherwise specified. Lesser clearances, but not generally less than 1.80m, may be used on connecting roadways or ramps at inter- changes.

    - Where a median is 3.6 m or less in width, consideration should be given to spanning over both roadways without a central support. Where overhead sign supports cannot be placed at a safe distance away from the line of traffic or in an otherwise protected site, they should either be so designed as to minimise the impact forces or protect motorists adequately by a physical barrier or guard rail of suitable design.

- Number of Signs at an Overhead Installation

In no case should there be more than three signs displayed at any one location including regulatory or warning signs, either on the on the overhead structure or on its support.

- . Materials for Overhead Sign and Support Structure

    - . Aluminium alloy or galvanized steel to be used as truss design supports shall conform to relevant IS. These shall be of sections and type as per structural design requirements as shown on the plans.

    - After steel trusses have been fabricated and all required holes punched or drilled on both the horizontal truss unites and the vertical and support units, they shall be galvanized in accordance with IS Specifications.

    - Where aluminium sheets are used for road signs, they shall be of smooth, hard and corrosion resistant aluminium alloy conforming to IS: 736 Material Designation 24345 or 1900. The thickNess of sheet is taken as 1.5mm.

    - High Strength bolts shall conform to IS: 1367 whereas precision bolts, nuts etc. shall conform to IS: 1364.

    - Plates and support sections for sign posts shall conform to IS: 266 and IS: 2062.

    - The overhead signs shall be reflectorised with high intensity retro-reflective sheeting preferably of encapsulated lens type.

- Size, Locations, etc. of Signs

    - The size of the signs, letters and their placements shall be as specified in the Contract Drawings and Specifications.

    - . In the absence of details or for any missing details in the Contract documents, the signs shall be provided as directed by the Engineer.

- Installation

    - The supporting structure and signs shall be fabricated and erected as per details given in the plans.

    - Sign posts, their foundations and sign mountings shall be as constructed as to hold signs in a proper and permanent position to adequately resist swaying in the wind or displacement by vandalism.

    - The work of construction of foundation for sign supports including excavation and backfill, forms, steel reinforcement, concrete and its placement shall conform to the relevant Specifications given in these Specifications.

    - The structures shall be erected with the specified camber and in such a manner as to prevent excessive stresses, injury and defacement.

    - Brackets shall be provided for mounting signs of the type to be supported by the structure. For better visibility, they shall be adjustable to permit mounting the sign faces at any angle between a truly vertical position and three degree from vertical. This angle shall be obtained by rotating the front lower edge of the sign forward. All brackets shall be of a length equal to the heights of the signs being supported.

    - Before erecting support structures, the bottom of each base plate shall he protected with an approved material which will adequately prevent any harmful reaction between the plate and the concrete.

    - The end supports shall be plumbed by the use of levelling nuts and the space between the foundation and base plate shall he completely filled with an anti-shrink grout.

    - Anchor bolts for sign supports shall be set to proper locations and elevation with templates arid carefully checked after construction of the sign foundation arid before the concrete has set.

    - All nuts on aluminium trusses, except those used on the flanges, shall be tightened only until they are snug. This includes the nuts on the anchor bolts. A thread lubricant shall be used with each aluminium nut.

    - All nuts o galvanized steel trusses, with the exception of high strength bolt connections, shall be tightened only to a snug condition.

    - Field welding shall not be permitted.

    - After installation of signs is complete, the sign shall be inspected by the Engineer. If specular reflection is apparent on any sign, its positioning shall be adjusted by the Contractor to eliminate or minimize this condition.

- Measurements for Payment

    - Aluminium or steel overhead sign structure will be measured for payment by the specific unit (each) complete in place or for each component of the overhead sign structure as indicated in the Bill of Quantities and the detailed drawing(s).

    - Flat sheet aluminium signs with retro-reflective sheeting thereon shall be measured for payment by the square metre for each thickNess, complete in place.

##### ROAD MARKINGS

  - General

The colour, width and layout of road markings shall be in accordance with the Code of Practice for Road Markings with paints, IRC : 35, and as specified in the drawings or as directed by the Engineer.

  - Materials

Road markings shall be of ordinary road marking paint, hot applied thermoplastic compound, or reflectorised paint as specified in the item and the material shall meet the requirements as specified below.

  - Ordinary Road Marking Paint

    - Ordinary paint used for road marking shall conform to Grade I as per IS: 164.

    - The road marking shall preferably be laid with appropriate road marking machinery.

    - Laying thickNess of road marking paint shall be as specified by the Engineer.

  - Hot Applied Thermoplastic Road Marking

    - General:

- The work under this section consists of marking traffic stripes using a thermoplastic compound meeting the requirements specified herein.

- The thermoplastic compound shall be screeded / extruded on to the pavement surface in a molten state by suitable machine capable of controlled preparation and laying with surface application of glass beads at a specific rate. Upon cooling to ambient pavement temperature, it shall produce an adherent pavement marking of specified thickNess and width and capable of resisting deformation by traffic,

- The colour of the compound shall be white or yellow (IS colour No. 556) as specified in the drawings or as directed by the Engineer.

- Where the compound is to be applied to cement concrete pavement, a sealing primer as recommended by the manufacturer, shall be applied to the pavement in advance of placing of the stripes to ensure proper bonding of the compound. On new concrete surface any laitance and/or curing compound shall be removed before the markings are applied.

    - Thermoplastic Material

      - General: The thermoplastic material shall be homo generously composed of aggregate, pigment, resins and glass reflectorizing beads.

      - Requirements:

- Composition: The pigment, beads, and aggregate shall be uniformly dispersed in the resin. The material shall be free from all skins, dirt and foreign objects and shall comply with requirements indicated in Table 800-3.

TABLE 800-3. PROPORTIONS OF CONSTITUENTS OF MARKING MATERIAL (Percentage by weight)

Note: Amount of yellow pigment, calcium carbonate and inert fillers shall be at the option of the manufacturer, provided all other requirements of this Specification are met

- Properties: The properties of thermoplastic material, when tested in accordance with ASTM D36/BS-3 262-(Part 1), shall be as below:

  - Luminance:

White: Daylight luminance at 45 dcgrees-65 per cent min. as per AASHTO M 249

Yellow: Daylight luminance at 45 degrees-45 per cent min. as per AASHTO M 249

  - Drying time: When applied at a temperature specified by the manufacturer and to the required thickNess, the material shall set LO bear traffic in not more than 15 minutes.

  - Skid resistance: not less than 45 as per BS 6044.

  - Cracking resistance at low temperature: The material shall show i-o cracks on application to concrete blocks.

  - Softening point: 102.5 ± 9.5° C as per ASTM D 36.

  - How resistance: Not more than 25 per cent as per AASHTO M 249.

  - Yellowness index (for white thermoplastic paint): not more than 0.12 as per AASHTO M 249

- Storage life: The material shall meet the requirements of these Specifications for a period of one year. The thermoplastic material must also melt uniformly with no evidence of skins or unmelted panicles for the one year storage period. Any material not meeting the above requirements shall be replaced by the manufacturer/ supplier/Contractor.

- Reflectorisation: Shall be achieved by incorporation of beads, the grading and other properties of the beads shall be as specified in Clause 803.4.3.

- Marking: Each container of the thermoplastic material shall be clearly and indelibly marked with the following information:

  - The name, trade mark or other means of identification of manufacturer

  - Batch number

  - Date of manufacture

  - Colour (white or yellow)

  - Maximum application temperature and maximum safe heating temperature.

- Sampling and testing: The thermoplastic material shall be sampled and tested in accordance with the appropriate ASTM/BS method. The Contractor shall furnish to the Employer a copy of certified test reports from the manufacturers of the thermoplastic material showing results of all tests specified herein and shall certify that the material meets all requirements of this Specification.

    - Reflectorising glass beads

      - General: This Specification covers two types of glass beads 10 be used for the production of reflectorised pavement markings.

Type 1 beads are those which are a constituent of the basic thermoplastic compound vide Table 800-3 and Type 2 beads are those which are to be sprayed on the surface vide Clause 803.6,3.

      - The glass beads shall be transparent, colourless and free from milkiness, dark particles and excessive air inclusions. These shall conform to the requirements spelt out in Clause 803.4.3.3,

      - . Specific requirements

- Gradation: The glass beads shall meet the gradation requirements for the two types as given in

Table 800-4.

GRADATION REQUIREMENTS FOR GLASS BEADS

- Roundness: The glass beads shall have a minimum of 70 per cent true spheres.

- Refractive index: The glass beads shall have a minimum refractive index of 1.50.

- Free flowing properties: The glass beads shall be free of hard lumps and clusters and shall dispense readily under any conditions suitable for paint striping. They shall pass the free flow-test.

      - Test methods: The specific requirements shall be tested with the following methods:

- Free-flow test- Spread 100 grams of beads evenly in a 100 mm diameter glass dish. Place the dish in a 250 mm inside diameter desiccator which is filled within 25 mm of the lop of a desiccator plate with sulphuric acid water solution (specific gravity 1.10). Cover the desiccator and let it stand for 4 hours at 20 lo 29 degree C. Remove sample from desiccator, transfer beads to a pan aid inspect for lumps or clusters. Then pour beads into a clean, dry glass funnel having a 100 mm stern and 6 mm orifice. If necessary, initiate flow by lightly tapping the funnel. The glass spheres shall be essentially free of lumps and clusters and shall flow freely through the funnel.

- The requirements of gradation, roundness and refractive index of glass beads and the amount of glass beads in the compound shall be tested as per B3 6088 and BS 3262 (Part I).

- The Contractor shall furnish to the Employer a copy of certified test reports from the manufacturer of glass beads obtained from a reputed laboratory showing results of all tests specified herein mid shall certify

that the material meets all requirement of this Specification. However, if so required, these tests may be carried out as directed by the Engineer.

    - Application properties of thermoplastic material

33.4.4.1  The thermoplastic material shall readily get screeded / extruded at temperatures specified by the manufacturers for respective method of application to produce a tine of specified thickness which shall be continuous and uniform in shape having clear and sharp edges. 803.4.4.2. The material upon heating to application temperatures shall not exude fumes, which are toxic, obnoxious or injurious to persons or property.

    - Preparation:

- The material shall be melted in accordance with the manufacturer's instructions in a healer filled with a mechanical stirrer to give a smooth consistency to the thermoplastic material lo avoid local overheating. The temperature of the mass shall be within the range specified by the manufacturer, and shall on no account be allowed to exceed the maximum temperature stated by the manufacturer. The molten material should be used as expeditiously as possible and for thermoplastic material which has natural binders or is otherwise sensitive to prolonged heating, the material shall not be maintained in a molten condition for more than 4 hours.

- After transfer lo the laying equipment, the material shall be maintained within the temperature range specified by the manufacturer for achieving the desired consistency for laying.

    - Properties of finished road marking:

- The stripe shall not be slippery when wet.

- The marking shall not lift from the pavement in freezing weather.

- After application and proper drying, the stripe shall show no appreciable deformation or discolouration under traffic and under road temperatures upto 60°C.

- The marking shall not deteriorate by contact with sodium chloride, calcium chloride or oil drippings from traffic.

- The stripe or marking shall maintain its original dimensions and position. Cold ductility of the material shall be such as to permit normal movement with the road surface without chopping or cracking.

- The colour of yellow marking shall conform 10 IS Colour No. 356 as given in IS: 164.

  - Reflectorised Paint

Reflectorised paint, if used, shall conform to the Specification by the manufacturers and approved by the Engineer. Reflectorising glass beads for reflectorising paints where used shall conform to the requirement of Clause 803.4,3.

  - Application

    - Marking shall be done by machine. For locations where painting cannot be done by machine, approved manual methods shall be used with prior approval of the Engineer. The Contractor shall maintain control over traffic while painting operations are in progress so as to cause minimum inconvenience to traffic compatible with protecting the workmen.

    - The thermoplastic material shall be applied hot either by screeding or extrusion process. After transfer to the laying apparatus, the material shall be laid at a temperature within the range specified by the manufacturer for the particular method of laying being used. The paint shall be applied using a screed or extrusion machine.

    - The pavement temperature shall not be less than 10°C during application. All surfaces to be marked shall be thoroughly cleaned of all dust, dirt, grease, oil and all other foreign matter before application of the paint.

The material, when formed into traffic stripes, must be readily renewable by placing an overlay of new material directly over an old line of compatible material. Such new material shall so bond itself to the old line that no splitting or separation takes place.

Thermoplastic paint shall be applied in intermittent or continuous lines of uniform thickNess of at least 2.5 mm unless specified otherwise. Where arrows or letters are to be provided, thermoplastic compound may be hand-sprayed. In addition to the beads included in the material, a further quantity of glass beads of Type 2, conforming to the above noted Specification shall be sprayed uniformly into a mono-layer on to the hot paint line in quick succession of the paint spraying operation. The glass beads shall be applied at the rate of 250 grams per square metre area.

    - . The minimum thickNess specified is exclusive of surface applied glass beads. The method of thickNess measurement shall be in accordance with Appendices B and C of BS - 3262 (Part 3).

    - . The finished lines shall be free from ruggedness on sides and ends and be parallel to the general alignment of the carriageway. The upper surface of the lines shall be level, uniform and free from streaks

  - Measurements for Payment

    - The painted markings shall be measured in sq. metres of actual area marked (excluding the gaps, if any).

    - In respect of markings like directional arrows and lettering, etc., the measurement shall be by numbers.

##### HECTOMETRE/KILOMETRE STONES

  - General

The work covers the supply, painting, lettering and fixing of distance measurement stones and shall include:

- Hectometre stones

- Kilometre stones

- 5th Kilometre stones

The dimensions of the stones and the size, colour, arrangement of letters and script shall be as per IRC: 26 "Type Designs for 200 Metre Stones" and IRC: 8 "Type Designs for Highway Kilometre Stones",

The hectometre/kilometre stones may be made of local stones, concrete or any other material available locally and approved by the Engineer. The stones shall be bedded into the ground with adequate foundations as indicated in the drawings or in the relevant I.R.C. Specifications or as directed by the Engineer. The orientation and location of the stones shall be as indicated in the drawings or in the relevant

I.R.C. Specifications or as directed by the Engineer.

Measurements for Payment

The measurement will be in numbers of 200 metre, kilometre and 5th kilometre stones fixed at site.

##### BOUNDARY STONES

  - General

The work comprises of supplying and fixing boundary stones as per designs and Specifications given in IRC: 25 "Type Designs for Boundary Stones" and at locations indicated in the drawings or-as directed by the Engineer.

  - Measurements for Payment

The measurement shall be made in numbers of boundary stones 1ieu at site.

##### FENCING

  - General

The work comprises of fixing Mild Steel (M.S.) posts and providing barbed wire fencing including necessary stays and entry gates as shown in the drawing (s) and as directed by the Engineer.

The M.S. posts shall conform to IS: 226 and shall be of angle iron of size indicated in the drawings. The angle iron shall be embedded in concrete to a sufficient depth below ground as indicated in the drawings. The steel shall be fabricated and painted to conform to Section 1900 of these Specifications,

The barbed wire shall be of galvanised iron and shall conform to 15:278.

Entry gate(s) shall be made of M.S. rods or other metal as per the design shown in the drawing(s).

  - Measurements for Payment

The measurement shall be in running metre of fencing including the entry gates.

##### TUBULAR STEEL RAILING

  - General

The work shall consist of supplying, fixing and erecting tubular steel railings as shown on the drawings and as directed by the Engineer.

The railings shall be of tubular steel in conformance to IS: 1239. The fabrication and painting except for the final coat shall be completed before despatch to the site. Prior to the painting, all surfaces shall be grit blasted to the satisfaction of the Engineer and pickled. The priming coat of paint shall be applied as soon as the steel has dried,

The posts shall be vertical and of the type as shown in the drawing with a tolerance not exceeding 6 mm in a length of 3 m. The railing shall be erected true to line and grade.

  - Measurements for Payment

The railing shall be measured in linear metre from end to end along the face of the railing, including end and intermediate posts, with no deductions for gaps as shown on the drawings.

##### CONCRETE CRASH BARRIER

  - General

This work shall consist of construction, provision and installation of concrete crash barrier at the edges of the road and median at locations and of dimensions as shown on the drawings or as directed by the Engineer.

Concrete barrier shall generally be located on approaches to bridge structures, at locations where the embankment height is more than 3 metres and at horizontal curves,

  - Materials

All materials shall conform to Section 1000-Materials for Structures as applicable, and relevant Clauses in Section 1600 shall govern the steel reinforcement. The concrete barriers shall be constructed either by the "cast- in-place with fixed forms" method or the "extrusion or slip form" method or a combination thereof at the Contractor's option with the approval of the Engineer. Where "extrusion or slip form" method is adopted, full details of the method and literature shall be furnished.

Concrete barriers shall be constructed with M'20 grade concrete and with High Yield Strength deformed reinforcement conforming to IRC: 21.

An expansion joint with pre- moulded asphalt filler board shall be provided at the junction of crash barrier on structure and crash barrier on the fill. The crash barrier on the fill shall be constructed in pieces of length not exceeding 20 m, with pre-moulded asphalt filler board joints.

  - Construction Operations

The location of crash barrier shall be strictly adhered to as shown on the drawing and as directed by the Engineer. Concrete crash barriers shall present a smooth, uniform appearance in their final position, conforming to the horizontal and vertical lines shown on the plans or as ordered by the Engineer and shall be free of lumps, sags or other irregularities. The top and exposed faces of the barriers shall conform to the specified tolerances, as defined in Clause 809.4, when tested with 3 m straight edge, laid on the surface.

. When concrete barriers are to be constructed on recently completed bridges, the height of the barriers shall be adjusted to compensate for die camber and dead load deflection of the superstructure. The amount of adjustment shall be determined by the Engineer and shall be ordered before the concrete is placed. Such barriers shall be placed after form work has been released and as long after the superstructure construction as possible without hampering the progress of the work.

Backfilling to the concrete barriers shall be compacted in layers to the compaction of the surrounding earthwork.

Tolerance The overall horizontal alignment of rails shall not depart from the road alignment by more than ± 30 mm, nor deviate in any two successive lengths from straight by more than 6 mm and the faces shall not vary more than 12 mm from the edge of a 3 m straight edge. Barriers shall be at the specified height as shown in die plans above the edge of the nearest adjacent carriageway or shoulder, within a tolerance of ± 30 mm.

  - Measurements for Payment

All barriers will be measured by linear metres of completed and accepted length inplace, corresponding end to end along the face of concrete barriers including approach and departure ends.

##### METAL BEAM CRASH BARRIER

  - General

This work shall consist of furnishing and erection of metal beam crash barrier of dimensions and at locations as shown on the drawing (s) or as directed by the Engineer,

Metal beam crash barrier shall generally be located on approaches to bridge structures, at locations where the embankment height is more than 3 metres and at horizontal curves.

  - Materials

Metal beam rail shall be corrugated sheet steel beams of the class, type, section and thickNess indicated on the plans. Railing posts shall be made of steel of the section, weight and length as shown on the plans. All complete steel rail elements, terminal sections, posts, bolts, nuts, hardware and other steel fittings shall be galvanised. All elements of the railing shall be free from abrasions, rough or sharp edges and shall not be kinked, twisted or bent.

Steel beam elements and terminal sections shall be galvanised (zinc coated, 0.55 kg per square metre, minimum single spot) unless otherwise specified. The galvanising on all other steel parts shall conform to the relevant IS Specifications, All fittings (bolts, nuts, washers) shall conform to the IS: 1367 and IS: 1364. All galvanizing shall be done after fabrication.

Concrete for bedding and anchor assembly shall conform to Section 1700 of these Specifications.

  - Construction Operations

The line and grade of railing shall be true to that shown on the plans. The railing shall be carefully adjusted prior to fixing in place, to ensure proper matching at abutting joints arid correct alignment and camber throughout their length. Holes for field connections shall be drilled with the railing in place in the structure at proper grade and alignment.

Unless otherwise specified on the drawing, railing steel posts shall be given one shop coat of paint (primer) and three coats of paint on structural steel after erection, if the sections are not galvanised. Any part of assembly below ground shall be painted with three coats of red lead paint.

Splices and end connections shall be of the type and designs specified or shown on the plans and shall be of such strength as to develop full design strength of the rail elements.

  - Installation of Posts

Holes shall be dug or drilled to the depth indicated on the plans or posts may be driven by approved methods and equipment, provided these are erected in proper position and are free from distortion and burring or any other damage.

All post holes that are dug or drilled shall be of such sizes will permit proper setting of the posts and allow sufficient room or backfilling and lapping.

Holes shall be backfilled with selected earth or stable materials in layers not exceeding 100 mm thickNess and each layer shall be thoroughly tamped and rammed. When backfilling and tamp are completed, the posts or anchors shall be held securely in place.

Post holes that are drilled in rock and holes for anchor posts shall be back filled with concrete.

Posts for metal beam guardrails on bridges shall be led to the structure as detailed on the plans. The anchor bolts shall be set to proper location and elevation with templates and carefully checked.

  - 39.4.6. Erection

All guardrail anchors shall be set and attachments made rand placed as indicated on the plans or as directed by the Engineer.

All bolts or clips used for fastening the guardrail or fittings to the posts shall be drawn up tightly. Each bolt shall have sufficient length to extend atleast 6 mm through and beyond the full nut, except which such extensions might interfere with or endanger traffic in which case the bolts shall be cut off flush with the nut. All railings shall be erected, drawn and adjusted so that the longitudinal tension will be uniform throughout the entire length of the rail.

  - Tolerance

The posts shall be vertical with a tolerance not exceeding 6 mm in a length of 3 metre. The railing barrier shall be erected true to line and grade.

  - Measurements for Payment

Metal beam railing barriers will be measured by linear metre of completed length as per plans and accepted in place. Terminals/ anchors of various types shall be paid for by numbers.

No measurement for payment shall be made for projections or anchors beyond the end posts except as noted above. Furnishing and placing anchor bolts and/or devices for guard rail posts on bridges shall be considered incidental to the construction and the costs thereof shall be included in the price for other items of construction.

No measurement for payment will be made for excavation or backfilling performed in connection with this construction.

##### ROAD TRAFFIC SIGNALS

  - General

The traffic signal, its configuration, size and location shall be in accordance with IRC: 93 and IS: 7537 and as shown in the drawings or as directed by the Engineer. Prior to installation of signals, the Contractor shall submit to the Engineer, for approval, detailed proposals showing the signal type, sizes, paint and structural details of the signal posts including control system.

The traffic signals shall have a complete electronic mechanism for controlling the operation of traffic with an auxiliary manual controller. The time plan of signals shall be as per drawing and shall be modified as directed by the Engineer.

  - Materials

The various materials and fabrication thereof shall conform to the following:

Signal foundation: The signal foundations shall be constructed as per Specifications given in Clause 13 of IRC: 93 or as shown in the drawings.

Constructional requirements: The constructional requirements for post, signal head assembly, signal head, optical system, lamp and holder, visor, post, supports for overhead mounted signals, equipment housing, locks, inter-connecting cables, earthing, mains termination, controller electrical components, etc., shall conform to IS: 7537 unless otherwise stated in IRC: 93. The post shall be painted and protected as per Clause 3.7 of IS: 7537.

Optical requirements: The shape of all signal lenses shall be circular and shall be of specified colour and size and as shown in the drawing. Quality of lenses, arrangement of lenses, illuminations, visibility and shielding of signals shall be as per relevant Clauses of IRC: 93 and 15:7537.

  - Tests

Tests shall be carried out on all components of traffic signal including tests on complete system for its performance as per relevant Clauses of IRC: 93 and IS: 7537.

  - Maintenance of Traffic Signals

It shall be the responsibility of the Contractor to provide for maintenance of the signal section system throughout the warranty period for at least five (5) years after installation and as per Clause 18 of IRC: 93.

  - Measurements for Payment

The measurement for traffic signalisation system shall be by unit for complete work as specified and as per drawing for complete road junction.

ADDITIONAL CONDITIONS FOR CIVIL WORKS.

1.0	GENERAL:

The intent of specification covers the following :

Design, engineering, and construction of all civil works relating to entire job including, delivery chamber etc. All civil works shall also satisfy the general technical requirements specified in other sections of this specification and as detailed below. They shall be designed to the required service conditions/loads as specified elsewhere in this Specification or implied as per National/International Standards.

All civil works shall carried out as per applicable Indian Laws, Standards and codes All material shall be of best quality confirming to relevant Indian Standard and Codes, The Contractor shall furnish all design, (Unless otherwise specified) drawings labour, tools, equipment, materials, temporary works, constructional plant and machinery fuel supply transpiration and all other incidental items not shown or specified but as may be required for complete performance of the works in accordance with approved drawings, specifications and direction of department.

The work shall be carried out according to the design/drawings to be developed by the contractor and approved by the Department or supplied to the contractor by the department. For all buildings, structures. Foundations etc, necessary layout details shall be developed by the contractor keeping in view of the functional requirement of the equipment’s and facilities and providing enough space and access for operation use and maintenance based on the input provided by the department Certain minimum requirements are indicated in this specification for guidance purpose only. However the Bidder shall quote according to the complete requirement.

  - VOID:

  - SITE PREPARATION:

The layout and levels of all structure etc. Shall be made by the contractor at his own cost from the general grid of the plot and benchmarks given by the Engineer-in-Charge. The Contractor shall give all help in instruments, materials and personnel to the engineer-in-charge for checking the detailed layout and shall be solely responsible for the correctness of the layout and levels.

    - SCOPE:

This clause covers the design and execution of the work for site preparation, such as clearing of the site, supply and compaction of fill material, excavation and compaction of back fill for foundation, road construction. Drainage, trenches and final topping by gravel (broken hard stone).

    - GENERAL:

- The contractor shall develop the site area to meet the requirement of the intended purpose, The site preparation shall conform to the requirements of relevant sections of this specification or as per stipulations of standard specification.

- If fill material is required the fill material shall be suitable for the above requirement, The fill shall be of such a material and the site so designed as to prevent the erosion by wind and water of material from its final compacted position of the in-situ position undisturbed soil.

- Material unsuitable for founding of foundation shall be removed and replaced by suitable fill material and to be approved by KNNL.

- Backfill material around foundations or other works shall be suitable for the purpose for which it is used and compacted to the density described under Compaction.

    - EXCAVATION AND BACKFILL:

- The scope includes soil investigation to be conducted by the bidder

- Excavation and back fill for foundation shall be in accordance with the relevant code.

- Whenever water table in met during the excavation, it shall be denatured and water table shall be maintained below the bottom of the excavation level during excavation concerting and back filling.

- When embankments are to be constructed on slopes of 15 or greater benches or steps with horizontal and vertical faces shall be cut in the original slope prior to placement of embankment material. Vertical faces shall measure not more than I am in height.

- Embankments adjacent to abutments culverts retaining walls and similar structures shall be constructed by compacting the material in successive uniform horizontal layers not exceeding 15 cm in thickness (of loose material before compaction) Each layer shall be compacted as required by means of mechanical tempest approved by the Owner. Builders Rocks later than 10 cm Shall not be placed in embankment adjacent to structures.

- Earth embankments of roadways and site areas adjacent to buildings shall be place in successive uniform horizontal layers not exceeding 20 cm in thickness in loose stage measurement and compacted to the full width specified. The upper surface of the embankment shall be shaped so as to provide complete drainage of surface water at all times.

    - COMPACTION:

- The method and equipment used to compact the fill material shall be suitable to achieve the density that will give the allowable soil bearing pressure required for the foundations, roads etc, in each layer of fill material. Each layer of earth embankment when compacted shall be as close to optimum moisture content as practicable. Embankment material which does not contain sufficient moisture to obtain proper compaction shall be wetted. If the material contains an excess of moisture. Then it shall be allowed to dry before rolling. The rolling shall begin at the edges overlapping half the width of the roller each time and progress to the center of the road or towards the building as applicable. Rolling will also be required on rock fills No compaction shall be carried out in rainy weather.

- At all times unfinished construction shall have adequate drainage. Upon completion of the road’s

surface course. Adjacent shoulders shall be given a final shaping true alignment and grade.

- The density to which fill materials shall be compacted shall be as per relevant IS and as per direction of Engineer-in-Charge, All compacted send filling shall be confined as far as practicable. Back filled earth shall be compacted to minimum 95 of the Standard proctor’s density at filling shall be compacted to minimum 95 of the Standard proctor’s density at OMC.

- 3. 5  REQUIREMENT FOR FILL MATERIAL UNDER FOUNDATION:

The thickness of fill material under the foundations shall be such that the maximum pressure from the footing. Transferred through the fill material and distributed onto the original undisturbed soil will not exceed the allowable soil bearing pressure of the original undisturbed. For expansive soils the fill materials and other protections etc. to be used under the foundation is to be got approved by the KNNL.

  - ANTIWEED TREATMENT & SITE SURFACING:

    - SCOPE OF WORK:

The contractor shall furnish all labor, equipment and materials required for complete performance of the work in accordance with the drawing specification and direction of the Engineer in Charge.

    - GENERAL REQUIREMENT:

The material required for site surfacing/gravel filling shall be free from all types of organic materials and shall be of standard approved quality and as directed by the Engineer-in- Charge.

      - The contractor shall furnish and install the site surfacing to the lines and grades as shown in the drawing and in accordance with the requirements and direction of the Engineer-in-Charge. The soil of the entire switchyard area shall be subjected to sterilization/ anti-weed treatment before

placing the site sum acing/gravel fill material strictly as per instruction/requirement of the manufacture of the chemical required for soil sterilization/anti-weed treatment. After all the structures and equipment have been corrected and accepted, and soil sterilization as specified is complete the site shall be maintained to the suitable water sprinkling to form a smooth and compact surface condition which shall be matching with finished ground level of the switchyard area.

      - After the soil sterilization material is applied and surface prepared compacted to the required slope/grade a base layer of uncrushed/crushed broken stone/pebbles (grouch of 20mm nominal size shall be spread and rolled/compacted by using ½ ton toiler (30m width and 24 dia) with 4 to 6 passes and water sprinkling to form a minimum 50mm layer on the designed finished formation level of the entire switchyard area.

      - A final surface course minimum 50mm. Uniform layer of encrusted crushed broken stone/pebble (gravel) of 20mm. nominal size as specified shall be spread over the base layer/course. This final surface course shall be applied in all areas exclusive of roadways and shall extend beyond the fenced area as medicated in the drawing This surface course shall ten be compacted by light roller using ½ ton steel roller (width 30 x dia 24) and 4 to 5 passes or any other means with water sprinkling as directed by the Owner Engineer-in-Charge. Water shall be sprinkled in such a manner that bulking does not take place The 20mm nominal size (for both layers) shall pass 100 present through I.S. Sieve designation 10mm and nothing through 16.0mm I.S. Sieve.

      - In areas that are considered by the Engineer-in-Charge to be too congested with foundation and structures for proper tolling of the base course material by normal rolling equipment’s the material shall be compacted by hand if necessary. Due care shall be exercised so as not to damage any foundation structure or equipment during rolling compaction.

      - CHEMICAL TO BE USED FOR SOIL STERILIZATION ANH-WEED TREATMENT:

The details of quantities and method of application of chemicals used for soil sterilization/anti-weed treatment shall be as per manufacturers recommendations Bidders are required to submit the details of chemicals proposed to be used and recommendation of manufacturer with required guarantee along with their bids for necessary approval of KNNL. Approval of KNNL by no means shall relieve the Contractor from their contra actual obligations as stipulated in General and Special conditions of contract

  - SITE DRAINAGE:

- Adequate site drainage system shall be provided by the Contractor. The Contractor shall obtain rainfall data and design the storm water drainage system, (culverts. Ditches, drains etc..) to

accommodate the most intense rainfall that is likely to occur over the catchments area in one hour period on an average of one per ten years. The surface of the site shall be sloped to prevent the pounding of water.

- The maximum velocity for pipe drains and open drains shall be limited to 2.4 m/sec and 1.8m/sec respectively. However, minimum non-silting velocity of 0.6m/sec shall be ensured. Longitudinal bed slope not milder than 1 in 1000 shall be provided.

- For design of RCC pipes for drains and culverts. IS:456 and IS: 783 shall be followed.

- The Contractor shall ensure that water drains are away from the site area and shall prevent damage to adjacent property by this water. Adequate protection shall be given to site surface, roads, ditches, culverts, etc, to prevent corrosion of material by water.

- The drainage system shall be adequate without the use of cable/pipe trenches.

- For pipe drains, concrete pipe of class NP2 shall be used. However, for road crossings etc, higher strength pipe of class NP3 shall be provided. For rail Crossings, pipes conforming to railway loading standards or at least NP4 class shall be provided Manholes shall be provided at every 30m interval at connection pints and at every change of alignment.

- Open surface drains shall be provided with bricks of class designation 75 in cement mortar 1:4 including 100mm thick bed concrete of grade 1:4:8 and 12mm thick cement plaster 1:4 with a floating coat of neat cement inside the drains. Its top and exposed sides as per design and drawing to be got approved by the KNNL, For expansive soils, the guide lines of IS: 9451 shall be followed.

- In general. Effluent drainage shall be through buried concrete pipes and all storm water drainage shall be designed to drain the road surface as well as the entire free and covered areas etc.

- Pipe drains shall be connected through manholes at an interval of max 30m effluents shall be suitably treated by the Contractor to meet all the prevalent statutory requirements and local pollution control norms and beaded effluents shall be conveyed to the storm water drainage system at a suitable location for its final disposal.

- Invert of the drainage system shall be decided in such a way that the water can easily be discharged above the High Flood Level (1111) outside substation boundary at suitable location and approved by KNNL pumps for drainage of water (if required) shall be provided by Contractor.

11. All internal site drainage system, including the final connection/disposal to KNNL acceptance points shall be part of Suppliers scope including all required civil work, mechanical & electrical systems. The Contractor shall connect his drain(s) at one more points,

- The precast manholes shall be preferred against cast-in-situ type. The drainage scheme may either employ open drain system or underground pipe system or a combination of both. A manhole

shall be provided at every turn Corner in case of underground type in addition to the normal requirements.

- Suitable pumping arrangement shall be provided by the contractor to pump out the water from sump to the open channel automatic float valve type pump shall be provided and installed by Contractor.

- The Contractor shall locate the out fall pint outside the substation vicinity and the substation storm drainage must be connected to this point.

- The drainage scheme and associated drawings shall be got approved.

  - ROADS AND CULVERTS:

- Roads provided for access to equipment and building are in the scope of bidder. Layout of the roads shall be based on General detail & Arrangement Drawing. Parking areas, shall be provided for site personnel and visitors at convenient locations. Adequate turning space for vehicles shall be provided and bend radii shall be set accordingly. Road to the. Transformer/Reactors shall be as short and straight as possible.

- All roads be constructed so as to permit transportation of all heavy equipment. The single lane road shall have minimum. 5.5 m black topping with 1.5m wide shoulder on either side of the road.

- Finished top ( crest) of roads shall be 600mm (min) above the surrounding grade level (Formation level)

- Road construction shall be as per IRC standards.

- Adequate provision shall be made for road drainage.

- All the culverts and its allied structure (requited for road/rail. Drain trench crossings etc.) shall be designed for class AA loading and checked for Class A loading as per IRC standard.

- All roads shall be designed for class ‘E’ of traffic as per IRC-37-1984 Guide-lines’’ for the design of

flexible pavements.

  - TRANSFORMER FOUNDATION,RAIL TRACK/ROAD CUM RAIL TRACK.

The contractor shall provide a permanent transfer track system integrated with the transformer foundation to enable installation and the replacement of any failed unit by the spare unit located at the site. The transfer track system shall be suitable to permit the movement of any failed unit fully assembled (including OLTC bushings) with integral radiators and oil, without the deenergization of any other equipments to the station. This system shall enable the removal of any failed unit from its foundation to a repair area and the installation of the spare unit. This system, preferably shall not interfere with the normal internal road and trench system. If trench/drain crossings are required then suitable RCC culverts shall be provided in accordance with IRC code/relevant IS.

Rail tracks shall be or RCC minimum M20 grade. The space between the tracks shall be suitably filled with local sand and 75mm thick PCC of grade 1:3:6 placed over sand filling. The top of PCC shall be up to the formation level. In case of road cum rail track 75mm thick PCC of grade 1:2:4 shall be placed up to the road level. Suitable drainage system between the tracks shall be provided.

The rails shall be first quality 52 kg/m medium, magnese steel as per Indian Railway specification T-12-64 and its subsequent revision, joined together by fish plates as per per Indian Railway specification T-1/57 and their drawing no.090M and 27mm diameter fish bolts.

A Pylon support system shall be provided for supporting the fire fighting system by the contractor.

    - DESCRIPTION

Each transformer including oil conservator tank and cooler banks etc, shall be placed in pit surrounded by retaining walls (pit walls). The minimum clear distance of the retaining wall from the transformer shall be 20% of the transformer height or 0.8m whichever is more. The pit thus formed shall have a capacity equal to twice the volume of oil in the transformer along the NGR including conservator tank and cooler banks below the MS grating. The MS grating placed at the formation level shall be covered with 100 mm thick gravel of 40mm nominal size, which acts as an extinguisher for flaming oil.

  - FIRE PROTECTION WALLS

    - GENERAL.

Fire protection walls shall be provided in accordance with Tariff Advisory Committee (TAC) recommendations.

    - APPLICATION CRITERIA

A fire wall shall be erected between the transformers if the free distance between the various pieces of equipment is less than 10m to protect each one from the effects of fire on another.

    - FIRE RESISTANCE

The fire wall shall have a minimum fire resistance of 3 hours. The partitions which are made to reduce the noise level of the transformer shall have the same fire resistance where the partitions are also used as fire walls. The walls of the building, which are used as fire walls, shall also have a minimum fire resistance of 3 hours. The firewall shall be designed in order to protect against the effect of radiant heat and flying debris from an adjacent fire.

    - MECHANICAL RESISTANCE

The fire wall shall have the mechanical resistance to withstand local atmospheric conditions. If this wall serve as a support for equipment such as insulators etc, its mechanical rigidity must be increased .

Connecting the walls by steel or other structures, which may produce a reversing torque if overheated, shall be avoided.

    - DIMENSIONS

The firewall shall extend at least 2m on each side of the power transformers or reactors and at least 1m above the conservator tank or safety vent. These dimensions might be reduced in special cases, and if TAC permits so, where there is lack of space. A minimum of 2m clearance shall be provided between the equipments e.g transformer reactor fire walls. The building walls, which act as firewalls, shall extend at least 1m above the roof in order to protect it.

    - MATERIALS

The fire wall may be made of reinforced concrete (M-20 grade) fire brick, concrete blocks or corrugated iron on a steel structure as per the system requirements. Materials used must conform to the standards of the National fire Prevention Association & ATC norms.

  - CABLE & PIPE TRENCHES:

- The cable trenches shall be constructed by stone masonry as per drawing furnished by the KNNL and present removable RCC. Cover( with lifting arrangement) shall be constructed using RCC of M20 grade.

- The cable trenches shall be constructed as per the drawing furnished by the owner for the following loads.

- Cable trench covers shall be designed for self-weight of top slab + concentrated load of 200 kg at span on each panel.

- Cable trench crossing the road/rails shall be designed for class AA class A and class 70R loading or IRC/relevant IS Code and should be checked for transformer / reactor loading.

- Trenches shall be drained. Necessary sumps be constructed and sump pumps shall be supplied. Cable trenches shall not be used as storm water drains.

- The top of trenches shall be kept at least 1502mm above the finished ground level. The top of cable trench shall be such that the surface rainwater do not enter the trench.

- All metal parts inside the trench shall be connected to the earthling system.

- Cables from trench to equipment’s shall run in hard conduit pipes.

- Trench wall shall not foul with the foundation. Suitable clear gap shall be provided.

- A Clear (vertical) space of at least 200mm shall be available for each tier in cable trench. From trench bed to lowest tier, a minimum clearance of 150mm shall be available.

- The trench bed shall have a slope of 1/500 along the run & 1/250 perpendicular to the run.

- All the construction joints of cable trenches i.e. between base slab to base slab and the junction of vertical wall the base slabs well as from vertical wall to wall and all the expansion joints shall be provided with approved quality PVC water stops of approx. 230 * 5 mm size for those section

where the ground water table is expected to rise above the junction of base slab and vertical wall of cable trenches.

- Cable trenches shall be blocked at the ends if required with brick masonry in cement sand mortar lid and plaster with 12mm thick 1:6 cement sand mortar.

  - FOUNDATION / RCC CONSTRUCTION:

    - GENERAL:

- Work covered under this Clause of the specification comprises the design supply and installation of foundations and other RCC constructions for

switchyard structures. Equipment supports. Trenches drains. Jacking pad pulling block fencing & systems buildings tanks or for any other equipment or service and any other foundation required to complete the work. This clause is as will applicable to the other RCC constructions. The circuit reakers/ reactor / transformer shall rest on block foundations only.

- Concrete shall conform to the requirements	mentioned in IS:456 and all the tests shall be conducted as per relevant Indian standard Code.

- If the site is sloppy the foundation height will be adjusted to maintain the exact level of the top of structures to compensate such slopes.

- The switchyard foundation’s plinths and building plinths shall be minimum 300mm and 500mm

above finished ground level respectively.

- Minimum 75mm thick lean concrete (1:4:8) shall be provided below all underground structures. Foundations, trenches, etc to provide a base for construction.

- Concrete made with Portland slag cement shall be carefully cured and special importance shall be given during the placing of concrete and removal shuttering.

- The design and detailing of foundations shall be done based on the approved soil data and sub-soil conditions as well as for all possible critical loads and the combinations there of. The spread footings foundation or pile foundation as may be required based on soil/sub-soil conditions and superimposed load shall be provided.

- If pile foundations are adopted the same shall be cast-in-situ driven/bored or precuts of under reamed type as per relevant IS code. Only RCC piles shall be provided. Suitability of the adopted pile foundations shall be justified by way of full design calculations. Detailed design calculations shall be submitted by the bidder showing complete details of piles/pile groups proposed to be used. Necessary initial load test shall also be carried out by the bidder at his cost to establish the piles design capacity. Only after the design capacities of piles have been established, the contractor

shall take up the job of piling. All the work (design & testing) shall be planned in such a way that these shall not cause any delay in project completion.

    - DESIGN:

- All foundations shall be in reinforced cement concrete. The design and construction of RCC structures shall be carried out as per IS-456 and minimum grade of concrete shall be M-20 Higher grade of concrete than specified above may be used at the discretion of Bidder, which has to be stated at the time of bidding.

- Limit state method of design shall be adopted unless specified otherwise in the specification.

- For design and construction of steel concrete composite beam IS:1 1384 shall be followed.

- For detailing of reinforcement IS:2502 and SP:34 shall be followed. Cold twisted deformed bars (Fe=415 N/mm2) conforming to IS:1786 shall be used as reinforcement. However in specific areas. Mild steel Grade D conforming to IS:432 can also be used Two layers of reinforcement (inner and outer face) shall be provided for wall & slab sections basing thickness of 150 mm and above. Clear cover to reinforcement towards each face shall be 40mm in case of side walls of cable ducts and for sewer foundations & equipment foundation clear cover shall be 50mm.

- RCC water retaining structures like storage tanks. Cooling water basin etc, shall be designed as uncracked section in accordance with IS: 3370 (part 1 to 4) by working stress method. However, water channels shall be designed as cracked section with limited steel stresses as per IS: 3370 (part 1 to 4) by working stress method.

- The procedure used for the design of the foundations shall be the most critical loading combination of the steel structure and or equipment and /or super structure and other conditions which produce the maximum stresses in the foundation or the foundation component and as per the relevant IS Codes of foundation design. Detailed design calculations shall be submitted by the bidder showing complete details of piles/pile groups proposed to be used.

- All foundations shall rest below virgin ground level and the minimum depth of foundation below the virgin ground level shall be at least 500mm for equipment foundations and 1000mm for towers, transformers and reactors.

- Design shall consider any sub-soil water pressure that may be encountered following relevant standard strictly.

- Necessary protection to the foundation work if required shall be provided to take care of any special requirements for aggressive alkaline soil, black cotton soil or any other type of soil. which is detrimental/harmful to the concrete foundations.

- RCC columns shall be provided with rigid connection at the base.

- All sub-structures shall be checked for sliding and overturning stability during both construction and operating conditions for various combinations of load. Factors of safety for these cases shall be taken as mentioned in relevant IS codes or as stipulated elsewhere in the Specifications. For checking against overturning, weight of soil vertically above footing shall be taken and inverted frustum of pyramid of earth on the foundation should not be considered.

- Earth pressure for all under ground structures shall be calculated using coefficient of earth pressure at rest coefficient of active or passive earth pressure (whichever is applicable). However, for the design of substructures of any underground enclosures. earth pressure at rest shall be considered.

- In addition to earth pressure and ground water pressure etc. a surcharge load of 2T/Sq.m shall also be considered for the design of all underground structures including channels sumps Tanks, trenches substructure of any underground hollow enclosure etc. for the vehicular traffic in the vicinity of the structure.

- Following conditions shall be considered for the design of water tank in pumps house. Channels sumps trenches and other underground structured.

  - Full water pressure from inside and no earth pressure & ground water pressure & surcharge pressure from outside (application only to structures, which are liable to be filled up with water or any other liquid).

  - Full earth pressure, surcharge pressure and ground water pressure from outside and no water pressure from inside.

  - Design shall also be checked against buoyancy due to the ground water during construction and maintenance stages. Minimum factor of safety of 1.5 against buoyancy shall be ensured ignoring the superimposed loading.

- Base slab of the any underground enclosure shall also bed designed for empty condition during construction and maintenance stages with maximum ground water table (GWT). Minimum factor of safety of 105 against buoyancy shall be ensured ignoring the superimposed loadings.

- Base slab of any underground enclosure like water storage tank shall also be designed for the condition of different combination of pump sumps being empty during maintenance stages with

maximum GWT. Intermediate dividing piers of such enclosures shall be designed considering water in one pump sump only and the other pump sump being empty for maintenance.

- The foundations shall be proportioned so that the estimated total and differential movements of the foundations are not greater than the movements that the structure or equipment is designed to accommodate.

- MACHINE FOUNDATIONS:

  - All machine foundations shall be designed in accordance with the provisions of the relevant parts of latest revisions of Indian Standards IS: 2974, IS: 456 and IS: 2911. The provisions of DIN 4024 (latest) shall also be followed.

  - All block foundations resting on soil or piles shall be designed using the classic half space theory.

The mass of the RCC block shall not be less than three times the mass of the machine. Dynamic analysis shall be carried out to calculate natural frequencies in all the modes including couple modes and to calculate vibration amplitudes. Frequencies and amplitude criteria as laid down by the relevant IS codes and/or machine manufacturers shall be satisfied. Minimum reinforcement shall be governed by IS: 2974 and IS: 456.

  - For the foundations supporting minor equipment’s weighing less than one tone or if the mass of the rotating parts is less than one hundredth of the mass of the foundation. No dynamic analysis is necessary. However, if such minor equipment is to be supported on building structures. Floors etc. suitable vibration isolations shall be provided by means of springs neoprene pads etc. and such vibration isolation system shall be designed suitably.

- OTHER FOUNDATIONS:

All foundations shall be designed in accordance with the provisions of the relevant part latest revisions of Indian Standards IS: 2911 and IS 456.

- Type of foundation system i.e. isolated footing or raft or pilling shall be decided based the load intensity and soil strata. Of foundation system i.e., isolated footing or raft or pill shall be decided based on the load intensity and soil strata.

- Minimum three piles shall be provided in any pile group if required.

- The tower and equipment foundations shall be designed for a factor of safety of 2.2 normal/broken wire condition and 1.65 for short circuit condition.

    - ADMIXTURES & ADDITIVES:

- Only approved admixtures shall be used the concrete for the Works. When more than one admixture is to be used, each admixture shall be batched in its own bat and added to the mixing

water separately before discharging into the mixture. Admixtures shall be delivered in suitably labeled containers to enable Identification.

- Admixtures in concrete shall conform to IS: 9103. The water proofing cement additives shall conform to IS: 2645. Concrete Admixtures/Additives shall be approved by the KNNL.

- The Contractor shall use an approved neutralized vinyl resin air-entraining agent all concrete. The Air entraining agent shall be supplied add batched as a solution with a solids content not exceeding 15 percent by weight with suitable stable an consistent PH. Air-entraining requirements shall be in accordance with CP 100 part I.

- The Contractor may propose and the KNNL may approve the use of a water-reduction set-reducing admixture in some of the concrete. The use of such an admixture will not be approved to overcome problems associated with inadequate concrete plan capacity of improperly planned placing operating and shall only be approved as a aid overcoming unusual circumstances and placing conditions.

- The water-reducing set-retarding admixture shall be an approved brand of Iron sulphonate type admixture..

- The water-proofing cement additives shall be used as required/advised by KNNL.

    - HOT WEATHER REQUIREMENTS:

- As per relevant Code during hot weather. Precautions shall be taken to avoid premature stiffening of the fresh mix and to reduce water absorption and evaporator losses and when the temperature of the surrounding air is higher than 30 degree C the following shall apply unless otherwise approved by the KNNL.

  - The framework shall be continuously sprayed with cold water in advance of concertina and excess water shall be remove from inside the forms immediately prior to placement of concrete.

b The reinforcement and the framework (if metal forms are used) shall be protected form the effect of hot winds and direct sunlight..

- Suitable barriers shall be provided to protect the freshly placed concrete from wind until the concrete is sufficiently hard.

- The concrete when place. Shall be maintained at a temperature of less than 30 degree C by the use of chilled water or by spraying the aggregate with cold water.

- The concrete shall be mixed. Transported, placed and consolidated, as rapidly as possible and shall then be covered with an impervious membrane or wet Hussein until moist curing begins.

- Curing compounds shall not be used as an alternative to the requirements of clause 8.10.3.

- During hot weather (atmospheric temperature above 40 degree C) or cold weather (atmospheric temperature at or below 5 degree c) the concreting shall be done as per the procedure set out in IS: 7861 (part I &II)

  - CHAIN LINK FENCES AND GATE

    - GENERAL

Tenderer to furnish the layout for the area and proposal for fencing to the requirement of KNNL for approval.

    - AREAS REQUIRING FENCING

Fencing area accommodating the installations such as jackwell, pump house, substation, portion of rising main including the manifold shall be provided with suitable fencing with gate arrangement. It shall be graded/levelled suitably.

Wherever necessary anti-reptile fixtures/arrangement shall be provided along with fencing.

    - PRODUCT MATERIALS

- The minimum requirements are as follows.:

  - Chain link fence fabric in accordance to IS-2721

  - Size of mesh :75mm

  - Size of coated wire :3.15 mm dia

  - Width of chain link : 2400mm

  - Class of zinc coating : medium

- POSTS.:

| Angle section | Spacing mm |  |
| --- | --- | --- |
| Intermediate | 1.45 x45x 6 | 2500 |
| Straining posts | 1.65x 65x 6 2500 |  |
| Stay post | 1.45 x45x 6 | 2500 |

All structural steel shall confirm to IS:2062 and shall be painted with a coat of approved steel primer and two coats of synthetic enamel paint.

The chain link fabric shall be fixed to the post at the top and bottom of the fence by welding / fixing 50mm MS flat all through its length.

- Fencing shall be either of galvanized barbed tape or of galvanized barbed barbed wire , 6 strands barbed tape shall conform to IS:1730 . Barbed wire shall conform to IS:278.

The barbed wire shall consist of two splices per reel. The barbed wire shall be formed by twisting two line wires, one containing the barbs,. The barbed wire shall be of 12 SWG galvanized

steel with its weight 155-136 gm/m length of the wire. Distance between two barbs shall be 75mm. The barbs shall carry four points and shall be formed by twisting two points wires, each two turn tightly round one line wire, making altogether 4 complete turn. The barbs shall be finished in such a way that the four points are set and locked at right angles to each other. The barbs shall have a length of not less than 13 mm and not more than 18mm. The points shall be sharp and well pointed.

- Above chain link,3-rows (6 Nos) of barbed tape/wire shall be provided in each arm of the Y shaped barbed arm at top. With barbed tape/wire above the chain link fence, the total fence height shall be minimum 3000mm above finished gravel level.

- barbed tape/wire same as intermediate and straining post.

- Fasteners: single strand aluminium or galvanized steel wire conforming to requirements for fence fabric 4mm diameter.

- Tension wire: single strand, high tensile, galvanized steel wire 4mm dia.

- Fittings and hardware.: cast aluminium alloy or galvanized steel, malleable or ductile cast iron, turn buckles to be drop forged.

- For every 50 reels or part thereof samples of the barbed tape/wire and the individual line wires shall be put to tensile test and in case of failure to conform to the tensile properties given below, two additional tests of each kind shall be made on the samples cut from other reels. TENSILE PROPERTIES

Breaking load of line wire: Minimum 216 Kg / Maximum 302 kg. Minimum breading load of complete barbed wire/tape: 444 Kg.

On the results of these additional tests, the whole or portion of the barbed wire/tape shall be accepted or discarded by the KNNL as the case may be.

    - INSTALLATION :

- Fence shall be installed along lines shown on approved drawings.

- Post holes shall be excavated by approved methods.

- Intermediate posts shall be spaced 2.5m apart measured parallel to ground surface.

- Straining posts shall be installed at equal intervals not exceeding 25.00m.

- Straining posts shall be installed at sharp changes in grade, at corners at change of direction and where directed.

- All corner post will have two stay post and every tenth post will have a transverse stay post.

- Posts shall be set in concrete. Concrete work shall conform to relevant clause. Posts shall be braced and held in plumb position and true alignment and elevation until concrete has set.

- Fence fabric shall not be installed until concrete has cured a minimum of 5 days.

- Bottom and top of the fence fabric shall be fixed with MS flats of 50 mm x 6 mm(Min)

- Fence fabric shall be laid out with barbed edge on top, stretched tightly and shall be fastened to intermediate, gate and straining post with 50 mm x 6 flats.

- Fabric shall be secured to tension wires with tie wires at 400 mm intervals.	Tie wires shall be given not less than two twists

- Barbed tape shall be spliced with standard wire splices.

- Barbed tape shall be stretched to have uniform tension.

- Barbed tape shall be attached to barbed wire arms with approved metal	clips.

- Gates shall be installed in locations shown on drawings. Next to the main gate, a men gate (1.24m wide , single leaf) shall also be provided.

- Bottom of gates shall be set approximately 40 mm above ground surface and necessary guiding mechanism shall be fitted.

- A 345/380 mm thick ( one and a half brick size) toe wall of Brick/Rubble masonry or concrete with notches shall be provided below all fencing and shall be minimum 200 mm above and 500mm below finished ground level. All exposed surfaces of brick toe wall shall be provided with 15mm 1:6 cement sand plaster and coated with two coats of water proofing cement paint. In case of rubble masonry is provided suitable pointing shall be done.

    - GATES

- The Gate frame shall be made of medium duty MS pipe confirming to relevant IS with welded joints.

- The gates shall be fabricated with welded joints to achieve rigid connections. The gate frames shall be painted with one coat of approved steel primer and two coats of synthetic enamel paint.

- Gates shall be fitted with approved quality iron hinges, latch and latch catch. Latch and latch catch shall be suitable for attachment and operation of pad lock from either side of gates. Hinges shall permit gates to swing through 180 degree back against fence.

- Gates shall be fitted with galvanized chain hook or gate hold back to hold gates open. Double gates shall be fitted with centre rest and drop bolt to secure gates in closed.

  - BUILDINGS- GENERAL REQUIREMENTS

    - GENERAL.

The scope include the design, engineering and construction of building including sanitary, water supply, electrification etc. The tentative layout showing the facilities to be provided for control room building is enclosed. The size and layout of the building may be modified as per requirements of SLD with the approval of the KNNL.

    - DIMENSIONS

An open space of 1-m minimum shall be provided on the periphery of the rows of panels and equipment generally in order to allow easy operator movement and access as well as maintenance.

    - DESIGN.

- The buildings shall be designed:

  - to the requirements of the National Building Code of India and the standards

quoted therein.

  - for the specified climatic and loading conditions.

  - to adequately suit the requirements of the equipment and apparatus contained

in the buildings and in all respects to be compatible with the intended use and occupancy .

  - with a functional and economical space arrangement.

  - for a life expectancy of structure, systems and components not less than that of the equipment which is contained in the building, provided regular maintenance is carried out.

  - to be aesthetically pleasing. Different buildings shall show a uniformity and consistency in architectural design.

  - to allow for easy access to equipment and maintenance of the equipment.

  - with, wherever required, fire retarding materials for walls, ceilings and doors, which would prevent supporting or spreading of fire.

  - with materials preventing dust accumulation.

- suitable expansion joints shall be provided in the longitudinal direction wherever, necessary with provision of twin columns.

- Individual members of the buildings frame shall be designed for the worst combination of forces such as bending moment, axial force, shear force, torsion etc.

- Permission stresses for different load combinations shall be taken as per relevant IS codes.

- All cable vaults shall be located above ground levels i.e cable vaults shall not be provided as basements in the buildings.

- The building lighting shall be designed in accordance with the requirements of relevant section.

- The building auxiliary services like air conditioning and ventilation systems, fire protection and detection systems and all other miscellaneous services shall be designed in accordance with the requirements specified in relevant section or elsewhere in this specification.

    - DESIGN LOADS.

Building structures shall be designed for the most critical combinations of dead loads, super-imposed loads, equipment loads, crane load, wind loads, seismic loads and temperature loads. In additions, loads and forces developed due to differential settlement shall also be considered.

Dead loads shall include the weight of structures complete with finishes , fixtures and partitions and should be taken as per IS;1911 ( latest revision). Super-imposed loads in different areas shall include live loads, minor equipment loads, cable trays, small pipe racks/hangers and erection, operation and maintenance loads. Equipments loads shall constitute if applicable all load of equipments to be supported on the building frame.

For crane loads an impact factor of 30% and lateral crane surge of 10% (lifted weight + trolly) shall be considered in the analysis of frame according to provisions of IS:875 (latest revision). The horizontal surge shall be 5% of the static wheel load.

The wind loads shall be computed as per IS: 875, seismic co-efficient method shall be used for the seismic analysis as per IS: 1893 ( latest revision).

For temperature loading, the total temperature variation shall be considered as 2/3 of the average maximum annual variation in temperature. The average maximum annual variation in temperature for the purpose shall be taken as the difference between the mean of the daily minimum temperature during the coldest month of the year and mean of daily maximum temperature during the hottest month of the year. The structure shall be designed to with stand stresses due to 50% of the total temperature variation.

Wind and seismic forces shall not be considered to act simultaneously.

Floors / slabs shall be designed to carry loads imposed by equipment , cables piping travel of maintenance trucks and equipment and other loads associated with building. In general, floors shall be designed for live loads as per relevant IS and cable and piping loads not less than 5 kN/sqm. Hanging from the underside.

In addition, beams shall be designed for incidental point loads of 20 kN to be applied at any point along the beams. The floor loads shall be subject to KNNL approval.

For consideration of the loads on structure, IS:875 “code of practice for structural safety of building” shall be followed. The following minimum superimposed live loads shall however, be considered for the design.

- Roof	150kg/m2   for accessible roofs

75 kg/m2   for non-accessible roofs

- RCC floors 500 kg/m2	for offices and minimum 1000 kg/m2 for

Equipment floors or actual requirement , if Higher than 1000 kg/m2 based on equipment Component weight and layout plans.

- Stair and balconies 500kg/m2

- Toilet rooms	200 kg/m2

- Cheque-red plate	floor 400kg/m2

    - . SUBMISSION: The following information shall be submitted for review and approval to the KNNL.

- Design criteria shall comprise the codes and standards used, applicable climatic data including wind loads, earthquake factors maximum and minimum temperatures applicable to the building locations, assumptions of dead and live loads, including equipment loads impact factors, safety factors and other relevant information.

- Structural design calculations and drawing (including construction/ fabrication) for all reinforces concrete and structural steel structures.

- Fully, dimensioned floor plans, cross sections, longitudinal section and elevations of each building. These drawings shall be drawn at a scale not smaller than 1:50 and shall identify the major building components.

- Fully dimensioned drawing showing details and sections drawn to scales of sufficient size to clearly show sizes and configuration of the building components and the relationship between them.

- Product information of building components and materials, including walls,partitions, flooring, ceiling, roofing , door and windows and building finishes.

- A detailed schedule of building finishes including colour schemes.

- A door and window schedule showing door type and locations, door locks sets and latch sets and other door hardware. Approval of the above information shall be obtained before ordering materials or starting fabrication or construction as applicable.

  - CONTROL ROOM BUILDING:

Construction including anti termite treatment of control room building for associated switchyard shall be in the scope of the bidder. The control room building shall be of RCC framed structure

of minimum concrete M-20 grade. The minimum area required is shown in the drawings enclosed with the specification.

  - FINISHING SCHEDULE

The preliminary indicative finishing schedule is given in subsequent clauses. However, at the time of detailed engineering, the KNNL reserves the right to alter the finishing schedule and specifications and such changes shall have no additional financial implication whatsoever to the KNNL.

  - FLOORING:

Pump House: The flooring shall be with mosaic tiles of superior quality which shall be got approved and executed as per reverent IS specification latest versions.

Flooring in various rooms of control room building shall be as under:

- Control room:	2mm thick PVC tiles over under bed of 50mm thick

PCC 1:2:4

- Battery Room:	Acid resistance tiles

- Front Lobby:	Kota stone

- Office, Library etc:	Terrazo flooring.

- Cable valut:`	I.P.S Flooring.

For all buildings , suitable arrangement for draining out water collected from equipment below down, leakages, floor washings, fire fighting etc, shall be provided for each floor.

  - ROOFING:

Pump House: The roof of pump house shall be with GI sheets mounted on trusses of superior quality which shall be got approved and executed as per relevant IS specification, latest versions.

  - MISCELLANEOUS GENERAL REQUIREMENTS

    - Dense concrete with controlled water cement ratio preferable 0.45 shall be used for all underground concrete structures such as pump hourse. Tanks water rating strucuture, cable and pipe trenches etc. For achieving water tightness.

    - All joints including construction and expansion joints for the water retaining structures shall be made watertight by using PVC ribbed water stops with general bulb. However kicker type (externally placed) PVC water stops shall be used for the base slab and in other areas where it is required to facilitate concreting. The minimum thickness of PVC water stops shall be 5mm and minimum width shall be 230mm.

    - All steel sections and fabricated structures which are required to be transported on sea shall be provided with anti-corrosive paint to take care of sea worthiness.

    - All mild steel parts used in the water retaining structures shall be hot-dip galvanized, the minimum coating of the zinc shall be hot-dip galvanize. The minimum coating of the zinc shall be 750

gm/sq. for galvanized structures and shall comply with IS: 2629 and IS:2633 . Galvanizing shall be checked and tested in accordance with IS:2629. The galvanizing shall be followed by the application of an etching printer and dipping in black bitumen in accordance with BS:3416.

    - A screed concrete layer not less than 100mm thick and of grade not weaker than M10 conforming to IS:456-1978 shall be provided below all water retaining structures. A sliding layer of bitumen paper or craft paper shall be provided over the screed layer to destroy the bond between the screed and the base slab concrete of the water retaining structures.

    - Bricks having minimum 75 kg/cm2 compressive strength can only be used for masonry work. Bidder shall ascertain himself at site regarding the availability of bricks of minimum 75 kg/cm2 compressive strength before submitting his affer.

    - Monorails, monorail girders and fixtures shall be provided where ever required.

    - Doors and windows on external walls of the buildings (other than areas provided with insulated metal claddings) shall be provided with RCC sun-shade over the openings with 300mm projection on either side of the openings. Projection of sunshade from the wall shall be minimum 450mm over window openings and 750mm over door openings.

    - Stairs shall have maximum riser height of 150mm and minimum tread width of 300mm . Minimum width of the stairs shall be 1500mm.

    - Angles 50x50x6 mm (minimum) with lugs shall be provided for edge protection all around cut outs/openings in floor slab. Edges of drains supporting grating covers. Edges of RCC cable/ pipe trenches supporting covers, edges of manholes supporting covers, supporting edges of precise cover and any other place where breakage of corners of concrete is expected.

    - Anti termite chemical treatment shall be given to column pits, wall trenches, foundations of buildings , filling below the floors etc, as per IS :6313 and other relevant Indian standard.

    - Hand-railing minimum 900mm high shall be provided around all floor/roof openings projections/balconies, walk-ways, platforms, steel stairs etc. All handrails and ladder pipes shall be 32mm nominal bore MS pipes (medium class) and shall be galvanized(medium class as per IS:277). All rungs for ladder shall also be galvanized as per IS:277 medium class.

For RCC stairs: Hard railing with 20mm square MS bars. Balustrades with suitable MS flats and aluminium handrails shall be provided.

1.18.  INERFACING:

The proper coordination and execution of all interfacing civil works activities like fixing of conduits in roofs/walls./floors. Fixing of foundation bolts. Fixing of lighting fixtures. Fixing of supports / embedment, provisions of cutouts etc shall be the sole responsibility of the contractor. He shall plan all such activities in

advance and execute in such a manner that interfacing activities do not become bottlenecks and dismantling, breakage etc, is reduced to minimum.

  - WATER SUPPLY

The contractor shall be overall responsible for supply of water within switchyard for firefighting drinking purpose and other miscellaneous purposes water shall be made available at single point by the contractor by providing at least 1 bore points To scope is also inclusive of supply and erection of all tanks pipes. Fittings etc required for water supply to be taken from the terminal point to the respective buildings A scheme still be prepared by the contractor indicating the layout and details of water supply when shall be got approved by the owner before actual start of work. Any extra boreholes if required shall be within the scope of contractor.

  - STATUTORY RULES:

    - Contractor shall comply with all the applicable statutory rules pertaining to enquire act (as applicable for the sate). Fire safety rules of Tariff Advisory committees water act for pollution control etc.

    - Preventions for fireproof doors of staircases fire separately we plastering on structural members (in fire prone at case) etc., shall be made according to the recommendations of Tariff Advisory Committee.

    - Statutory clearance and norms of state pollution control board shall be showed as per Water Act for effluent quality from plant.

    - Requirement of sulfate resistant cement (SRC) for sub-structural works should decided in accordance with the Indian Standards based on the findings of the detailed investigation to be carried out by the Bidder

    - Foundation system adopted by Bidder shall ensure that relating settlement shall be as per provision in IS: 1904 and other Indian Standards

    - All water retaining structures designed as un-cracked section shall also be tested for water tightness at full water level in accordance with clause no 10 of 3370 (part-I).

    - Construction joints at the following locations shall be provided.

      - At the meeting points of the columns and the raft.

      - At the point of contra flexure in the columns.

Additional reinforcements and shear keys shall be provided at the construction joints.

- All underground concrete structures like basements pumps. retaining structures etc. shall have plasticizer cum water proofing cement addition conforming to IS: 9103. In addition. Limit an permeability as given is IS: 2615 shall also be met with. The concrete surface of these

structures in contact with earth shall also be provided with two coat of bituminous painting for water/damp proofing In case of water leakage in the above structures. Injection method shall be applied for repairing the leakage.

### SECTION – XIII

Technical Specifications for MS Pipe

- The scope of work includes:

The scope includes installation of MS Gravity Pipe from each delivery chamber including necessary kinetic air valves, scour valves, Control valves, Manhole chambers, MS bends, and MS specials etc. as per ground profile and design considerations.

The scope includes providing 0.5 mm internal epoxy lining and 4 mm thick factory made coal tar bituminous pipe coating with steel wire mesh of required size. The scope includes installation of MS Gravity Pipe including necessary kinetic air valves, scour valves, surge protection, MS bends, and MS specials etc. as per ground profile and design considerations.

Construction and installation of MS Gravity Pipe of suitable type diameter with required number of rows from Exit of existing canal with anchor blocks, valve chambers, manhole chambers, Thrust blocks, Intake well and other structure as required. Entire process right from design to commissioning shall be carried out as per relevant IS Standard. MS Gravity Pipe design shall conform to IS: 5822 and IS: 3589 (latest edition).

The contractor shall provide all the material required such as tapers, distance pieces, bends, nut bolts gaskets. The work of joining delivery pipelines to the respective manifolds for turbulence free smooth flow is included in this tender. Flanged joints shall be adopted for valves and but welding joints of flanged joints in jointing of delivery pipe.

Concrete saddles for valves and pipe work shall be provided by the contractor as per design and drawings furnished by him and approved by Engineer.

The scope should include necessary excavation foundation with anchor supports concrete thrust blocks, anchor blocks, valve chambers, manhole chambers and MS Gravity Pipe.

For design of MS Gravity Pipe following criteria shall be followed:

- Velocity shall be in the range of 0.8 m/sec to 1.8 m/sec

- Wall thickness proposed shall be without any negative tolerance.

- Minimum Hydraulic seal should be maintained at the upstream head as per the standard IS codes.

- Operating pressure, maximum gauge pressure and designed test pressure of system.

- Stability of pipe system.

- Protection against corrosion.

- MATERIAL OF CONSTRUCTION:

All the pipes and specials shall be fabricated out of steel plates confirming IS 2062.

The fabrication of pipe should generally confirm IS 1582-1966. The fasteners required for delivery pipe connections shall be of carbon steel.

The flange thickness shall be as per BS-1504.

- PAINTING

The interior of the pipe work and specials shall be provided with coal tar epoxy inner lining and pipe coating of thickness as per IS 1916:1989/IS: 3589-2001 (latest version).

- SURGE ANALYSIS AND PROTECTION:

This shall be calculated as per standard procedure necessary have to be provided a appropriate by them or the rising main for dampening and elimination of the surge effect. This is included in the scope of the work.

- Water hammer in pump discharge line caused by power balance.

- Due to sudden failure of single pump where multiple pumps are in parallel

- Due to variation in discharge.

- Due to sudden stoppage of pump due power supply failure.

Adequate surge protection to the rising mains and the entire system shall be provided after surge analysis.

- MS PIPES- GENERAL GUIDELINES CONSTRUCTION

Manufacturing of MS pipes shall be done in conformity with IS: 3589 subject to following :

The pipe shall be fabricated out of steel plates or strips of mild steel conforming to IS: 2062 and having minimum specified tensile strength of 410 Mpa. MS pipelines shall be of grade 410, helical seams/spiral longitudinally welded with Straight seams, without circumferential joints with beveled ends as per IS 3589. The pipes shall be manufactured in an approved factory/fabrication yard having quality control system, well equipped testing laboratory.

The end of the pipes, short pipes shall be beveled end for welding.

- Manufacturing process shall ensure that¬

  - Base material i.e., HR coils/ steel plates shall be of required Quality.

  - Production equipment is well designed automatic machine.

  - Quality control is comprehensive.

  - Hydro test of each pipe before lining.

- The thickness of the pipe line shall be decided by the bidder to meet the requirements. Also the thickness calculations shall be furnished for approval of the owner before procurement.

- Flanges should be machined on both faces. Fabrication of flanges from segment plates should be avoided. However, if under special circumstances flanges from segment plates are to be provided, on specific instructions of the Owner, such flanges should be completely stress relieved after welding and all welds shall be subject to dye penetration test. These flanges should also be machined.

- All welds are to be continuous single V butt welds with finished head of size equal to thickness of plate. All welding shall be as per provisions laid in IS-816/equivalent standard (latest revision). Welding shall be done by experienced and good operators who have been qualified by tests as specified in IS-817/equivalent standard (latest revision). Welding shall be by automatic machine and shall be carried out by using approved electrode with compatible flux.

- Bolts and nuts shall be of hexagonal head conforming to -1367/equivalent standard (latest revision).

- The pipe sections shall be carefully placed on the sand bed prepared as per specification. All joints before welding shall be thoroughly cleaned and requisite welding gap maintained.

- Welding sequence shall be done in such a way so as to minimise the distortion due to welding shrinkage. Any distortion will be duly rectified by the bidder without additional cost.

- Welding shall not be carried out when the surface of the parts to be welded are wet for any cause and during periods of rain and strong winds unless the welder and work are properly shielded.

- Precaution shall be taken to prevent any crack or damage in the external coating during installation. Pipes shall be laid in trenches excavated along the route and the over-ground portion shall be installed as per final layout drawings.

- The damaged portion of External coating or internal lining of the pipe Length at the joints due to welding shall be made good by manual application of external coating/internal lining to the required thickness and shall form a smooth continuous surface particularly with internal lining of the two adjacent pipes welded so that the flow through the pipeline is not affected due to manually applied coating.

- On completion of all welding in the pipe lines, the same shall be tested hydrostatically and after successful testing, shall be covered by sand wrapping and backfilling with earth where the pipes are laid in trenches

- Installed pipe shall be closed up at both ends at the end of each day by water tight plug or other means approved by the Owner to prevent debris/animals/human beings from entering the pipe.

- Specific Guidelines for Spirally/Longitudinally Welded MS Piping:

All spirally/Longitudinally welded MS pipes proposed to be procured under this section shall be fabricated out of steel plates or strips of mild steel coils (HR coils) conforming to IS 2062 and to the requirements of IS-3589 or equivalent standard and shall have minimum thickness as per recommendations of standards which shall be got approved by the contractor. There shall be no negative tolerance in the thickness of the Plates used.

i. Tolerance on outside dia of pipes (12.3.1 – IS 3589-2001: Table 6) Outside dia Tolerance (For all sizes)

For seamless pipes	±1% For Electric resistance Welded Pipes (ERW) & Submerged Arc

Welded (SAW) (including spirally Welded pipes) ±0.75%

Tolerance for straightness of pipeline (12.5.1 – IS 3589 –2001)

Each of the finished pipe shall not deviate from straightness by more than 0.2% of the total length.

Checking shall be carried out using a taught string or wire from end to end along the side of the pipe to measure the greatest deviation.

Ovality (Clause 12.3.3 – IS 3589 –2001)

Ovality shall not exceed 0.75% of the specified outside diameter of the pipes.

- TESTING OF PIPES

The pipes shall be tested to the following requirements.

- Continuous monitoring of dia. Thickness, fabrication.

- Visual inspection of all pipes from inside and outside for permissible tolerances as per IS: 3589

- Online ultrasonic testing of weld and body as per IS: 4260 during welding

- Radiographic testing as per IS: 4853

- Each pipe shall be hydraulically tested at 1.5 times the design pressure s per IS 3589 at the

manufacturer’s works.

- Mechanical test of finished pipes as per IS: 3589.

- MARKING

Each pipe shall be legibly marked as per clause 18 of IS: 3589 with following details :

a.Manufacturer’s name or trademark.b) Outside diameter & specified wall thicknessc) Pipe

designation

- QUALITY ASSURANCE

During the whole process of manufacturing, Owner’s representative shall have authority to supervise the Quality assurance process and witness the tests performed and also to get any pipe selected at random for repetition of tests and the Contractor shall carry out the tests at no extra cost to the Owner.

- FABRICATION OF MS SPECIALS AND FITTINGS

Unless and otherwise mentioned in the para below all MS specials and fittings (bends, tees, reducers, enlargers etc.) shall be fabricated using MS plate/sheet conforming to IS: 2062. the thickness shall be adequate to sustain field test pressure but shall not be less than the thickness of the pipe at that point.

The Contractor shall submit the detailed drawing for each special to be used in the pipeline. On approval of the same by the Owner, the Contractor will take-up the manufacturing. All specials shall be manufactured and coated at the manufacturer’s premises. In exceptional circumstances when welding in trench is unavoidable a flanged opening shall be provided for access inside the special for welding. The Contractor has to ensure the timely manufacturing of the MS specials so that they can be laid in synchronization with the pipe laying. The joints of adjacent pipe stretches have to be made with gap pieces approved by the Owner.

On completion of the manufacturing, the coating and lining for the special will be done by the Contractor as per the specifications for coating mentioned in specification. The Owner or his representative may at his discretion check the same and if the lining and coating are found defective in quality or thickness, the Contractor shall carryout the tests on all the remaining pipes not laid, again in the presence of the Owner or his representative.

- FLANGED BRANCHES

Flanged branches shall be fabricated in accordance with the general specification and to the Owner’s requirement. Flanged branches for air valves shall be welded into pipe in the required position. The branch for an air valve shall be vertical and at right angle to the longitudinal axis of pipe.

All the flanges shall be machined to standard thickness, square to the axis of the pipe.

- BENDS

Bends to provide change of alignment in pipe laying shall be manufactured to suit the site conditions from manufactured and tested pipes by angle cutting of the barrel or by such other standard procedure and re- welding. Bends shall be lined internally and coated externally as specified that for the pipes.

Bends shall be fabricated taking into account the vertical and horizontal angles for each case.

- The bends shall have welded joints and the upstream and downstream ends of each bend shall have a straight piece of variable lengths as required.

- When the point of intersection of a horizontal angle coincides with that of a vertical angle, or when these points can be made to coincide, a single combined or compound bend shall be used.

- TAPERS

Tapers shall be manufactured out of steel plates and lined internally and coated externally. Stiffener rings shall be provided to afford rigidity to pipe. They shall be manufactured generally in accordance with IS: 7322.

- MS FLANGES

Welding neck flanges confirming to IS 6392 be used in accordance to the design pressure at the place appurtenance with which they are to be used. The flange drilling shall conform to IS: 1538.

The Contractor shall assemble the flanges in the exact position by marginal cutting, if necessary so as to get the desired position of the sluice valves etc., either vertical or horizontal and shall then fully weld the flanges from both sides in such a way that no part of the welding protrudes beyond the face of the flanges. In case the welding protrudes beyond the flanges and if the Owner orders that such protrusions shall be removed, the Contractor shall file or chip them off. If required and when desired by the Owner, the Contractor shall provide and weld gusset stiffeners, as directed on site.

- BLIND FLANGES

Blank flanges shall be provided at all ends left unattended for the temporary closure of work and also for commissioning a section of the pipeline or for testing the pipeline laid. For temporary closure, non-pressure blank flanges consisting of mild steel plates, tack welded at the pipe ends may be used. For pipes subjected to pressures, the blank flanges or domes suitably designed as per Owner’s requirement shall be provided. The thickness of the blank flanges shall be as defined in IS: 6392 for the nominal size and design pressure at the place of installation, the flange drilling for all flanges upto 1500 mm shall conform to the provision of IS: 1538 and those above 1500 mm shall conform to IS: 6392.

- STIFFENER RINGS

The Contractor shall provide stiffener rings wherever required as per designs. The Contractor shall weld the same to the pipes with one circumferential run on each side.

- MANHOLES

For manhole installation, a fabricated tee with one side flanged must be used. The size of manhole shall not be less than 600 mm and it shall project at least 27.5 cm above the pipe crown. The 600 mm end must be provided with blind flanges.

- CLOSING OR MAKEUP SECTIONS

Closing or make up sections shall be furnished at appropriate locations on the line to permit field adjustments in pipeline length to compensate for shrinkage in field welded joints, differences between actual and theoretical lengths and discrepancies in measurements.

- TEST HEADS

Test heads may be ellipsoidal, standard dished as per relevant ASME code or hemispherical heads. They shall be welded and removed after the test. Allowance shall be made in the length of the pipe section receiving the test head for the welding and removal of the head and preparation of the plate edges for the final weld after testing.

- DISMANTLING JOINT

All butterfly, or any other online valves etc. shall be installed between flanges with a flexible MS dismantling joint at one side. The joint must allow dismantling of the valve meters, etc. without causing stress to the joints of the attached pipes. The minimum clearance of the dismantling joint shall be five (5) cm. The pressure class of the dismantling joint shall be the same as that of the pipe. Drawings of the dismantling joint shall be submitted to the Owner for approval. The nuts and bolts of the joint shall be galvanized. The joints shall be painted/ coated as per specification given for exposed pipes.

- INSPECTION AND TESTS ON PIPE AND FITTINGS / SPECIALS

The hydraulic test pressure shall be as per clause 13 of IS: 3589 for specials. Dye penetration test as prescribed in IS: 7322 and VT is acceptable in lieu of hydraulic test for bends only.

All works and material under specification will be rigidly inspected during all phases of manufacture and testing and such inspection shall not relieve the Contractor of his responsibility to furnish material and perform work in accordance with these specifications.

The Owner or the authorized inspection agency shall have free access to those parts of the plants that are concerned with the furnishing of materials of the performance of work under this specification. The bidder shall furnish the Owner reasonable facilities and space without charge for inspection, testing and obtaining

of any information he desires in respect of the quality of material used and the progress and manner of work.

Contractor shall provide and operate suitable equipment capable of conducting the specified hydraulic test pressure to the inside surfaces of the pipe and of sustaining the required period.

- SURGE SHAFTS /PRESSURE SUSTAINING VALVES

The bidder shall carry out surge analysis duly taking in to accountthe length of delivery pipe up to the delivery pond including valves, expansion joints, etc. and propose a system suitable to take care ofthe surges during shut down of pump sets. The bidder shall provide a surge tank based on the surge analysis studies and same shall be proved.

- PAINTING& COATING

  - Lining:

The inner surface of over ground/buried pipe shall be provided with epoxy paint. The following are the procedures generally adopted.

  - Cleaning:

Pipe surfaces shall be thoroughly cleaned and dried before the application of lining / coating, and shall be free of dirt, grease, oil rust, scale or other foreign matter. The pipe shall be cleaned by any one of the following methods:

    - Grit/shot blasting

    - Sand blasting, and

    - Mechanical cleaning

Before sand or shot/ grit blasting, all oil and grease if present on the metal surface should be removed by using suitable solvent and clean rags. Other foreign matters which cannot be removed by blast cleaning should be removed by suitable means. Surfaces then should be thoroughly cleaned by blast cleaning and the operation should remove scale, rust or any other superficial impurities from the surfaces exposing base metal presenting a grayish matter appearance except that slight shadows, streaks or discoloration caused by rust stings or mill scale oxides need not be removed.

Adequate moisture separators should be used so as to remove effectively oil and moisture from the air supply of the blasting unit. After cleaning, the pipes shall be protected from and maintained free from all oil, grease and dust that may fall on the pipes from outside sources till the pipe has received lining / coating.

Any pipe, that show deep pitting after blasting has been done, should be set aside pending examination by the Owner or his representative for approval for reconditioning or rejection.

  - EPOXY COATING:

The MS pipes after fabrication and cleaning as described above should be epoxy coated in the internal surface. The surface is to be provided with two coats of 40micron thick Zink rich epoxy primer and 3 coats of 100 micron thick each coat coal tar epoxy paint.

  - OUTER COATING

Outside surface of buried / over ground steel pipes and fittings shall be protected by the application of Reinforced cement-mortar coating with pipe wrapping applied over the outer surfaces of the piping sections and specials as per the requirement of AWWA C 205/ IS 3589

A   CEMENT MORTAR COATING

- REINFORCEMENT

Unless otherwise specified by the Owner, the reinforcement for the coating of pipe sections shall be spiral wire fabric/mesh of approved gauge size (ribbon mesh). Reinforcements shall be free of oil, grease, and other contaminants that might reduce the adherence between the coating and reinforcement. All reinforcement shall be placed in the middle third of the coating. When cement mortar coating is applied over a dielectric undercoat, the reinforcement shall not be attached to or otherwise be in contact with the steel pipe.

- SPIRAL WIRE AND WIRE MESH

Attachments of ends and splices in the wire shall be by welding or other suitable means acceptable to the Owner. Maximum spacing of the wire shall be 35 mm. The wires on 50 mm spacing on the 50mm x 100mm fabric shall extend circumferentially around the pipe.

Attachment of ends and splices in the wire shall be approved by the Owner. In 25mm x 25mm fabric, the spiral lap shall be 35mm and the sliced lap shall be 110 mm minimum.

- APPLICATION OF MORTAR COATING

Mortar coating shall be applied by mechanical or steam pneumatic placement to the specified thickness in one or more continuous application and shall consist of not more than 3 parts sand to 1 part cement by weight.

The water in the mixture shall be carefully controlled so that mortar will not run, sag or segregate.

The soluble chloride-ion (Cl) content of the cement mortar mix shall not exceed 0.15 percent expressed as a percentage of cement weight.

Allowance shall be made for splices of reinforcing wire. When reinforcement of special wire type is used, the end of the wire at the edges of the portion to be left uncoated shall be attached to the pipe shell by welding or other suitable means.

If applied in more than one course, the interval between the first and last course shall be not more than 2 hrs. The mortar shall be projected at high velocity against the exterior surfaces of the pipe or shall be applied by an equivalent method to produce a hard , tight adhering coating of the specified thickness in one or more continuous applications.

- DEFECTIVE COATING

If any sand pockets and porous spots occur they shall be completely cut out and replaced by pneumatic placement or hand application of mortar in the proportion of 2 parts sand to 1 part cement, by weight.

- COATING CRACKS

Care shall be exercised to minimize the occurrence of cracks in the mortar coating. Repair procedures shall include the brushing or wiping of near cement into cracks, autogenously healing of the cracks by additional moist curing the painting of the cracks with an epoxy coating, or combination of these methods.

- DAMAGES TO LINING/COATING

During the process of welding the pipe joints or any other location, the inner lining and outer coating may get damaged. At all such locations, the damaged or peeled off portion of the lining/coating shall be restored by Hand application of lining/coating material. Such application shall also ensure smooth continuous surface at all the joints to ensure smooth flow of water.

- CURING OF COATING

After the initial set has taken place, the mortar coating shall be cured by the moist or accelerated curing methods or unless otherwise specified by the purchaser, a membrane material may be applied immediately following the coating application. Moist and accelerated curing may be used interchangeably

on a time ratio basis of 5 hrs or moist curing to 1 hr of accelerated curing, except curing temperatures shall not exceed the maximum allowable for dielectric undercoat material.

The coating shall be kept continually moist by intermittent or continuous spraying for a period of at least four days. Moist curing may be used only if the minimum ambient temperature exceeds 5 deg-c continuously during the minimum required curing period, and no credit shall be allowed for any time during which the temperature drops below 10 deg-c.

- ACCELERATED CURING

Accelerated curing of the pipe or special may begin immediately after completion of the coating operation or within 6 hrs thereafter. The temperature of the pipe or special shall not exceed 30 deg C until the cement mortar coating has taken its initial set or until a period of 3 hrs has elapsed, whichever occurs first. The relative humidity shall be not less than 85% at a temperature between 45 deg C to 65 deg C for at least 18 hrs.

Coating of Specials- Mortar coating for pipe bends & other special section shall be reinforced with wire fabric or ribbon mesh. Fabric shall be applied over surface of pipe to be coated and shall be held away from pipe shell with self-furring mesh, furring clips etc. The application of coating shall conform to clause 5.6 of AWWA C-205 with the exception that hand application shall be substituted for mechanical/ pneumatic placement. Thickness shall be as required for straight section.

- MEMBRANE CURING

Membrane curing shall consist of the complete encapsulation of the coating by application of a material that will retain the moisture of the applied cement mortar coating.

- PRECAUTIONS

During the entire period of the application of the lining and coating and the curing thereof, the section shall be carefully supported and handled to avoid damage to the mortar. If a pipe section must be moved such an operation shall be done with every reasonable precaution to protect against damage. Any damaged portion of the lining or coating shall be cut out and replaced.

- DRAWINGS, CURVES AND INFORMATION REQUIRED

The various drawings/data and documents to be furnished by the successful BIDDER after award of contract shall include the following

  - A complete list of all piping and fittings of various sizes including but not limited to transition, bends, taper pieces, bulkheads, manhole arrangement with their quantities and details eg. nominal size, O.D, I.D (as applicable), thickness, design pressure, material of construction/code/standards etc.

  - GA of piping system based on tender drawings on verification of site condition.

  - A complete list of all valves and specials with their Data Sheets

  - Manufacturer's catalogue indicating complete range of available size and rating of pipes and fittings and other procured items.

  - Descriptive literature on the manufacturing process and quality control procedures highlighting the manufacturing, fabricating and testing facilities available in the shop.

  - Detailed fabrication drawing showing the sizes, materials and weld edge preparation etc. The fabrication drawings shall give all necessary information for fabrication, erection and painting of steel work in accordance with provisions of this specification. Welding symbols used shall be in accordance with the requirements of IS:813¬latest revision and shall be consistent throughout. Weld lengths called on the drawings shall be net effective lengths.

  - Welder’s Qualification record.

  - Bidder shall submit working drawing for excavation, sand-Filling and backfilling purpose as mentioned earlier.

  - Any other drawings or calculations that may be required for the clarification of work.

  - Instruction Manuals covering maintenance, repair and replacement of equipment fabricated and supplied by the BIDDER.

- TESTING

All the tests mentioned in the following shall be arranged by the CONTRACTOR.

- RADIOGRAPHY: The Longitudinal & circumferential joints will be random radio graphed limited to 2% of the total number of pipes for longitudinal joints and 5% of number of joints in case of circumferential joints at the discretion of the OWNER. The testing shall be arranged by the CONTRACTOR. Necessary labour& materials for welding of support etc. required for carrying out X-raying shall be provided by the CONTRACTOR for carrying out the test.

- ULTRASONIC TESTING: Longitudinal and circumferential joints will be subjected to ultrasonic sound test randomly to the extent of 2% of number of pipes for longitudinal joints and 5% of the number of circumferential joints. Necessary labour, equipment and material required shall be provided by the CONTRACTOR for carrying out the test.

- Dye penetration test on the root runs shall be carried on 100% joints after grinding before proceeding with filler runs.

- RECTIFICATION & RETESTING: Any defect noticed by radiographic / U.T shall be provided by the CONTRACTOR free of cost. The re-testing charges will be to the account of the CONTRACTOR.

  - HYDRAULIC TESTING OF PIPELINE

Each pipe shall be hydraulically tested after the pipe is internally cement mortar lined / externally coated in accordance with AWWA M11. Water required for testing shall be arranged by the BIDDER at his own cost.

All the longitudinal and circumferential welded seams shall be subjected to chalk and kerosene test prior to hydraulic testing of the complete pipe line. This shall be done in the presence of the Owner. In addition to this, test coupons shall have to be provided for each longitudinal seam for mechanical tests (tensile and bend), if considered necessary by the Owner. The test coupons are to be broken in presence of the Owner. Bidder shall satisfy the Owner that work is being carried out in accordance with the specification drawings and other conditions. Owner shall have full access to the Contractor's working area.

Testing shall be done before backfilling & under dewatered condition. However, the bidder shall backfill & compact the soil in the region of bends to avoid undue thrust on the anchor blocks. Any temporary arrangements that may be required to ensure stability of pipeline are also deemed to have included in the quoted rate.

The hydraulic test pressure is usually applied for a period of 24 hours before the test is assumed to begin, primarily to allow for the lining material to absorb as much water as is possible. After that the pipeline should be inspected for evidence of leakage.

  - BACKFILLING OF PIPE LINE TRENCHS:

This section covers specification for the work consists of backfilling the pipeline trenches with selected soil from excavated/selected soil from borrow area in layers of 150mm thickness including watering and compacting the backfill to the desired compaction etc., complete with all leads and lifts.

All fill material will be subject to OWNER’s approval. If any material is rejected by OWNER, Bidder shall remove the same forth with from the site at no extra cost. Surplus fill material shall be deposited / disposed off as directed by OWNER after the fill work is completed.

No earth fill shall commence until surface water discharges and streams have been properly intercepted or otherwise dealt with as directed by OWNER.

Material to the extent available, selected surplus soils from excavated materials shall be used as backfill. Fill material shall be free from clods, salts, sulphates, organic or other foreign material. All clods of earth shall be broken or removed. Where excavated material is mostly rock, the boulders shall be broken into pieces not larger than 150mm size, mixed with properly graded fine material consisting of murum or earth to fill up the voids and the mixture used for filling.

If any selected fill material is required to be borrowed, Bidder shall make arrangements for bringing such material from outside borrow areas. The material and source shall be subject to prior approval of OWNER. The approved borrow area shall be cleared of all bushes, roots of trees, plants, rubbish etc., top soil containing salts / sulphate and other foreign materials. The materials so removed shall be burnt or disposed off suitably as directed by OWNER. Bidder shall make necessary access roads to borrow areas and maintain the same, at his cost, till completion of the work.

  - FILLING IN TRENCHES

After laying and testing of the pipeline and construction of valve cistern, anchor blocks, thrust blocks etc., the filling in trenches shall be commenced immediately with soft selected excavated materials. This shall be done without any delay. The materials shall be laid, adequately watered and tamped in layers of 23 cms with a small tamper under, around and over the pipes and specials upto the original ground level taking due care that no damage is caused to the pipes, specials, structures etc. The compaction shall comply with the specified density at moisture content, differing not more than 4% from the optimum moisture content. The Contractor shall arrange for sampling and testing of the filling as directed by the Owner to ascertain whether specified density has been achieved. The cost of all such sampling and tests shall be borne by the Contractor and is deemed to be included in the rates quoted.

Filling of the trenches shall be carried simultaneously on both sides of the pipe to avoid unequal pressure on the pipe. Backfill shall not be dropped directly upon or against any structure / facility where there is a danger of displacement or damage. Trucks or heavy equipment for depositing or compacting backfill shall not be used within 1.5m of head walls, piers or other facilities which may be damaged by their weights or operation method of compaction. The method of depositing and compacting backfill shall be approved by owner.

SECTION -8 DRAWINGS

| No. | Description | Drawing No. |
| --- | --- | --- |
| a. | Index Map of Channagiri Tank Filling Scheme |  |
| b. | Schematic Drawing Showing the Components of the scheme |  |

SECTION - 9 BILL OF QUANTITIES

(Schedule B)

##### BILL OF QUANTITIES (SCHEDULE – B)

Name of work: “Survey, Investigation, design, Supply, Installation, Testing and Commissioning of Lift Irrigation system (Head Works consisting of Intake canal, Jack well cum pump house, Power supply including substations and Transmission lines, Rising Main including Thrust Block, Valve Chambers,  Delivery chamber, approach roads  etc) to Filling up of Kogaluru percolation tank coming under minor irrigation department from Kogaluru tank in Channagiri Taluk Davanagere  District on Turn-key basis”

| Sl. No. | Description of item | Total lumpsum contract price in Crores |
| --- | --- | --- |
| 1 | “Survey, Investigation, design, Supply, Installation, Testing and Commissioning of Lift Irrigation system (Head Works consisting of Intake canal, Jack well cum pump house, Power supply including substations and Transmission lines, Rising Main including Thrust Block, Valve Chambers, Delivery chamber, approach roads etc) to Filling up of Kogaluru percolation tank coming under minor irrigation department from Kogaluru tank in Channagiri Taluk Davanagere District on Turn-key basis” | 400.83 |
|  | Total for Work Portion = | 400.83 |
|  | GST = | 72.15 |
|  | Grand Total = | 472.98 |

Note:

- Quoted price shall not include the charges payable towards power supply / deposits to be paid to HESCOM.

PRICE BREAKUP AGAINST QUOTED LUMPSUM PRICE FOR CIVIL WORKS

| Item No. | Description of Item | Amount in figure | Amount in words |
| --- | --- | --- | --- |
| 1 | : “Survey, Investigation, design, Supply, Installation, Testing and Commissioning of Lift Irrigation system (Head Works consisting of Intake canal, Jack well cum pump house, Power supply including substations and Transmission lines, Rising Main including Thrust Block, Valve Chambers, Delivery chamber, approach roads etc) to Filling up of Kogaluru percolation tank coming under minor irrigation department from Kogaluru tank in Channagiri Taluk Davanagere District on Turn-key basis” |  |  |
|  | Total for Work Portion = |  |  |
|  | GST = |  |  |
|  | Grand Total = |  |  |

Note:-

  - Tenderer to submit detailed breakup of price in support of lump sum quoted as above.

| Item No. | Description of Item | Amount in figure | Amount in words |
| --- | --- | --- | --- |
| 2 | Supply of recommended spare parts for all equipment’s, required for 5 years operation and maintenance. |  |  |
|  | Total for Work Portion = |  |  |
|  | GST = |  |  |
|  | Grand Total = |  |  |

Note:-List of spares with price breakup sheet to be enclosed.

| Item No. | Description of Item | Amount in figure | Amount in words |
| --- | --- | --- | --- |
| 3 | Price for technical manpower required for operation of substation, pumping machinery for a period of 5 years. |  |  |
|  | Total for Work Portion = |  |  |
|  | GST = |  |  |
|  | Grand Total = |  |  |

Note:-

    - Tenderer to select pump as described in specifications based on their design.

    - Tenderer to liason with CEIG for getting their approval & other statutory approval up to the stage of commissioning of the system on behalf of KNNL.

    - The technical specifications given under Section-6 for electrical, mechanical and civil works may generally be followed. However all works shall be carried out as per PWD hand book / Irrigation manual, Indian standards, Inspectorate of Electrical code and rule, and as directed by Engineer-in-charge.

    - The amount should be quoted both in words and in figures in ink only.

    - The break up cost of various components given by bidder along with schedule ‘B’ shall be subject to

approval or such changes as deemed appropriate by KNNL for the purpose of intermediate payments

    - Tenderer to submit detailed BOQ with price breakup in support of lump sum quoted above for Kogaluru Tank Filling Scheme.

    - The lumpsum price shall be excluding GST and including royalty charges, cess and other statuory recoveries, Quoted Price shall also include necessary fire extinguisher, first aid box, danger boards, shock. Treatment charts one set and fire buckets as required. Quoted price shall also include the charges towards satisfactory O & M of Entire Pipe Distribution network for a period of 5 years from the date of successful commissioning of entire system.

    - Electrical supply shall be arranged through KPTCL from nearby source, tenderer shall prepare his design based on this data.

    - Tenderer to liaison with KPTCL regarding power supply requirement by submitting necessary drawings getting their approval& and other statutory approval up to the stage of commissioning of electrification on behalf of KNNL.

    - The technical specifications given under section for electrical, mechanical and civil works may be generally followed. However all works shall be carried out as per PWD hand book, Indian standards inspectorate of electrical code and rule and as directed by engineer-in-charge.

    - The amount should be quoted both in words and in figures in INR only.

    - The break up cost of various components of the scheme given by bidder along with price breakup (schedule ‘B’) shall be subject to approval or such changes as deemed appropriate by KNNL for the purpose of intermediate payments.

    - Tenderer to liason with CEIG for getting their approval & other statutory approval up to the stage of commissioning of the system on behalf of KNNL.

##### PRICE BREAKUP AGAINST QUOTED LUMPSUM PRICE

| Item No. | Description of Item | Amount in figure | Amount in words |
| --- | --- | --- | --- |
| 1. | Pumping Machinery and Pump house electrical works. |  |  |
| 2. | Design supply, installation, testing and commissioning of Electrical sub station. Construction of Terminal Bay at existing KPTCL substation, Erection of Transmission line & Crop compensation, Land compensation for Transmission |  |  |
| 3. | Construction of Intake canal, Forebay & Jack well cum pump house |  |  |
| 4. | Construction of Approach Road |  |  |
| 5. | Detailed Engineering consisting of detailed designs and working drawings for Jack well cum pump house, design of electrical works, (1.0% of the estimated cost). |  |  |
| 6. | Operation and Maintenance of the Scheme for 5 years |  |  |
| TOTAL |  |  |  |

MECHANICAL WORKS:-

| Mechanical works | Ex-works price per unit | Freig ht | GS T | Packin g forward ing | Insuran ce | Cost of one set | Erecti on price + GST | Price per set | Quant ity | Amou nt |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 |
| Pumps and motors |  |  |  |  |  |  |  |  |  |  |
| Valves |  |  |  |  |  |  |  |  |  |  |
| Mechanical supports/disconnecting joints |  |  |  |  |  |  |  |  |  |  |
| MS Manifold and piping suction and delivery (inside pump house) |  |  |  |  |  |  |  |  |  |  |

ELECTRICAL WORKS INSIDE PUMPHOUSE

| Electrical works inside pump house | Ex- works price per unit | Freight | GST | Packing forwarding | Insurance | Cost of one set | Erection price + GST | Price per set | Quantity | Total Amount |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 |
| 1.a)HT panel b)Powerfactor capacitors c) HT soft starters |  |  |  |  |  |  |  |  |  |  |
| 2.HT cable (incoming) |  |  |  |  |  |  |  |  |  |  |

| Electrical works inside pump house | Ex- works price per unit | Freight | GST | Packing forwarding | Insurance | Cost of one set | Erection price + GST | Price per set | Quantity | Total Amount |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 |
| 3. HT cable(pump feeder) |  |  |  |  |  |  |  |  |  |  |
| 4.Earthing |  |  |  |  |  |  |  |  |  |  |
| 5.Auxiliary transformer |  |  |  |  |  |  |  |  |  |  |
| 6.MV switch board |  |  |  |  |  |  |  |  |  |  |
| 7.LT cabling feeders for crane, battery charger etc., |  |  |  |  |  |  |  |  |  |  |
| 8. Battery charger with set of battery |  |  |  |  |  |  |  |  |  |  |
| 9. DC distributory board |  |  |  |  |  |  |  |  |  |  |
| 10. Remote control panel |  |  |  |  |  |  |  |  |  |  |
| 11. Miscellaneous electrical works |  |  |  |  |  |  |  |  |  |  |

ELECTRICAL WORKS – SUB-STATION :

| Electrical works – sub-station | Ex- work s price per unit | Freig ht | GST | Packing forwarding | Insurance | Cost of one set | Erection price + GST | Total price per set | Quantity | Amount |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 |
| (i) Sub-station equipments |  |  |  |  |  |  |  |  |  |  |
| a)Power transformer with OLTC and accessories capacity----------- MVA |  |  |  |  |  |  |  |  |  |  |
| c)SF6 circuit breaker |  |  |  |  |  |  |  |  |  |  |
| e) GOS quantity |  |  |  |  |  |  |  |  |  |  |

| Electrical works – sub-station | Ex- work s price per unit | Freig ht | GST | Packing forwarding | Insurance | Cost of one set | Erection price + GST | Total price per set | Quantity | Amount |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 |
| f) CTs/PTs quantity |  |  |  |  |  |  |  |  |  |  |
| g)VCBS quantity |  |  |  |  |  |  |  |  |  |  |
| h)Control and relay panel |  |  |  |  |  |  |  |  |  |  |
| i)Out door structure quantity(MT) |  |  |  |  |  |  |  |  |  |  |
| j)Station earthing LOT |  |  |  |  |  |  |  |  |  |  |
| k)Control cables LOT |  |  |  |  |  |  |  |  |  |  |
| l)Lightning arrestors sets |  |  |  |  |  |  |  |  |  |  |
| m)Battery and battery charger |  |  |  |  |  |  |  |  |  |  |
| n)Yard lighting |  |  |  |  |  |  |  |  |  |  |
| o)Testing and commissioning |  |  |  |  |  |  |  |  |  |  |

# SECTION-10

FORMS OF BANK GUARANTEE FOR SECURITY DEPOSIT

BANK GUARANTEE FOR SECURITY DEPOSIT

To

The Executive Engineer

Address : KNNL, No 5 Bhadra Canal Division, Davanagere.

WHEREAS (Name and Address of Contractor)................................

**(thereinafter called “the Contractor”) has undertaken in pursuance of	Tender Notification/contract

No.	dated	to Tender/execute (Name of contract and brief description

of	works)...............................	..............................................................................................called	“The

Contract”.

AND WHEREAS it has been stipulated by you in the said contract that the contractor shall furnish you with a Bank guarantee by a Nationalised Schedule bank for the sum specified therein as Earnest Money Deposit/Security Deposit for compliance with his obligations in accordance with the contract:

AND WHEREAS we have agreed to give the contractor such a Bank Guarantee:

NOW THEREFORE we hereby affirm that we are the Guarantor and responsible to you, on behalf of the Contractor, upon a total of (Amount of Guarantee)..Rs...................................(in words)

Rupees	and we undertake to pay you, upon your first written demand and

without cavil or argument any sum of sums within the limits of (Amount of Guarantee).	as

aforesaid without your needing to prove or to show grounds or reasons for your demand for the sum specified therein.

We hereby waive the necessity of your demanding the said debt from the Contractor before presenting us with the demand.

We further agree that no change or addition to or other modification of the terms of the Contract or of the work to be performed hereunder or for any of the contract documents which may be made between you and the contractor shall in any way release us from any liability under this guarantee, and we hereby waive notice of any such change, addition or modification.

This Guarantee is valid until the date......................../60 days after the issuing of the Defect Liability Certificate.

SIGNATURE AND SEAL OF THE GUARANTOR..

(Name and Designation)

Place :	Name of Bank.................................................

Date:	Address.......................................................... WITNESS

      - ......................................................

      - ………………………………………

# SECTION- ANNEXURES

ANNEXURE III – G. O. NO. PWD / II / GMS / 64, dated 10.03.1996

Sub	:	Deduction of Shrinkage of settlement in earthwork embankment.

Ref	:	Correspondence ending with the letter No. BRP/EBR/TE-77/TA-4 dated 11th November 1965 from the Chief Engineer, Irrigation Project, Bangalore.

PREMABLE :4

The Chief Engineer, Irrigation Project has reported that there was no uniform practive of standard vouge for deduction for deduction for settlement in earth work embankment and that it was discussed in the meeting of Chief Engineers held in 1961 who have made certain recommendations. The recommendations on receipt in government were examined and Government asked Chief Engineer, Irrigation project to obtain report in the matter. Then the matter, has been referred to the Director, Karnataka Engineering Research Station, K.R. Sagar for conducting experiments on various types of the embankments and under various condition in order to take decision on the uniform procedure to be adopted in making deductions for shrinkage settlement in earthwork embankments. The Director Karnataka Engineering Research Station has made the following recommendations

| Sl. | Type of Embankment | Settlement in percent of height of bank |  |  |  |
| --- | --- | --- | --- | --- | --- |
|  |  | Before Monsoon | After Monsoon | After second Monsoon | After third Monsoon |
| 1 | 2 | 3 | 4 | 5 | 6 |
| 1 | Dry unrolled embankment in clay soil including black cotton soils | 25 | 12.5 | 6.5 | Nil |
| 2 | Dry unrolled embankment in all soils other than clayey soil | 15 | 10 | 5 | Nil |
| 3 | Compacted embankments without field control of placement |  |  |  |  |
| a) | Manual labour or rollers less than six tonnes | 15 | 7.5 | Nil | Nil |
| b) | By power rollers of more than six tonnes | 10 | 5 | 2.5 | Nil |
| 4 | Compacted embankment with field control placement | 5 | 2.5 | Nil | Nil |

The Matter was further referred to the Board of Chief Engineer for consideration and opinion. The board holds that the recommendations of Director are based on generalization and are indication of general trends in different types of soils. However, soil differs from place to place and it is desirable that actual tests are carried out and averages applied in individual cases. Where it is not possible to carry out the individual experiments the general values may be adopted.

ORDER NO. PWD / II / GMS / 64, BANGALORE DATED 10TH MARCH 1996

After considering all aspects of the case and also the opinion furnished by the Board of Chief Engineers, Government hereby directs that in respect of all important bank works actual tests are carried out and average applied and where it is not possible to carry out individual experiment the values given by the Director, K.E.R.S. as noted in the preamble may be adopted.

By Order and in the Name of the Government of Karnataka

(M.CHANNAPPA)

Deputy Secretary to Government P.W.D . KA/BG-GPO/2515/WPP-47/2006-08

ANNEXURE – IV

GOVERNMENT CIRCULAR REGARDING CONTROLLED BLASTING-I

No.ID 40 KBN 98	Karnataka Government Secretariat,

M.S.Building, Bangalore, dated 13.10.1998.

C I R C U L A R

Sub:-Guidelines for resorting to Controlled Blasting in excavation item applicable to allIrrigation Projects.

***

- Controlled blasting for hard rock excavation is normally adopted in situations where human habitation, permanent structures etc. have to be protected during blasting of hardrock.

- The Managing Director, Krishna Bhagya Jala Nigam Ltd., has requested to communicate guidelines to be followed while resorting to controlled blasting. Since there is a need to prescribe a uniform standard for resorting to controlled blasting applicable for all Irrigation Projects in the State, the Technical Advisory Committee was requested to advisethe Irrigation Department in this regard.

- This subject was discussed by the Technical Advisory Committee in the meeting held on

15.9.98 by inviting some experts in the field and after detailed discussion the Committee recommended that circular instructions may be issued by the Irrigation Department in this regard which would be applicable for all Irrigation Projects in the State.

- Hence, the following guidelines are issued for resorting to controlled blasting in excavation items in Irrigation Projects based on the advice of the Technical Advisory Committee.

  - The Chief Engineer should certify and authorise taking up of controlled blasting after considering the ground realities like vicinity of human habitation, actual safe distance and also financial implications of alternatives available such as cost of shifting/compensation to owner of permanent structures of acquisition of structures etc. The Executive Engineer should certify that he has examined all other alternatives and is of the opinion that controlled blasting is more economical and is the safest way of executing the work. The Executive Engineer should furnish a repot to the Chief Engineer along with a sketch (to scale) of the number of human habitation, public/private property, cost of these structures etc., while submitting his recommendation to the Superintending Engineer/the Chief Engineer. The financial implication of controlled blasting and alternatives should be explained in the report. Thereafter the Chief Engineer should consider and approve further course of action. The detailed blasting procedure for controlled blasting should be prepared by the Executive Engineer and got approved by the Chief Engineer before implementation and these details should be incorporated under “Detailed Specifications” in the tender schedules also:

  - Before resorting to controlled blasting, it is obligatory on the part of the Executive Engineer to get the authorisation from the concerned Chief Engineer to take up the controlled blasting;

  - Controlled blasting may be proposed, wherever necessary, keeping in view the danger zone of 300 m radial distance from the blasting site to the village limit, human habitation, permanent structures and the like;

  - Controlled blasting may also be proposed for a distance of 50 m on either side ofthe power transmission line. This should be done after necessary clearance from

K.E.B. and only if K.E.B. disagrees to disconnect or shift the transmission line for a short period;

  - Field Officers must ensure that the Agencies/contractors, during excavation of canal, should not resort to rig blasting wherever controlled blasting is resorted to;

  - The depth upto which controlled blasting is to be done, shall be decided by the Chief Engineer keeping in view the site specifies like nature of rock, stratification, cross section of the canal etc.

The above guidelines and procedure should be followed strictly while resorting to controlled blasting for excavation items in respect of all the Irrigation Projects in the State.

Sd/- (L.BASAVARAJU)

Secretary to Government,Irrigation Department.

ANNEXURE – V

GOVERNMENT CIRCULAR REGARDING CONTROLLED BLASTING-II

GOVENRMENT OF KARNATAKA

No.WRD 58 KBN 2004	Karnataka Government Secretariat, M.S.Building,

Bangalore, dated 29.07.2004

C I R C U L A R

Sub:- Guidelines for resorting to Controlled Blasting in excavation item applicable to all Irrigation Projects.

Ref:	1) Circular No.ID.40 KBN 90, dated 13.10.98.

2) Letter No.SE/M & E/ SRC / AEE-2 / 03-04 / 1127, dated 10.07.2003 and N o . 893-94, dated 2.7.2004.

****

Controlled blasting for hard rock excavation is normally adopted in situations where human habitation, permanent structures etc. have to be protected during blasting of hard rock.

The Managing Director, Krishna Bhagya Jala Nigam Ltd., has requested to communicate guidelines to be followed while resorting to controlled blasting. Since there is a need to prescribe a uniform standard for resorting to controlled blasting applicable for all Irrigation Projects in the State, the Technical Advisory Committee was requested to advisethe Irrigation Department in this regard.

This subject was discussed by the Technical Advisory Committee in the meeting held on

15.9.98 by inviting some experts in the field and after detailed discussion the Committee recommended that circular instructions may be issued by the Irrigation Department in this regard which would be applicable for all Irrigation Projects in the State.

Now S.R Committee has suggested to modify para (V) of the circular dated 13.10.98 videref (2) above.

Hence, the following modified guidelines are issued for resorting to controlled blasting in excavation items in Irrigation Projects based on the advice of the S.R Committee constitutes under the chairmanship of Caption Rajarao, Retired Secretary:-

- The Chief Engineer should certify and authorise taking up of controlled blasting after considering the ground realities like vicinity of human habitation, actual safe distance and also financial implications of alternatives available such as cost of shifting/compensation to owner of permanent structures of acquisition of structures etc. The Executive Engineer should certify that he has examined all other alternatives and is of the opinion that controlled blasting is more economical and isthe safest way of executing the work. The Executive Engineer should furnish a repot to the Chief Engineer along with a sketch (to scale) of the number of human habitation, public/private property, cost of these structures etc., while submitting his recommendation to the Superintending Engineer/the Chief Engineer. The financial implication of controlled blasting and alternatives should be explained in the report. Thereafter the Chief Engineer should consider and approve further course of action.The

detailed blasting procedure for controlled blasting should be prepared by the Executive Engineer and got approved by the Chief Engineer before implementation and these details should be incorporated under “Detailed Specifications” in the tender schedules also:

- Before resorting to controlled blasting, it is obligatory on the part of the Executive Engineer to get the authorisation from the concerned Chief Engineer to take up the controlled blasting;

- Controlled blasting may be proposed, wherever necessary, keeping in view the danger zone of 300 m radial distance from the blasting site to the village limit, human habitation, permanent structures and the like;

- Controlled blasting may also be proposed for a distance of 50 m on either side ofthe power transmission line. This should be done after necessary clearance from the concerned electricity supply companies and only if these companies disagrees to disconnect or shift the transmission line for a short period;

- Field Officers must ensure that the Agencies/contractors, comply with the following safety requirements for excavation of canal by controlled/normal blasting techniques.

    - Trial studies shall be conducted to fix up the drilling and blasting parameters to controlground vibration and fly rock problem within permissible safety limits.

    - Number of holes to be blasted at a time shall be limited as per trail study recommendations.

    - Safer and effective explosive devices such as electric delay detonator for jack hammer holes, shock tube detonators and trunk line delays for wagon drill holes shall be used to control ground vibrations and fly rocks.

    - Blast area shall be covered by chain link wire mesh and sand bags to avoid fly rock.

    - Whenever and where control blasting is approved, monitoring and recording of noise levels and vibration levels must be insisted and a record should be kept to confirm thatthe levels were within the permissible limits.

The above requirements are to be included in the contract specifications for excavation in hard rock.

- The depth upto which controlled blasting is to be done, shall be decided by the Chief Engineer keeping in view the site specifies like nature of rock, stratification, cross section of the canal etc.

The above guidelines and procedure should be followed scrupulously during controlled blasting for excavation items.

Sd/- (S.J.CHANNABASAPPA)

Secretary to Government, Water Resources Department.

ANNEXURE -VI – G. O. FD 59 PRO, CELL 2004, dated 26.11.2004

Subject: Procurement Reforms- Provision for price Adjustment Clauses in the tender documents.

Preamble:

In the country Procurement Assessment Reports prepared for the state of Karnataka, the World Bank has made a set of recommendations for Price Adjustment Reforms. One such recommendation in the Price Adjustment should be mandated in respect of all contracts of value more than Rs. 20 lakhs and completion period of more than 18 months and it should be made applicable from the date of opening tenders.

The state Government has examined the Recommendations. After considering all aspects in the matter, the Government issues following orders.

ORDER NO. No. FD 59 PRO, CELL 2004, BANGALAORE DATED26th NOVEMBER 2004

- In super-session off standing Rules and instructions, in respect of Price Adjustment Clause in the tender documents, the following instructions are issued for compliance.

  - A Price Adjustment Clause shall be included in all works contracts whose estimated cost put to tender is Rs. 100 lakhs or more and the period of completion is 12 months or more. The Price Adjustment Clause and the formulae for adjustment shall be as per Annexure-I.

  - In works contract where, Price Adjustment Clause is provided, the Price Adjustment shall be admissible from the date of opening of tender (Original or extended)

  - Price Adjustment Clause shall not be included in goods and Equipment tender documents. However in respect of tender documents for procurement of Electric cables, Transformers, generators, motors, that have raw material component subject to price fluctuations, appropriate Price Adjustment clauses may be incorporated by the Tender Inviting Authority in the tender documents, with the specific approval of the concerned Head of the Department of Managing Director of the Public Undertaking / Board.

- The above instructions will only be applicable prospectively and shall not be applicable for contracts concluded in the past or being concluded presently or for tenders already invited.

- The above instructions shall apply to all Procurement Entities as defined in Section 2(d) Chapter 1 of the Karnataka Transparency in Public Procurements Act, 1999.

- The above instructions should be appropriately incorporated in the Standard Tender Documents under Preparation.

By Order and in the name of Governor of Karnataka

(K.P.Pandey)

Additional Chief Secretary and Principal Secretary to Government,

Finance Department.

#### Annexure i

PRICE ADJUSTMENT CLAUSE FOR WORKS CONTRACTS

Price Adjustment:

Contract price shall be adjusted for increase or decrease in rates and prices of labour, materials, fuels and lubricants in accordance with the following principles and procedures and as per formula given hereunder.

  - The price Adjustment shall apply for the work done from the date of commencement upto the end of original period of completion or extensions granted by the Employer and shall not apply to work carried out beyond the stipulated period of completion for reasons attributable to the contractor.

  - The price adjustment shall be determined during each quarter from the formula given hereunder.

  - Following expressions and meanings are assigned to the work done during the quarter:

R= Total value of work done during the quarter. It would include the amount of secured advance for materials paid for (if any) during the quarter, less the amount of the secured advance recovered during the quarter. It will exclude value for works executed under variations for which price adjustment (if any) will be worked out separately based on the terms mutually agreed it will also exclude the value of work done during the quarter which was programmed to be done prior to this quarter as per the work schedule in the agreement.

  - To the extent that full compensation for any rise or fall in costs to the contractor is not covered by the provisions of this or other clauses in the Contract, the unit rates included in the contract shall be deemed to include amounts to cover the contingency of such other rise or fall in coasts.

Price Adjustment Formula:

Adjustment for labour component:

- Price adjustment for increase or decrease in the cost due to labour shall be paid in accordance with the following formula:

VL = 0.85 x PL / 100 x R x (Li-Lo)/Lo where,

VL= Increase or decrease in cost of work during the quarter under consideration	due to changes in rates for local labour:

Lo = The average consumer price index 2 for industrial workers for Hubli Centre for the quarter preceding the date of opening of tenders as published by the Labour Bureau, Ministry of Labour, Government of India;

Li = The average consumer price index for industrial workers for Hubli centre for the quarter under consideration as published by Labour Bureau, Ministry of Labour, Government of India;

PL = Percentage of labour component of the work.

Adjustment for Cement Component:

- Price adjustment for increase or decrease or decrease in the cost of cement component procured by the contractor shall be paid in accordance with the following formula.

Vc = 0.85 x Pc / 100 x R x (Ci-Co)/Co where,

Vc= Increase or decrease in cost of work during the quarter under consideration due to changes in rates for cement;

Co= The all India average wholesale price index for cement (Ordinary Portland cement) for the quarter preceding the date of opening of the tenders as published by the office of Economic Advisor, Ministry of Commerce and Industry, Government of India, New Delhi;

Ci = The all India average wholesale price index for cement (Ordinary Portland cement) for the quarter under consideration as published by the Office of Economic Advisor, Ministry of Commerce and Industry, Government of India, New Delhi;

Pc = Percentage of cement component of the work.

Note: For the application of this clause, index of Ordinary Portland Cement has been chosen to represent Cement group.

Adjustment for steel component:

- Price adjustment for increase or decrease in the cost of steel procured by the contractor shall be paid in accordance with the following formula.

Vs = 0.85 x Ps/100 x R x (Si-So)/So Where,

Vs = Increase or decrease in cost of work during the quarter under consideration due to changes in rates for steel;

So = The all India average wholesale price index for steel (M.S.Bars and rods) for the quarter preceding the date of opening of Bids as published by the Office of Economic Advisor, Ministry of Commerce and Industry, Government of India, New Delhi;

Si = The all India average wholesale price index for steel (M.S.,Bars and rods) for the quarter under consideration as published by the Office of Economic Advisor, Ministry of Commerce and Industry, Government of India, New Delhi;

Ps = Percentage of bitumen component of the work.

Note: For the application of this clause, index of M S bars, rods and steel plates have to be choseen to represent relevant and appropriate Steel groups.

Adjustment of Bitumen component

- Price adjustment for increase or decrease in the cost of bitumen shall be paid in accordance with the following formula:

VB = 0.85 x PB/100 x R x (Bi-Bo)/Bo Where,

VB = Increase or decrease in the cost during the quarter under consideration due to changes in the rate for bitumen.

Bo = The official retail price of bitumen at the IOC/HPCl/BPL or other depot at on the day 30 days prior to the date of opening of Bids.

B i= The official retail price of bitumen at the IOC/HPCl/BPL or other depot at for the 15th day of the middle calendar month of the quarter under consideration.

PB = Percentage of bitumen component of the work.

Adjustment of Fuel and Lubricant component:

- Price adjustment for increase or decrease in the cost of Fuel and Lubricants shall be paid in accordance with the following formula.

VF = 0.85 x PF / 100 x R x (Fi-Fu)/Fu Where,

VF = Increase or decrease in cost of work during the quarter under consideration due to changes in rates for Fuel and Lubricants;

Fu= The official retail price of High Speed Diesel (HSD) at the IOC /HPCL/BPL or other consumer pump at Bijapur on the day 30 days prior to the date of opening of Bids;

Fi = The official retail price of HSD at the IOC/HPCL/BPL or other consumer pump at Bijapur for the 15th day of the middle calendar month of the quarter under Consideration;

PF = Percentage of Fuel and Lubricant component of the work.

Note:	For the application of this clause, the price of HSD has been chosen to represent Fuel and Lubricant Group.

Adjustment for Plant and Machinery Spares component:

- Price adjustment for increase or decrease in the cost of plant and Machinery Spares Procured by the contractor shall be paid in accordance with the following formula.

Vp = 0.85 x Pp/100 x R x (Pi-Po) / PoWhere,

Vp = Increase or decrease in cost of work during the quarter under consideration due changes in rates for plants and machinery spares;

Po= The all India average wholesale price index for Heavy Machinery and Parts for the quarter preceeding the date of opening of bids, as published by the Office of the Economic

Advisor, Ministry of Commerce and Industry, Government of India, New Delhi;

Pi = The all India average wholesale price index for Heavy Machinery and Parts for the quarter under consideration as published by the office of the Economic Advisor, Ministry of Commerce and Industry, Government of India, New Delhi;

Pp = Percentage of plant and Machinery Spares component of the work (PF)

Note: For the application of this clause index of Heavy Machinery and parts 10 has been chosen to represent the plant and Machinery Spares Group.

Adjustment for Other materials:

- Price adjustment for increase or decrease in the cost of other materials other than cement, steel, bitumen and Fuel and Lubricants 11, procured by the contractor shall be paid I accordance with the following formula.

VM = 0.85 x PM / 100 x R x (Mi-Mo) / Mo Where,

VM = Increase or decrease in cost of work during the quarter under consideration due to changes in rates for local materials other than cement, steel, bitumen and Fuel & Lubricants;

Mo = The all India average wholesale aprice index for all commodities for the quarter preceding the date of opening of bids, as published by the Office of the Economic Advisor, Ministry of Commerce and Industry, Government of India, New Delhi;

Mi = The all India average wholesale price index for all commodities for the quarter under consideration as published by the office of the Economic Advisor, Ministry of Commerce and Industry, Government of India, New Delhi;

PM = Percentage of other material component (Other than cement, steel, bitumen and Fuel and Lubricants) of the work.

The following percentages will govern the price adjustment for the entire contract:

| 1. Labour – PL | % |
| --- | --- |
| 2. Cement – PC | % |
| 3. Steel – PS | % |
| 4. Bitumen – PB | % |
| 5. Fuel and Lubricants – PF | % |
| 6. Plant and Machinery Spares – PP | % |
| 7. Other Materials – PM | % |
| TOTAL | 100% |

ANNEXURE VII - G. O. NO. FD 3 PCL 2008, dated:21-11-2008

Subject: Provision for price Adjustment for specified materials for works –

Revision Reg.

Read : Govt. Order No. FD 59 PRO CELL 2004, dated:26-11-2004

Preamble :

In Government Order No. FD 59 PRO CELL 2004 dated: 26th November 2004 read above, the following instructions were issued about price adjustment.

  - A Price Adjustment clause shall be included in all Works contracts whose estimated cost put to tender is Rs.100 lakhs or more and the period of completion is 12 months or more. The Price Adjustment clause and the formulae for adjustment shall beas per Annexure-1 of the said G.O.

  - In works contracts where, Price Adjustment Clause is provided the Price Adjustment shall be admissible from the date of opening of tenders (original or extended).

  - Price Adjustment Clause shall not be included in Goods and Equipment tender documents. However in respect of tenderdocuments for procurement of electric cables, transformers, generators, motors, that have raw material component subject to price fluctuations, appropriate Price Adjustment clauses may be incorporated by the Tender Inviting Authority in the tender documents, with the specific approval of the concerned Head of the Department or Managing Director of the Public Undertaking/Board.

The PWD has requested for certain modifications in the above conditions as the Department is facing problem in procurement ofagencies for implementation of various works due to rapid fluctuation of rates of construction materials especially cement, steel and bitumen. This has resulted in poor response to the tenders floated by the department and also slowdown or stoppage of on-going works by the agencies. Further, the tender premiums being quoted by the agencies are very high which creates an opinion that the Schedule of Rates or the estimates are defective. Hence, P.W.D has requested to resolve this problem suitably by modifying the existing contract agreement to absorb the fluctuation in the market prices of major construction viz., cement, steel and bitumen.

In the procurement Reforms Standing Committee Meeting held on 2-8-2008, the proposal of PWD for effecting certain changes in the price adjustment clause in the Tender Documents was discussed in detail and considering the frequent fluctuations in the basic rates of construction materials i.e. Cement, Steel, Bitumen, it was recommended by the Committee to modify the Government Order dated: 26.11.2004 referred to above.

The Government has considered the issue in detail and accordingly the following orders are issued.

Government Order No.FD 3 PCL 2008, Bangalore, dated:21-11-2008.

In the circumstances explained in the preamble, in modification of the Government Order dated: 26-11- 2004, it is directed that the following price adjustment methods are applicable hereafter.

    - For all works costing more than Rs.50 lakhs, if the period of execution is more than 12 months, the price adjustment will be calculated as prescribed in Annexure to G.O. No: FD 59 PRO Cell/ 2004, dt: 26.11.2004.

    - If the period of execution is more than 6 months but less than or equal to 12 months for work costing more than Rs.50 lakhs, star rates in respect of specified materials (cement, steel and bitumen) only shall be payable to the contractor based on the all India average wholesale price index for the said materials. The star rates adjustment shall be as per the increase or decrease in the index as applied to the said materials between the last date for receiving bids and the date of execution as per the approved programme of works submitted by the contractor at the time of execution of agreement which shall mandatorily be a part of the agreement.

    - If the period of execution is less than or equal to 6 months, for all works irrespective of the cost of the works, price adjustment or star rates shall not be applicable.

    - In works contracts where price adjustment clause is provided, the price adjustment shall be admissible from the date of opening of tenders (Original or extended).

    - Price adjustment clause shall not be included in Goods and Equipment tender documents. However, in respect of tender documents for procurement of Electric Cables, Transformers, Generators, Motors that have raw material component subject to price fluctuations, appropriate price adjustment clausesmay be incorporated by the Tender Inviting Authority in the tender documents, with the specific approval of the concerned Head of the Department or Managing Director of the Public Sector Undertaking/Board.

  - The above mentioned methods of price adjustment clause are subject to the following conditions:

- The price adjustment clause or the star rates shall not be admissible if the contract period is extended due to lapse on the part of the contractor.

- For the cases (a) and (b) above, if the contract period is extended due to no fault of the contractor, the modified programme shall be approved by the competent authority and shall become a part of agreement for which price adjustment/star rates will be applicable.

- For the purpose of working out price adjustment and star rates, the price index issued from time to time by the Ministry of Commerce and Industry, Government of India should be adopted.

- The formulae for price adjustment shall be as prescribed in Annexure-1 to the G.O. No: FD 59 PRO.Cell/2004 dated: 26.11.2004, which is appended.

  - The above instructions will only be applicable prospectively and shall not be applicable for contracts concluded in the past or being concluded presently or for tenders already invited.

  - The above instructions shall apply to all Procurement Entities as defined in Section 2(d) Chapter I of the Karnataka Transparency in Public Procurement Act, 1999.

  - The above instructions should be appropriately incorporated in the Standard Tender Documents.

By order and in the name of the Governor of Karnataka,

Sd/-

(M.R. Sreenivasa Murthy)

Principal Secretary to Government, Finance Department

To:

The Compiler, Karnataka Gazette for publication in the next issue of the Gazette and to supply 500 copies to Finance Department

Copy to:

The Chief Secretary/Additional Chief Secretaries to Government The Principal Secretaries and Secretaries to Government

The Principal Secretary to Hon’ble Chief Minister

The Accountant General (A&E), Karnataka, Bangalore

The Secretary to Government (Expenditure), Finance Dept. The Secretary, Karnataka Legislative Assembly/Council

The Registrar, Karnataka High Court, Bangalore	With a covering letter The Registrar, Karnataka Lokayukta, Bangalore

The Secretary, Karnataka Public ServiceCommission, Bangalore() All the Deputy Commissioners

All the CEOs of Zilla Panchayats All the Heads of Departments

All the CEOs of Boards and Corporations All Internal Financial Advisors

Joint Secretaries / Deputy Secretaries / Special officers / Under Secretaries to Govt., Finance Department.

ANNEXURE VIII – G. O. NO. 791 Exp-12/2015, dated 26.02.2016

ANNEXURE IX - G.O. No. CRM 2009 dated 30.09.2010 (STAR rates)

ANNEXURE X – WATER RESOURCE DEPARTMENT CIRULAR NO. WRD/127/MBI/2020 Dated 30.05.2020 ON MOBILIZATION ADVANCE

ANNEXURE XI – PROFORMA FOR JOINT VENTURE AGREEMENT

(To be executed on Rs. 200/- Stamp paper)

JOINT VENTURE AGREEMENT By and Between:

Names of Members :

Herein after to be collectively referred to as “The Joint Venture Member”

WHEREAS the KARNATAKA NEERAVARI NIGAM LIMITED (hereinafter referred to as “PURCHASER”) has invited a tender for ““Survey, Investigation, design, Supply, Installation, Testing and Commissioning of Lift Irrigation system (Head Works consisting of Intake canal, Jack well cum pump house, Power supply including substations and Transmission lines, Rising Main including Thrust Block, Valve Chambers,  Delivery chamber, approach roads  etc) to Filling up of Kogaluru percolation tank coming under minor irrigation department from Kogaluru tank in Channagiri Taluk Davanagere  District on Turn-key basis”

WHEREAS the JOINT VENTURE MEMBERS desire by means of this agreement to establish and define their respective rights and obligations in their collaboration on the PROJECT WORK.

NOW THEREFORE in consideration of the premises and undertaking herein contained, it is HEREBY AGREED as follows:

- DEFINITIONS

In the text of this agreement, the meanings of the following works shall be as here in below defined.

“JOINT VENTURE MEMBER (s) ” : Shall mean (name of the members) individually or all them

collectively.

“JOINT VENTURE”: Shall mean the temporary collaboration of all Members relating to the PROJECT

WORK as defined in this agreement.

“CONTRACT” : Shall mean the agreement entered into between the PURCHASER and THE JOINT

VENTURE.

CONTRACT PRICE : Shall mean the particular part or parts of the PROJECT WORK for which an individual Member is to be respectively responsible and liable as more particularly described in Article 7 of this Agreement.

- OBJECTIVE:

The objective of this Agreement is to define the rules which shall govern the relationship between the JOINT VENTURE MEMBERS prior to Signature and during the performance of the contract for satisfactory execution of the PROJECT work on single responsible basis.

- NATURE OF THE JOINT VENTURE:

The legal status of the Joint venture is that of a temporary collaboration of the MEMBERS. While all the MEMBERS accept joint and several responsible and liability among themselves and to the PURCHASER for the PROJECT WORK, such joint and several liability shall not extend to other parties. The Joint Venture shall not constitute a separate legal entity nor partnership and each JOINT VENTURE MEMBER shall hear as to the other JOINT VENTURE MEMBERS and as to other third parties the individual responsibilities and liabilities by this Agreement and their respective agreements with other third parties.

- EXCLUSIVITY:

During the term of this Agreement, all the MEMBERS shall fully co-operative with each other on an exclusive basis with respect to the PROJECT WORK. No MEMBER shall submit to the PURCHASER, directly or indirectly, separately or in combination with others, any proposal related to the PROJECT WORK, nor agree to participate directly or indirectly, separately or in combination with others, in the execution of the PROJECT WORK otherwise than in accordance with this Agreement.

- OBLIGATION of EACH JOINT VENTURE MEMBER:

Each member shall be jointly and severally responsible and liable towards each other and to the PURCHASER for the execution of the PROJECT WORK in accordance with the provisions of the overall Agreement and this Agreement.

NOTWITHSTANDING the forgoing, each MEMBER shall be responsible for the execution of its Scope of works as defined in Article-7. In executing its Scope of work each MEMBER shall owe a duty to the other MEMBERS so as to ensure that all the plant, material and equipment used or provided by it is in conformity with the CONTRACT and that all the tasks undertaken by that JOINT VENTURE MEMBER is executed in a good and workman like manner.

- LEADERSHIP:

(NAME OF THE FIRM) shall act as Leader and/or Chief Co-Ordinator for the execution of the Joint Venture project work. As such, it shall act as co-ordinator of the MEMBERS combined activities (NAME OF THE FIRMS) shall carry out the functions..

- Prepare and submit the tender on the basis of the individual tenders of all Members.

- Convene the co-ordinating committee from time to time, prepare the agenda for the meetings and execute decisions taken by all the MEMBERS.

- Assume the administrative, commercial and technical coordination of the project.

- Prepare in consultation with all the members the overall schedule of completion of the PROJECT WORK on the basis of the individual schedule supplied by each MEMBER, keep such overall schedule up to date and keep all the MEMBERS informed of scheduled revisions.

- Conduct all discussion of any kind with the PURCHASER, with the assistance, when needed of the MEMBERS.

- Act as the Channel of Communication between the PURCHASER and the MEMBER, receiving and retransmitting all correspondence and communications of any sort between the PURCHASER and the Consortium Members.

- TECHNICAL RESPONSIBILITIES AND SCOPE WORK:

The technical responsibility of each member with Scope of work shall be defined in detail.

- DEFAULT:

In the event of the material default by a MEMBER in the discharge of its obligation under the CONTRACT with respect to which it fails to take reasonable corrective measures within thirty days of notice to take over the Scope of Work of the defaulting Consortium Member and may assign it to another Company after the approval of the PURCHASER and without affecting the completion schedule of the PROJECT.

- CONFIDENTIALITY:

  - The MEMBERS agree not to disclose to any third party the existence or provisions of the Agreement without the consent in writing of the other MEMBERS.

  - All plants, drawings and information of any kind disclosed in connection with this agreement or the PROJECT WORK shall be confidential vis-à-vis any third party and may not be used for any purpose other than for the execution of his Agreement. All such documents communicated to the other MEMBER shall remain the property of the MEMBER communicating the same.

- TERMS

This Agreement shall be effective as of the date hereof and shall terminate when all Contractual obligations have been entirely discharged by the JOINT VENTURE MEMBERS and all accounts differences and disputes among JOINT VENTURE MEMBERS and approved by the PURCHASER.

- AMENDMENTS:

This agreement shall not be amended or modified in any way other than by agreement in writing executed by all JOINT VENTURE MEMBERS and approved by the PURCHASER.

- GOVERNING LAW AND JURISDICTION:

This agreement shall in all respects be subject to and constructed and interpreted in accordance with the laws in force in India except any portion of such laws which would operate to exclude the applicability of Indian law. The courts at Bangalore shall have Jurisdiction.

EXECUTED on the 	by the duly authorized representatives of the parties hereto

Signature of all the Members of the Joint

Venture

Witness:

1.

2.

ANNEXURE XII – CIRCULAR FD 455 Exp-12/2020 dated 29.03.2021

ANNEXURE XIII – G. O. No. FD 455 Exp-12 2020 dated 25.08.2020

ANNEXURE XIV – CIRCULAR FD-CAM/16/2022(P-2) dated 22.08.2022

ANNEXURE XV – G. O. NO. FD 55 Pro Cell 2004 dated 17.02.2005

Sub: Third Party Inspection of Works, Goods and Equipment Preamble:

- There are no specific provision regarding Inspection of Works in the Karnataka Public Works Department Manual, Clauses 12 (b) and (c) of the PWG 65.  the approved tender document

for works, lay down the Guidelines for inspection of Works. The contractor is primarily responsible to ensure that the works are executed as per specifications and deliver the Works is sound condition. The Departmental Officers have to make periodical checks to ensure the quality of works. The Government is concerned over the deterioration in he quality of the works executed. To assist the Departmental Officers to ensure quality works, in some major projects separate in-house quality control organizations have been set up and in some other projects funded by international Donor 133 Agencies, Supervision Consultants have been employed. However for most of the works under execution, the Departmental Officers (here- in-after called Employer) and responsible for ensuring the quality of the works.

- Similar is the position in respect of procurement of goods and equipment. The inspection is mostly in-house. In some PSUs third party inspections are adopted on a case-by-case basis and there is no consistency and uniformity of approach.

- Complaints regarding acceptance of poor quality of works and procurement of goods and equipment not conforming to stipulated specifications continue to be reported.

- The Sub-Committee under the Chairmanship of Secretary PWD, constituted by Government vide No. PWD 122 SO/FC 2003, Bangalore dated 8.5/2003 to examine and make recommendations regarding various aspects of Procurement Reform in the State examined the measures to improve quality control of works, inspection of goods and equipment and has made recommendations for improvement of Quality Control. The Working Group constituted vide GO No. PWD 1359 SO/FC 2001 dated 14/8/2002 reviewed and endorsed the recommendations of Sub-Committee. The standing Committee for Procurement Reforms Action Plan based on CPAR. Karnataka constituted vide GO No. PWD 1359 SO/FC 2001 dated 5/8/2002 examined the recommendations in detail.

- Third party inspection of Works and Supplies would ensure adherence to quality standards, leading to value for money. This will also check corruptive practices and instill public confidence in the system.

Government Order No. FD 55 Pro. Cell 2004, Bangalore, Dated: 17.02.2005

Based on the recommendations of the Standing Committee the following orders are issued.

  - The appointment of independent third Party Inspectors designated quality supervision Consultants would go a long way in assisting the Departmental Officers to ensure adherence to quality standards in construction works and procurement of goods and equipment;

  - Third party Inspection shall be mandatory in respect of all works contracts of estimated value more than Rs. 2 crore and all goods and equipment contracts estimated to cost more than Rs. 25 lakhs for an item of goods and equipment;

  - Reputed Quality Supervision Consultants (either Individual of Firm) known for integrity and professionalism should be appointed by following the procedures for procurement of Consultancy services issued vide Go No. PWD 121SO/Fc 2003, Bangalore dated 26/9/2003 with amendments issued from time to time thereof. The terms of Reference should be well defined. Detailed Checklists, to be completed by the Quality Supervision Consultants, should be prepared ( with the assistance of experts if need be) to ensure that the consultants perform their obligations satisfactorily;

  - The employment of the Quality Supervision Consultants could be either for one or more contracts for works or procurement or goods and equipment or for procurement made in a term or stipulated period for a procurement Entity.

  - Heads of the Department of the Government Managing Directors of PSUs Boards/ Societies Local Bodies Shall employ the Quality Supervision Consultants and order payments to them on satisfactory performance. The expenditure on the employment of the quality Supervision Consultants shall be charged to the cost of the works and goods and goods and equipment under procurement;

  - The quality Supervision consultant shall inspect the works periodically, submit reports along with the prescribed checklists duly completed to the employer for taking action with a copy to the Secretary to the Government Managing Director of the Corporation/Board/ Society/Local body. Who will be responsible for review of the Action Taken Reports of the Employer;

  - The quality Supervision consultant shall inspect the goods and equipment during manufacture/before dispatch after receipt, assembly and commissioning as per the terms of the contract and submit reports along with prescribed checklists duly completed to the purchaser with a copy to the Secretary to the Government/Managing Director of the Corporation Board Society/Local body who will be responsible for Review of the Action Taken Reports of the Purchaser;

  - The employment of the quality Supervision Consultant and the inspections conducted by them shall not absolve the primary responsibility of the employer to ensure completion of works of sound quality as per stipulated specifications and of Purchasers for Procurement of goods and equipment of good quality as per stipulations in the specifications. The quality Supervision Consultants are there to assist the Employer/ Purchaser in discharging their primary responsibility.

  - The quality Supervision Consultants should not be employed in respect of works and goods and equipment contracts of projects, where a specialized in house quality Control Organization exists is planned or a separate Supervision Consultant has been employed.

    - This order will apply prospectively and will not be applicable for contracts concluded in the past or for tenders already invited.

    - This order shall apply to all Procurement Entities as defined in Section 2 (d) of Chapter 1 of the KTPP Act, 1999

    - This order shall be appropriately incorporated in the Special Conditions of Contract of the Tender documents.

    - The contents of this order are appropriately incorporated in the Karnataka Public works Department and other Manuals.

By Order and in the name of the Governor of Karnataka

(Sudhakar Rao)

Principal Secretary to the Government Finance Department

# SECTION – 11 ADDITIONAL ANNEXURES

Annexure

##### DATA SHEETS FOR KOGALURU TANK FILLING SCHEME

TECHNICAL PARTICULARS OF PUMPS OFFERED

| I | EQUIPMENT AND SERVICES OFFERED |  |  |
| --- | --- | --- | --- |
| 1 | Pump as per specification | YES/No |  |
| 2 | Motor or the prime mover | YES/No |  |
| 3 | Necessary instruments, test connections | YES/No |  |
| 4 | Foundation bolts | YES/No |  |
| 5 | Base plate | YES/No |  |
| 6 | Companion flanges | YES/No |  |
| 7 | Suction strainer | YES/No |  |
| 8 | Prefabricating tank with Accessories | YES/No |  |
| 9 | Spare parts | YES/No |  |
| 10 | Maintenance & Special erection tools | YES/No |  |
| 11 | Pump set Erection and Commissioning | YES/No |  |
| 12 | Operation & Maintenance | YES/No |  |
| II | PERFORMANCE GUARANTEE |  |  |
| 1 | Manufacture's name |  |  |
| 2 | Type of pump offered |  |  |
| 3 | Number of pumps offered |  |  |
| 4 | Maximum Capacity of each pumps |  |  |
| 5 | Rated capacity of each pump |  |  |
| 6 | Maximum head in meter |  |  |
| 7 | Duty point parameters |  |  |
|  | a. Specified head without losses | : | m |
|  | b. Friction loss in Column assembly | : | m |

- Discharge head loss	:	m

- Suction loss + any other applicable

headloss component	:	m

- Bowl assembly head

- Bowl input power in KW

- Line shaft loss in KW

- Thrust bearing loss in KW & any otherapplicable power loss component

- Power input to Pump in KW

- Minimum guaranteed pump efficiency at specified duty point

- Minimum guaranteed motor efficiency at specified duty point

- Power input to Motor in KW at specified Duty point (For evaluation purpose)

- Range of het:1d at which the pump can work

- Pump losses at rated capacity

- Discharge head at rated capacity

- Maximum head developed by pump.

- Shut off head

- Pump speed in RPM

- Critical speed

- Efficiency at rated capacity.

- Range/head curve enclosed.

- Power requirement at rated capacity in KW

- Transmission & thrust bearing losses in KW

- Bearing cooling water, required in m3/hr

- Quantity & pressure in Kg/cm2

- Number of stages

- Type of Impeller

- Dimension of impeller

- Weight of impeller

- Clearance between impeller and bowl

- Size of the suction bed Whether intake strainer provided

- Type of coupling offered

- Type of drive transmission

- Type of stuffing box sealing offered

- Location of Thrust Bearing

- Hydraulic thrust load on thrust bearing

  - at duty point

  - at shut-off condition

- Type of pump lubrication

- Non reversible rachet provided

- Diameter of the water column in mm

- Size of suction bell in mm

- Discharge pipe in mm

- Flange drilling standard

- Height at which discharge elbow is provided

- Whether dimension drg, Furnished

- Peak value of the vibration of the pump motor assembly,

- Peak value of the noise level of the assembly

- Vertical load particulars

- Wt. of Pump only in (Dry) Kgs

- Wt. of water column in Kgs.

- Wt. of Pump with water in _gs

- Wt. of Motor in Kgs.

- Wt. of Pump motor assembly (Dry) in Kgs.

- Vertical Dynamic load of Pump assembly with applicable tolerance.

- Total Vertical dyn. Load of Pump & motor assembly with applicabletolerance.

- Unbalanced dyn. Force at ratedhead & rated discharge.

- Point & direction of action of hydraulic thrust (to be furnished in the form of sketch)

- Hydraulic thrust load

- at duty point

- at shut-off condition.

- Place where the performance test of the equipment carried out

      - III	DELIVERY PIPE & MANIFOLD

  - Manifold details

    - Overall size ( L X B)

    - Type of steel used

    - Type of construction

    - Test pressure and duration

    - Type of coating used to reduce corrosion and also friction

    - Type of coating on the outside

    - Type of welding

    - Type of weld tests proposed tobe carried out

  - Before Manifold

- No. of runs

- Inner diameter

- Thickness of plate

- Type of steel used

- Design velocity

- Test pressure & duration

- Type of coating used to reducecorrosion ,& also friction.

- Type of coating on the outside

- Type of welding

- Type of weld tests proposed to be carried out

- Total length

  - After Manifold

- No. of runs,

- Inner diameter

- Thickness of plate

- Type of steel used

- Design velocity

- Test pressure & duration

- Type of coating used to reduce corrosion & also friction.

- Type of coating on the outside

- Type of welding

3	Type of weld tests proposed to be carried out

      - IV	MATERIALS OF CONSTRUCTION

- Base plate

- Discharge elbow/discharge head

- Column pipe

- Suction bell

- Impeller bowl

- Discharge casing

- Impeller

- Impeller wearing rings

- Head Shaft

- Line Shaft

- Impeller Shaft

- Shaft couplings

- Line bearings

- Suction strainer

- Stuffing Box

- Shaft sleeves

      - V	TEST AND INSPECTION

1	Inspection and test certificates as per - specification will be furnished

VI	DRAWINGS

      - Drawings to be submitted for approval of KNNL.

      - VII	DIMENSIONS

      - VIII	OTHER DETAILS

Maximum duration for which pump can be operated under

- Shut off condition

- Failure of bearing lubrication and cooling system

SEAL	SIGNATURE	:

DESIGNATION : COMPANY	:

DATE	:

TECHNICAL PARTICULARS OF INDUCTION MOTORS

      - GENERAL

- Application

- Manufacturer

- Applicable Standards

- Number of units

- Type of motor

      - RATING

- Continuous rating in KW

- Continuous over load capacity in KW

- Rated voltage

- Rated frequency

- Allowable variation in

  - Voltage

  - Frequency

  - Combined

  - Permissible unbalance in supply voltage

- RPM

      - DUTY

- Type of duty (CI. 9.2 of IS: 325 or equivalent)

- Duty designation (CI. 9.3 of IS: 325 or equivalent)

- Factor' of Inertia

- Current

  - Full load

  - Starting

5	Efficiency

- At full load

- At half load

- At quarter load Article XXXVIII ENCLOSURE

  - Type of enclosure	:

  - Designation for degree of protection	:

  - Normal winding connection	:

  - Type and No. of terminals broughtout	:

  - Whether motor is dust proof	:

  - Whether motor is vermin proof	:

  - Type of cooling	:

  - Dimensions	:

Article XXXIX OTHER DETAILS

- Shaft orientation	:

- Mounting symbol (IS: 2253 or equivalent)	:

- Type of coupling	:

- Whether half flange required YES/NO.	:

5	Rotation as seen from top Clock wise/	: Anti clock wise	:

- Type of bearing, drive end! non drive end	:

- Whether bed plate provided YES/NO.	:

- Colour shades of paint if Special	:

- Pads for vibration pickup YES/NO provided	:

- Weight of stator	:

- Weight of the rotor	:

- Total weight of motor	:

- Whether lifting lugs provided	:

- Whether the stator frame and other metals treated for rust removal and coated with rust resistant primer and three coats of

epoxy paint.	:

ADDITIONAL DETAILS

- Type and Frame size	:

- Starting Time	:

  - With 100% voltage at terminals	:

  - With 85% voltage terminals	:

  - With 80% voltage at terminals	:

- Power Factor

  - At full load

  - At half load

  - At quarter load Article XL.STARTING

- Whether designed for both direct on line start as well as soft starting

- Maximum torque

- Starting torque % Full load torque

- Pull out torque % Full load torque

- Ratio of starting current to rated current Article XLI.INSULATION

- Class of insulation

- Reference ambient temperature/Deg. C

- Maximum temperature rise in winding at rated capacity in Deg. C

Article XLII. TERMINATIONS

- TERMINAL BOX

  - Location as seen from non-drive end Right/left

  - Ratings.

Short time Current KA (RMS) Duration Seconds KA (Peak)

  - Cable entry

  - Maximum size of cable that it can take

  - Phase segregated

  - Size of box

  - Faults withstand capacity at rated voltage.

- EXTERNAL CABLE DETAILS

  - Type

  - Number of cores Size

INSTALLATION

- Location

- Hazardous area division (IS:5572 or equivalent)

- Safe stall time at 100% rated voltage and	: under hot condition

- Particulars at rated voltage and frequency	:

  - Starting time,	:

  - Pull - out torque	:

- Pull-up torque	:

- Minimum voltage required under	: starting conditions to accelerate driven

equipment to rated speed

- Permissible running time at full load at	: minimum allowable voltage

- Locked rotor current with stand time	: (safe stall time)

- At rated temperature (Hot)	:

- When cold	:

- Stator thermal time constant	:

- Whether suitable for

- 3 equally spread starts per hour	: under normal service conditions

- 2 starts in quick succession with	: cold machine at room temperature

- One hot restart	:

- Space heaters

- Voltage	:

- Rating (Total)	:

- Separate terminal box provided	:

- Cable gland included in Contractors YES	: scope of supply

- Type and range of cables that can be	: used with the cable glands for

- Main terminals	:

- Space heater terminals	:

- Terminal of motor for control valve	:

- Two earthing pads with nut/bolt	: arrangement provided on opposite

sides, each 'suitable to receive Purchasers conductor (material and size)

- Winding temperature detectors

- Type

- Number and locations where provided

- Resistance at 0° C

- Type of mounting

- Sealing arrangement for bearings

- Special features, if any

18	Total quaranteed losses comprising iron loss, copper loss, friction, windage

and stray losses.	KW

Break up: Iron ioss	KW

Copper loss	KW

Friction windage& stray losses	KW

- Motor bearings

- Type of bearing & expected life

- Permissible temperature rise for; bearings

- Design ambient temperature assumed for above

- Manufacturers reference No. of catalogues attached here-with

- Motor bearing lubrication system

- Inertia constant of motor

- Magnetisation current of motor at rated'

voltage and frequency

- Motor Reactance (for each type of motor)

  - Sub transient reactance

  - Transient reactance

  - Steady state reactance

2. NOTES

- Each bearing shall be insulated to prevent shaft-circulating current.

- Each bearing shall be provided with one embedded temperatur detector.

- Polarisation index test shall be carried out as a routine test on each motor

- The local bearing temperature, indicator provided for the motor shall be provided at the highest convenient position for recording maintenance.

- If single core cable are to be used, gland plate shell be of non-magnetic material.

SEAL	SIGNATURE	:

DESIGNATION : COMPANY	:

DATE	:

TECHNICAL DATA TO BE FURNISHED BY BIDDERS AS REFERRED TO IN TECHNICAL SPECIFICATION (PRICE BREAKUP SHALL BE FURNISHED SEPARATELY):-

- Design Data	To be enclosed

- Guaranteed Performance Data	To be enclosed

- Technical Data

  - Power Transformer: Required Rating and capacity

    - Name of manufacturer

    - Standards followed in design, manufacturing, and testing.

    - Continuous maximum rating MVA

    - Type of cooling

    - Transformer No load voltage

      - High voltage

      - Low voltage

    - Vector Group Reference

    - Temperature rise over specified Ambient Temp.in degree C.

      - In oil by thermometer

      - In winding by resistance

    - Maximum hot spot temp. in degree C

    - One minute Dry Power frequency Test withstand voltage in KV High voltage

Low voltage

    - ON LOAD Tap changer

    - Make

No. of plus taps No. of minus taps

Voltage per step.

    - Iron losses in KW at rated voltage & frequency

    - Copper losses in KW at rated full load current and frequency at 75° C.

    - Reactance voltage with guaranteed tolerance

in % at rated F.L. current and frequency at 75° C.

    - Impedance voltage with guaranteed tolerance

in % at rated F.L. current and frequency at 75°C.

    - Regulation in % of no load voltage @ F. L. current at 75° C. and

- With unity power Factor	:

- With 0.8 lagging	:

    - Efficiency in % at 75° C and at unity power factor for: 100% load

75% load

50% load

    - No load current in Amps at rated voltage and Frequency

    - In rush Magnetising current in percent of normal F. L. current

    - Details of winding insulation:

- Class of insulation Material'

- Turns insulation high voltage in,

Megaohms

- Turns insulation low voltage in Megaohms

- Insulation core to low voltage in Megaohms

- Insulation high voltage to low voltage in

Megaohms

- Losses: No. load (W)

Full load (W)

| 3.1.21. Details of termination of HV/L V side |  |  |
| --- | --- | --- |
| 3.1.22. Insulating oil Grade and Quantity |  |  |
| 3.1.23. Weight |  |  |
| Core and windings in |  | Kgs. |
| Tank & fitting |  | Kgs. |
| Oil in |  | Kgs. |
| Complete transformer filled with oil |  | Kgs. |
| 3.1.24. Overall dimensions |  |  |
| Length |  |  |
| Breadth |  |  |
| Height |  |  |
| 3.1.25. Fittings and accessories |  |  |
| (Refer specifications at 3.1.44) |  |  |
| 3.1.26. Tests as per IS 2026 |  |  |
| 1. Type test. |  |  |
| 2. ,Routine tests. |  |  |
| 3. Special tests. |  |  |
| 3.2. Air break switch with Earth Switch |  |  |
| 3.2.1. Name of the manufacturer |  |  |
| 3.2.2. Type of Air break switch |  |  |
| 3.2.3. Short time current rating | KA |  |
| 3.2.4. Rated voltage | KV |  |
| 3.2.5. Rated normal current | KA |  |
| 3.2.6. Temperature rise |  |  |

    - Basic insulation level

      - Lightning impulse withstand KV Peak voltage to earth

      - Rated power frequency KV rms withstand voltage to earth

    - Minimum creepage distance mm KV

    - Phase to phase spacing for mm installation.

    - Details of earth switch and interlocks

    - Rated Breaker Cucible.

    - Motor

    - Voltage

    - Rated Current.

    - S.C Level.

    - Protection Provided.

  - Ligntning Arrestor

    - Make and type of arrestor

    - Rated voltage	KV

    - Nominal discharge current	KV

    - Maximum 1.2/50 impulse spark over KV Peak voltage

    - Over head shield wire details

  - HT Capacitor

    - Make and type of HT capacitor

    - KVAR calculations to improve up to 0.95 – to be enclosed.

    - Dimensions and method of GA

    - Connection drawings

  - HT CAPACITOR

    - Make and type of HT capacitor

    - KVAR calculations to improve upto 0.95 to be enclosed

  - HT Switch gear.

    - Make of MCCB

    - Capacity

  - Batteries and Battery charger

    - Make & type of battery and battery charger.

    - Capacity

  - HT Cable XLPE

    - Make of cable

    - Cross section of cable

  - HT. Distribution Panel

- Name of manufacturer

- Make of ACB

- Rating ACB

- Breaking cap

- Single line diagram of L T panel showing various load details (to be enclosed)

  - Battery

    - Make

    - Capacity

    - Battery sizing calculations (to be closened)

    - Accessories provided

    - Make and capacity with details

SEAL	SIGNATURE	:

DESIGNA TION	:

COMPANY	:

DATE

The draft tender papers for the work of “Survey, Investigation, design, Supply, Installation, Testing and Commissioning of Lift Irrigation system (Head Works consisting of Intake canal, Jack well cum pump house, Power supply including substations and Transmission lines, Rising Main including Thrust Block, Valve Chambers,  Delivery chamber, approach roads etc) to Filling up of Kogaluru percolation tank coming under minor irrigation department from Kogaluru tank in Channagiri Taluk Davanagere  District on Turn-key basis” page no.1 to 601 and Two numbers drawings are submitted for kind approval.

Executive Engineer

KNNL, No5 BCD Division Davanagere.

The draft tender papers for the work of “Survey, Investigation, design, Supply, Installation, Testing and Commissioning of Lift Irrigation system (Head Works consisting of Intake canal, Jack well cum pump house, Power supply including substations and Transmission lines, Rising Main including Thrust Block, Valve Chambers,  Delivery chamber, approach roads etc) to Filling up of Kogaluru percolation tank coming under minor irrigation department from Kogaluru tank in Channagiri Taluk Davanagere  District on Turn-key basis”page no.1 to 601 and Two numbers drawings are submitted for kind approval.

Superintending Engineer KNNL, BRP Circle,

BR PROJECT.

The draft tender papers for the work of “Survey, Investigation, design, Supply, Installation, Testing and Commissioning of Lift Irrigation system (Head Works consisting of Intake canal, Jack well cum pump house, Power supply including substations and Transmission lines, Rising Main including Thrust Block, Valve Chambers,  Delivery chamber, approach roads etc) to Filling up of Kogaluru percolation tank coming under minor irrigation department from Kogaluru tank in Channagiri Taluk Davanagere  District on Turn-key basis”page no.1 to 601 and Two numbers drawings is hereby approved.

Chief Engineer KNNL, UTP Zone,

Shivamogga.