## GTP
TENDERS FOR PC-1494 THE MANUFACTURE AND SUPPLY OF EHV GRADE TRANSFORMER OIL AS PER GESCOM SPECIFICATIONS
Guaranteed Technical Particulars
Name Of the Bidder
Sl. No. | Property | Test Method | As per IS 335:2018 | Bidders Offer
A Function
i) | Viscosity at 40˚ C | IS 1448 (Part 25) | 15mm²/s, Max
ii) | Viscosity at 0˚C¹⁾ | IS 1448 (Part 25) | 1800mm²/s, Max
iii) | Viscosity at -30˚C¹⁾ | IS 1448 (Part 25) | 1800mm²/s, Max
iv) | Viscosity at -40˚C²⁾ | IS 16084 | 2500mm²/s, Max
v) | Pour point at 0˚ C | IS 1448 (Part 10/Sec 2) | -10˚C, Max
vi) | Water content | IEC 60814 | 30mg/kg
vii) | Breakdown voltage | IS 6792 | 30 kV/70 kV ⁵⁾, Min
viii) | Density at 20˚C | IS 1448 (Part 16) | 0.895 g/ml, Max
ix) | DDF at 90˚C | IS 16086 | 0.005, Max
x) | Particle content | IS 13236 | No general requirement 10⁾
B Refining / stability
xi) | Appearance | - | Clear, free from sediment and suspended matter
xii) | Acidity | IEC 620211 - 1 | 0.01 mg, KOH/g, Max
xiii) | Interfacial tension | ASTM D971 | No general requirement ⁶⁾
xiv) | Total sulphur content | ISO 14596 or ASTM D4294⁽²⁾ | No general requirement
xv) | Corrosive sulphur | DIN 51353 | Not corrosive
xvi) | Potentially corrosive sulphur | IS 16310 | Not corrosive
xvii) | DBDS | IS 16497 (Part 1) | Not detectable (<5 mg/kg)
xviii) | Inhibitors according to IS 13631/IEC 60666 | IS 13631 | (U) Uninhibited oil: not detectable (<0.01%)
(T) Trace inhibited oil: <0.08%
(I) Inhibited oils : 0.08% - 0.40%
xix) | Metal passivator additives according to IS 13631/IEC 60666 | IS 13631 | Not detectable (<5 mg/kg)
xx) | Other additives |  | As per IS 335:2018
xxi) | 2-Furfural and related compounds content | IS 15668 | Not detectable (<0.05 mg/kg) for each individual compound)
C Performance
xxii) | Oxidation stability | IS 12422 (Method C) | For oils with other antioxidant additives and mental passivator Additives (see 6.12) As per IS 335:2018
Test duration ¹¹⁾
(I) Uninhibited oil: 164 h
(T) Trace inhibited oil : 332 h
(I) Inhibited oil : 500h
a) | • Total acidity | 1.9.4 of IS 12422 | 1.2 mg KOH/g, Max
b) | • Sludge | 1.9.1 of IS 12422 | 0.8%, Max
c) | • DDF at 90˚C | 1.9.6 of IS 12422 | 0.500, Max
xxiii) | Gassing tendency | IEC 60628, Method A | No general requirement 8)
xxiv) | ECT | See 6.14 | No general requirement 8)
D Health, Safety and Environment (HSE) |  |  |  | `
xxv) | Flash point | IS 1448 (Part 21) | 135˚C, Min
xxvi) | PCA content | IP 346 | 3%, Max
xxvii) | PCB content | IS 16082 | Not detectable (<2 mg/kg)