## AFZAL-305-ms
MILE STONE
Providing Irrigation Facility to Sy. No. 305, 256, 314, 245 & 307 through Pipeline in Afzalpur Town in Afzalpur Taluka Kalaburagi District
7.57 | 45 | 6 | 11 | 12 | 12
Sl. No. | Description of Item | Unit | Quantity | Rate | Amount (Rs.) | Milestone-1 (for 1st three months) | [7 empty] | Milestone-2 (for 2nd three months) | [7 empty] | Total Amount | Remarks
[6 empty] | 1st month |  | 2nd month |  | 3rd month |  | Quantity | Amount | 1st month |  | 2nd month |  | 3rd month |  | Quantity | Amount
[6 empty] | Qty | Amount | Qty | Amount | Qty | Amount |  |  | Qty | Amount | Qty | Amount | Qty | Amount
1 | Supply and delivery of 10 HP, size 80x65 Head 34.50M, Discharge 840 LPM centrifugal pumpset at site brand new best make and with discharge duty confirming to ISI standards and its latest amendments with all leads and lifts, etc. complete and as per the direction of the Engineer-in-charge. | No. | 6 | 39504.15 | 237025 | 2 | 79008 | 2 | 79008 | 2 | 79008 | 6 | 237024.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 237025 |  | 0
2 | Supply and delivery at site brand new best make starter/ control panel suitable for 7.5-10 HP centrifugal pump confirming with ISI mark and its latest amendments with all leads and lifts, etc. complete and as per the direction of the Engineer-in-charge. | No. | 6 | 16327.5 | 97965 | 2 | 32655 | 2 | 32655 | 2 | 32655 | 6 | 97965 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97965 |  | 0
3 | Supply, delivery, erection and commissioning at site lighting distribution board suitable for monoblock centrifugal pump confirming with ISI mark and its latest amendments with all leads and lifts, etc. complete and as per the direction of the Engineer-in-charge. | No. | 6 | 3675 | 22050 | 2 | 7350 | 2 | 7350 | 2 | 7350 | 6 | 22050 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22050 |  | 0
4 | Supply, installing, testing and commissioning COMMON control panel consisting of the following INCOMING: 1 No set of Phase indicating lamps with SFU of suitable rating 1 No, Analog Ammeter, 1 No Analog Voltmeter 1ni with Phase selector switch, Isolating switch OUTGOING for Main Electrical Pump: 1 No. MCB 1 No. Direct Online Starter (DOL) of Star-delta (SD) Starter suitable for 6 to 15 HP pumps 1 No. Electrcal Protection Like single Phase preventor, under voltage over Volage, under current over current & dry run protection suitable for the pump described above 1 No. for outdoor type with all leads and lifts, etc. complete and as per the direction of the Engineer-in-charge. | No. | 6 | 18375 | 110250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 55125 | 3 | 55125 | 6 | 110250 | 110250 |  | 0
5 | Supply and delivery at site best indigenous brand new power capacitor as per IS 2834/1986 with latest amendments with KPTCL authorities and erection, electrification and commissioning of the same at the location of respective pump sets with all leads and lifts, etc. complete and as per the direction of the Engineer-in-charge. | KVAR | 30 | 577.5 | 17325 | 6 | 3465 | 6 | 3465 | 6 | 3465 | 18 | 10395 | 6 | 3465 | 6 | 3465 | 0 | 0 | 12 | 6930 | 17325 |  | 0
6 | Providing up to 4Cx50 Sqmm Epoxy Terminating Kit (Pothead) suitable for 1.1 kV, LTUG Cable with all leads and lifts, etc. complete and as per the direction of the Engineer-in-charge. | No. | 40 | 340.2 | 13608 | 9 | 3062 | 7 | 2381 | 7 | 2381 | 23 | 7824.6 | 8 | 2722 | 9 | 3062 | 0 | 0 | 17 | 5783 | 13608 |  | 0
7 | Supply, delivery, erection and commissioning at site ELCB suitable for monoblock centrifugal pump confirming with ISI mark and its latest amendments with all leads and lifts, etc. complete and as per the direction of the Engineer-in-charge. | No. | 6 | 4322.85 | 25937 | 6 | 25937 | 0 | 0 | 0 | 0 | 6 | 25937.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25937 |  | 0
8 | Labour charges for providing connection using 3½ x 16 sqmm insulated sheathed steel wire cable as per IS 1554/ 1988 with latest amendments from KPTCL pole to meter board unit, with all necessary materials ,tools and equipments,as per specificationswith testing with all leads and lifts, etc. complete and as per the direction of the Engineer-in-charge. | m | 30 | 283.5 | 8505 | 30 | 8505 | 0 | 0 | 0 | 0 | 30 | 8505 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8505 |  | 0
9 | Supply and delivery at site Brand new best make 1x3x6 Sqm PVC insulated cable of Flat 3 core (sheathed) of nominal cross sectional area as per IS 694-1990 with ISI Mark and as per its latest amendments with all leads and lifts, etc. complete and as per the direction of the Engineer-in-charge. | m | 60 | 194.25 | 11655 | 60 | 11655 | 0 | 0 | 0 | 0 | 60 | 11655 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11655 |  | 0
10 | Labour charges for erection of indoor type panel board and meter board units with all necessary materials and labour tools and equipments including cement concrete for foundation/bed etc,complete as per specification, with testing with all leads and lifts, etc. complete and as per the direction of the Engineer-in-charge. | Job | 6 | 1417.5 | 8505 | 6 | 8505 | 0 | 0 | 0 | 0 | 6 | 8505 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8505 |  | 0
11 | Labour charges for Erection, Electrification and commissioning of Pump sets, including aligning and balancing of all items including supply and erection of two pair of supporting clamps, bore well caps, cable clips and water tight gland cable protectors, bolts, nuts, valve and gauges,tools and equipments etc., involved in the job as per specifications, with necessary tests as per specifications, with testing with all leads and lifts, etc. complete and as per the direction of the Engineer-in-charge. | Job | 6 | 6825 | 40950 | 6 | 40950 | 0 | 0 | 0 | 0 | 6 | 40950 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40950 |  | 0
12 | Earthing: Providing and fixing and wiring earth electrode for grounding circuits IC cutouts and other equipments on the meter board in the pit. The pits should be filled up with equal proportion of salt and charcoal 150mm around the pipe to complete depth. The connection from the pipe to the conduits etc. is to established through GI wire of sizes as per clause 7.3.3 of IS 732 using 12mm bolts, nuts, washers and check nuts, the pipe shall have 16 through holes of 12mm dia with all leads and lifts, etc. complete and as per the direction of the Engineer-in-charge. | Job | 6 | 3937.5 | 23625 | 6 | 23625 | 0 | 0 | 0 | 0 | 6 | 23625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23625 |  | 0
13 | Earth work excavation for Foundation by mechanical means in all kinds of soils upto 3 m depth for all works & depth upto 3 m, as per drawing and technical specifications, including setting out, shoring, strutting, barricading, caution lights, including dressing of excavated surfaces, disposing off or levelling the excavated earth or sorting & stacking the selected earth for reuse in a radius of 50 m and lift upto 1.5 m including cost of labour, tools, usage of machinery & other appurtenaces required with all leads and lifts, etc. complete and as per the direction of the Engineer-in-charge. | Cum | 3081 | 107.1 | 329975 | 1500 | 160650 | 500 | 53550 | 500 | 53550 | 2500 | 267750 | 581 | 62225 | 0 | 0 | 0 | 0 | 581 | 62225 | 329975 |  | 0
14 | Providing and installing at site of work 160 mm dia (weight of pipe-3.923 kg) 8 Kg/m² P.V.C. pipes including cost of pipes and specials and labour, including lowering into trenches, laying true to line, level and perfect linking at joints leak proof including jointing of approved type with all labour charges and all lift charges, handling charges including encasing the pipe around to a depth not less than 15 cms with gravel or selected earth available from the excavation with all leads and lifts, etc. complete and as per the direction of the Engineer-in-charge. | m | 8855 | 1048.95 | 9288452 | 1000 | 1048950 | 1500 | 1573425 | 1400 | 1468530 | 3900 | 4090905 | 1800 | 1888110 | 1800 | 1888110 | 1355 | 1421327 | 4955 | 5197547 | 9288452 |  | 0
15 | Refilling available earth around trenches/ pipelines, cables in layers not exceeding 20 cms in depth, compacting each deposited layer by ramming after watering with a lead upto 50 m, and lift upto 1.5 m. Including cost of all labour complete with all leads and lifts, etc. complete and as per the direction of the Engineer-in-charge. | Cum | 2977.68 | 168 | 500250 | 0 | 0 | 800 | 800 | 800 | 134400 | 1600 | 268800 | 800 | 134400 | 577.68 | 97050 | 0 | 0 | 1377.68 | 231450 | 500250 |  | 0
16 | Providing, laying and jointing 75 mm dia HDPE pipes PE80-PN6.0 of specified grade and conforming to IS 4984-2016 with latest ammendments and conveying to work site including loading and unloading at both destinations and rolling and lowering into trenches, laying true to line and jointing of pipes and specials with electrofusion welding, giving hydraulic test as per relevant ISS with all lead and lifts including encasing the pipe alround to a depth of not less than 15 cms with soft gravel or selected earth available from the excation, testing and commissioning. The rate is exclusive of required specials and fittings wherever necessary like saddle Tee, stub ends, flanged sets, bends, reducers (Contractor will make his own arrangements for procuring water for testing) with all leads and lifts, etc. complete and as per the direction of the Engineer-in-charge. | m | 36 | 244.65 | 8807 | 0 | 0 | 0 | 0 | 18 | 4404 | 18 | 4403.7 | 18 | 4404 | 0 | 0 | 0 | 0 | 18 | 4404 | 8808 |  | -1
17 | Providing, laying and fixing of light Duty 100 mm dia GI pipes conforming to IS 1239: 1990 with latest amendments complete with GI fittings (excluding the cost of fittings) with cuts and threads wherever necessary, including testing for water tightness, and commissioning with all leads and lifts, etc. complete and as per the direction of the Engineer-in-charge. | m | 30 | 1022.7 | 30681 | 0 | 0 | 0 | 0 | 15 | 15341 | 15 | 15340.5 | 15 | 15341 | 0 | 0 | 0 | 0 | 15 | 15341 | 30682 |  | -1
18 | Supply and delivery at site wrought middle steel (galvanized) 100 mm dia GI bend confirming to IS 1239-II, 1991 with latest amendments if any with all leads and lifts, etc. complete and as per the direction of the Engineer-in-charge. | No. | 20 | 630 | 12600 | 0 | 0 | 0 | 0 | 10 | 6300 | 10 | 6300 | 10 | 6300 | 0 | 0 | 0 | 0 | 10 | 6300 | 12600 |  | 0
19 | Supply and delivery at site wrought middle steel (galvanized) 100 mm dia GI union confirming to IS 1239-II, 1991 with latest amendments if any with all leads and lifts, etc. complete and as per the direction of the Engineer-in-charge. | No. | 20 | 653.1 | 13062 | 0 | 0 | 0 | 0 | 10 | 6531 | 10 | 6531 | 10 | 6531 | 0 | 0 | 0 | 0 | 10 | 6531 | 13062 |  | 0
20 | Supply and delivery at site of brand new best make 80 mm non-return valve as per IS 778/1984 with ISI Mark and as per its latest amendments with all leads and lifts, etc. complete and as per the direction of the Engineer-in-charge. | No. | 15 | 1837.5 | 27563 | 0 | 0 | 0 | 0 | 7 | 12863 | 7 | 12862.5 | 8 | 14700 | 0 | 0 | 0 | 0 | 8 | 14700 | 27563 |  | 0
21 | Providing and fixing 80 mm dia kinetic air valve of PN 16.0 for automatic discharge of accumulate air during working condition, conforming to IS 14845/ EN 1074-4. Body and bonnet of DI conforming to IS-1865 of grade GGG-40/50, seals are made of approved EPDM, SS 304 float, guide and internals. Flange drilling according to IS-1538 with appurtenances complete. Body and bonnet shall be coated with electrostatically applied epoxy powder coating with a coating thickness of 250 micron both inside and outside etc. complete For K Air Valves of 80mm dia with all leads and lifts, etc. complete and as per the direction of the Engineer-in-charge. | No. | 10 | 27660.15 | 276602 | 0 | 0 | 0 | 0 | 5 | 138301 | 5 | 138300.75 | 5 | 138301 | 0 | 0 | 0 | 0 | 5 | 138301 | 276602 |  | 0
22 | Providing and fixing DI Resilient seated soft sealing PN10.0 and 80 mm sluice valve of variouis dia. with body bonnet of Ductile Iron (DI) conforming ti IS-1865 with the latest amendments and of grade GGG 40/ 50, shaft of stainless steel, wedge fully rubber lined with EDPM seals of NBR and the valves should be vacum tight and 100% leak proof with face to face dimensions as per IS 14846-2000 with the latest amendments only. The stem sealing should be with toroidal sealing rings (minimum 2 "O" rings). Body and bonnet should be coated with Electrostatically applied Epoxy Powder Coating with minimum coating thickness of 250 micron both inside and outside. The rate is inclusive of cost of valves, TP set, galvanized bolts & nuts and rubber insertions etc. but excluding earth work. For PN-10: (Note: TP set should be considered only for DI pipes estimate. For MS pipes estimates, TP sets cost of corresponding dia shall be deducted from the SR rates of valves and provision for corresponding dia MS flanges should be made in the estimate) with all leads and lifts, etc. complete and as per the direction of the Engineer-in-charge. | No. | 6 | 10912.65 | 65476 | 0 | 0 | 0 | 0 | 3 | 32738 | 3 | 32737.95 | 3 | 32738 | 0 | 0 | 0 | 0 | 3 | 32738 | 65476 |  | 0
23 | Supply and delivery at site GM (copper alloy) 80 mm dia gate valves confirming to Class-I as per IS 778 with latest amendments, 1 No. screwed in bonnet inside screw, rising spring spindle integral seat screwed females ends confirming to IS 554/ 1990 body hydraulically tested 1.5HP seat standard tested 1 HP with IS mark with all leads and lifts, etc. complete and as per the direction of the Engineer-in-charge. | No. | 8 | 1997.1 | 15977 | 0 | 0 | 0 | 0 | 4 | 7988 | 4 | 7988.4 | 4 | 7988 | 0 | 0 | 0 | 0 | 4 | 7988 | 15976 |  | 1
24 | Earth work excavation for Foundation by mechanical means in all kinds of soils upto 3 m depth for all works & depth upto 3 m, as per drawing and technical specifications, including setting out, shoring, strutting, barricading, caution lights, including dressing of excavated surfaces, disposing off or levelling the excavated earth or sorting & stacking the selected earth for reuse in a radius of 50 m and lift upto 1.5 m including cost of labour, tools, usage of machinery & other appurtenaces required with all leads and lifts, etc. complete and as per the direction of the Engineer-in-charge. | Cum | 375 | 107.1 | 40163 | 375 | 40163 | 0 | 0 | 0 | 0 | 375 | 40162.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40163 |  | 0
25 | Providing casing embankment using semi-pervious/ pervious approved soil from borrow areas in layers of 250 to 300 mm (before compaction) including cost of all materials, machinery, labour, all other operations such as collection of soil, spreading soil in layer of specified thickness, sorting out, breaking clods, levelling, sectioning edges/ sides, watering, compacting each layer to density control of not less than 95 percent or as stipulated using power roller and all other ancillary operations with all leads and lifts, etc. complete and as per the direction of the Engineer-in-charge. | Cum | 37.13 | 660.45 | 24523 | 37.13 | 24523 | 0 | 0 | 0 | 0 | 37.13 | 24522.51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24523 |  | 0
26 | Earth work in surface excavation by mechanical means for lowering & leveling the ground in all kinds of soils upto 300 mm depth for all works other than foundation in all kinds of soils & upto depth not exceeding 300 mm as per drawing and technical specifications, including setting out, shoring, strutting, barricading, caution lights, removal of stumps and other deleterious matter including dressing of excavated surfaces, disposing off or levelling the excavated earth or sorting & stacking the selected earth for reuse in a radius of 50 m and lift upto 1.5 m including cost of labour, tools, usage of machinery & other appurtenances required with all leads and lifts, etc. complete and as per the direction of the Engineer-in-charge. | Cum | 3.84 | 99.75 | 383 | 3.84 | 383 | 0 | 0 | 0 | 0 | 3.84 | 383.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 383 |  | 0
27 | Providing and laying in position cement concrete mix 1:3:6 Using 40 mm nominal size graded crushed coarse aggregates for levelling course for all works in foundation. The granite/ trap/ basalt crushed graded coarse aggregates and fine aggregates as per relevant IS Codes machine mixed, laid in layers not exceeding 150 mm thickness, well compacted using plate vibrators, including all lead & lifts, cost of all materials of quality, labour, Usage charges of machinery, curing, and all the other appurtenances required with all leads and lifts, etc. complete and as per the direction of the Engineer-in-charge. | Cum | 0.77 | 6213.9 | 4785 | 0.77 | 4785 | 0 | 0 | 0 | 0 | 0.77 | 4784.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4785 |  | 0
28 | Providing size stone masonry with hard stone in foundation & plinth with cement mortar 1:6 (1 cement: 6 coarse sand) with all leads and lifts, etc. complete and as per the direction of the Engineer-in-charge. | Cum | 6.14 | 6682.2 | 41029 | 6.14 | 41029 | 0 | 0 | 0 | 0 | 6.14 | 41028.71 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41029 |  | 0
29 | Providing and laying in position cement concrete mix 1:2:4 using 20 mm nominal size graded crushed coarse aggregates for levelling course for all works in foundation. The granite/ trap/ basalt crushed graded coarse aggregates and fine aggregates as per relevant IS Codes machine mixed, laid in layers not exceeding 150 mm thickness, well compacted using plate vibrators, including all lead & lifts, cost of all materials of quality, labour, Usage charges of machinery, curing, and all the other appurtenances required with all leads and lifts, etc. complete and as per the direction of the Engineer-in-charge. | Cum | 0.77 | 6474.3 | 4985 | 0.77 | 4985 | 0 | 0 | 0 | 0 | 0.77 | 4985.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4985 |  | 0
30 | Providing 20 mm cement plaster of mix: 1:4 (1 cement: 4 fine sand) to brick/stone masonry including rounding off corners wherever required smooth rendering, providing and removing scaffolding, including cost of materials, labour, curing with all leads and lifts, etc. complete and as per the direction of the Engineer-in-charge. | Sqm | 15.36 | 371.7 | 5709 | 15.36 | 5709 | 0 | 0 | 0 | 0 | 15.36 | 5709.31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5709 |  | 0
31 | RCC hume pipe Circular pump house: Providing precast RCC Circular Hume pipe pump house with M.S door and RCC conical roof as per specification and drawings - Internal dia Mtr. 1200 mm & height of 2.5 Mtr With Wall thickness 65mm with all leads and lifts, etc. complete and as per the direction of the Engineer-in-charge. | No. | 2 | 17221.05 | 34442 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 34442 | 2 | 34442 | 34442 |  | 0
32 | Erection and positioning of RCC Hume pipe pump house/ Cistern on size stone masory platform including transportation charges and handling,finishing with all necessary tools ,plants and materials with all leads and lifts, etc. complete and as per the direction of the Engineer-in-charge. | No. | 2 | 1976.1 | 3952 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 3952 | 2 | 3952 | 3952 |  | 0
33 | HT Line: Supplying and erection of PSCC Pole-8 Mtr Long, 200 Kg WL including digging of pit, transportation of pole etc. complete (Dwg No. BESCOM/ GM/ QS&S/02 Dtd 24.11.2018) as per IS-785 with all leads and lifts, etc. complete and as per the direction of the Engineer-in-charge. | Each | 2 | 5380.2 | 10760 | 0 | 0 | 2 | 10760 | 0 | 0 | 2 | 10760.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10760 |  | 0
34 | Providing & fixing of 11 kV, Horizontal Cross Arm-Mild Steel (MS) (Dwg No. BESCOM/ GM/ QS&S/ 04 Dtd 24.11.2018) with all leads and lifts, etc. complete and as per the direction of the Engineer-in-charge. | Each | 3 | 876.75 | 2630 | 0 | 0 | 3 | 2630 | 0 | 0 | 3 | 2630.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2630 |  | 0
35 | Supply and fixing at site guy set with 2-No. of No. 15 strain insulator & concreting material galvanized steel wire with turn buckle and anchoring with all accessories with all leads and lifts, etc. complete and as per the direction of the Engineer-in-charge. | Set | 1 | 1716.95 | 1717 | 0 | 0 | 1 | 1717 | 0 | 0 | 1 | 1716.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1717 |  | 0
36 | Providing 11 kV Ceramic Pin Insulator (Shell Only) with all leads and lifts, etc. complete and as per the direction of the Engineer-in-charge. | No. | 6 | 87.15 | 523 | 0 | 0 | 6 | 523 | 0 | 0 | 6 | 522.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 523 |  | 0
37 | Providing DISC Insulator 45 kN Porcelain with all leads and lifts, etc. complete and as per the direction of the Engineer-in-charge. | No. | 6 | 535.5 | 3213 | 0 | 0 | 6 | 3213 | 0 | 0 | 6 | 3213 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3213 |  | 0
38 | Providing 11 kV GI Pin for 11 kV Ceramic Shell Insulator with all leads and lifts, etc. complete and as per the direction of the Engineer-in-charge. | No. | 6 | 69.3 | 416 | 0 | 0 | 6 | 416 | 0 | 0 | 6 | 415.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 416 |  | 0
39 | Providing and stringing of Rabbit ACSR (6/3.35 mm Al + 1/3.35 mm St), Std Wt: 214 Kg/Km with all leads and lifts, etc. complete and as per the direction of the Engineer-in-charge. | Km | 0.45 | 51884.7 | 23348 | 0 | 0 | 0.45 | 23348 | 0 | 0 | 0.45 | 23348.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23348 |  | 0
40 | Supply of Caution/ Danger Board with all leads and lifts, etc. complete and as per the direction of the Engineer-in-charge. | Each | 1 | 241.5 | 242 | 0 | 0 | 0 | 0 | 1 | 242 | 1 | 241.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 242 |  | 0
41 | Supply of GI barbed wire (12 mtr/ Kg) with all leads and lifts, etc. complete and as per the direction of the Engineer-in-charge. | Each | 2 | 137.55 | 275 | 0 | 0 | 0 | 0 | 2 | 275 | 2 | 275.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 275 |  | 0
42 | Double pole TC set for erection of transformer on RCC/ PSCC 9-m long poles as per IS 1977 for 100/300 kVA 4/5 star rated transformer with all leads and lifts, etc. complete and as per the direction of the Engineer-in-charge. | Each | 1 | 38489.85 | 38490 | 1 | 38490 | 0 | 0 | 0 | 0 | 1 | 38489.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38490 |  | 0
43 | Digging of Pit 1.8 Mtr depth in ordinary soil with all leads and lifts, etc. complete and as per the direction of the Engineer-in-charge. | Pit | 2 | 660.45 | 1321 | 2 | 1321 | 0 | 0 | 0 | 0 | 2 | 1320.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1321 |  | 0
44 | Providing 8 SWG GI Wire (4.064 mm Dia), Std Wt: 131 Kg/ Km with all leads and lifts, etc. complete and as per the direction of the Engineer-in-charge. | Kg | 5 | 78.792 | 394 | 5 | 394 | 0 | 0 | 0 | 0 | 5 | 393.96 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 394 |  | 0
45 | Providing 7/10 SWG Guy Wire (7/3.251 mm Dia), Std Wt: 680 Kg/ Km with all leads and lifts, etc. complete and as per the direction of the Engineer-in-charge. | Kg | 5 | 81.0873 | 405 | 5 | 405 | 0 | 0 | 0 | 0 | 5 | 405.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 405 |  | 0
46 | Supply and fixing at site guy set with 2-No. of No. 15 strain insulator & concreting material galvanized steel wire with turn buckle and anchoring with all accessories with all leads and lifts, etc. complete and as per the direction of the Engineer-in-charge. | Set | 2 | 1403.85 | 2808 | 2 | 2808 | 0 | 0 | 0 | 0 | 2 | 2807.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2808 |  | 0
47 | Providing Earthing including GI Grounding pipe, B-Class, 42 mm dia, 2.5 m long, 3.2 mm thick with bolt, nut, GI Strips and washer complete Minimum Weight of GI Pipe: 7.3 Kg including cost of charcoal and salt packed in 30 & 50 Kg gunny bags respectively with all leads and lifts, etc. complete and as per the direction of the Engineer-in-charge. | No. | 3 | 2811.9 | 8436 | 0 | 0 | 3 | 8436 | 0 | 0 | 3 | 8435.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8436 |  | 0
48 | Providing & fixing of 1.1 KV Class HR (Heat Resistant) 120 sqmm PVC Insulated & unsheathed Aluminium Wires Multistrand Single Core Lead wires as per IS-694: 2010 with all leads and lifts, etc. complete and as per the direction of the Engineer-in-charge. | m | 30 | 150.35 | 4511 | 0 | 0 | 30 | 4511 | 0 | 0 | 30 | 4510.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4511 |  | 0
49 | Wiring for lighting/power circuit using one of FRLS PVC insulted 1.1 kV grade multi strand copper with low conductor resistance 2.5 Sqmm single core wire in open are concealed system of wiring with specified IS-694-1990 and conform into GTP of group A with all leads and lifts, etc. complete and as per the direction of the Engineer-in-charge. | m | 30 | 36.75 | 1103 | 0 | 0 | 30 | 1103 | 0 | 0 | 30 | 1102.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1103 |  | 0
50 | Providing LT protection kit as per Dwg No. BESCOM/GM/QS&S/10 Dtd 24.11.2018 with all leads and lifts, etc. complete and as per the direction of the Engineer-in-charge. | No. | 1 | 2497.95 | 2498 | 0 | 0 | 1 | 2498 | 0 | 0 | 1 | 2497.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2498 |  | 0
51 | Providing 11 kV, HG Fuse Unit with Solid Core Insulator (Dwg No. BESCOM/GM/QS&S/21 Dtd 24.11.2018) with all leads and lifts, etc. complete and as per the direction of the Engineer-in-charge. | No. | 1 | 1371.3 | 1371 | 0 | 0 | 1 | 1371 | 0 | 0 | 1 | 1371.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1371 |  | 0
52 | Supply of 11 kV, 200 amps single break GOS as per Dwg No. BESCOM/ GM/ QS&S/ 23 dt: 24.11.2018) with all leads and lifts, etc. complete and as per the direction of the Engineer-in-charge. | Set | 1 | 11081.7 | 11082 | 0 | 0 | 1 | 11082 | 0 | 0 | 1 | 11081.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11082 |  | 0
53 | Providing 100 kVA aluminium wdg, 4-star rated 3-phase 11 KV/ 433V distribution transformer-stacked CRGO core with oil with all leads and lifts, etc. complete and as per the direction of the Engineer-in-charge. | Set | 1 | 223443.15 | 223443 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 223443 | 1 | 223443 | 223443 |  | 0
54 | LT Metering Box for housing the ETV Meter without CT's busbar wiring etc. with all leads and lifts, etc. complete and as per the direction of the Engineer-in-charge. | Unit | 1 | 3826.2 | 3826 | 0 | 0 | 1 | 3826 | 0 | 0 | 1 | 3826.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3826 |  | 0
55 | SMC metering box as above With CT Ratio 150/5 for 100 kVA DTC with all leads and lifts, etc. complete and as per the direction of the Engineer-in-charge. | Set | 1 | 6890.1 | 6890 | 0 | 0 | 1 | 6890 | 0 | 0 | 1 | 6890.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6890 |  | 0
56 | LT Line: Supplying and erection of PSCC Pole-8 Mtr Long, 200 Kg WL including digging of pit, transportation of pole etc. complete (Dwg No. BESCOM/GM/QS&S/02 Dtd 24.11.2018) as per IS-785 with all leads and lifts, etc. complete and as per the direction of the Engineer-in-charge. | No. | 1 | 5380.2 | 5380 | 0 | 0 | 1 | 5380 | 0 | 0 | 1 | 5380.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5380 |  | 0
57 | Supplying and erection of RCC Pole-8 Mtr Long, 115 Kg WL including digging of pit, transportation of pole etc. complete (Dwg No. BESCOM/GM/QS&S/02 Dtd 24.11.2018) as per IS-785 with all leads and lifts, etc. complete and as per the direction of the Engineer-in-charge. | No. | 1 | 6881.7 | 6882 | 0 | 0 | 1 | 6882 | 0 | 0 | 1 | 6881.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6882 |  | 0
58 | Supply and delivery at site MS LT-4 pin cross arms with clamps, bolts, nuts & washers with braces with all accessories with all leads and lifts, etc. complete and as per the direction of the Engineer-in-charge. | No. | 3 | 565.95 | 1698 | 0 | 0 | 0 | 0 | 3 | 1698 | 3 | 1697.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1698 |  | 0
59 | Supply and fixing at site guy set with 2-No. of No. 15 strain insulator & concreting material galvanized steel wire with turn buckle and anchoring with all accessories with all leads and lifts, etc. complete and as per the direction of the Engineer-in-charge. | Set | 1 | 1403.85 | 1404 | 0 | 0 | 0 | 0 | 1 | 1404 | 1 | 1403.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1404 |  | 0
60 | Providing 1.1 kV Ceramic Pin Insulator (Shell Only) with all leads and lifts, etc. complete and as per the direction of the Engineer-in-charge. | No. | 4 | 32.55 | 130 | 0 | 0 | 0 | 0 | 4 | 130 | 4 | 130.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 |  | 0
61 | Providing 1.1 kV GI Pin for 11 kV Ceramic Shell Insulator with all leads and lifts, etc. complete and as per the direction of the Engineer-in-charge. | No. | 4 | 36.75 | 147 | 0 | 0 | 0 | 0 | 4 | 147 | 4 | 147 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 147 |  | 0
62 | Providing No. 8 strain insulator with all leads and lifts, etc. complete and as per the direction of the Engineer-in-charge. | No. | 8 | 28.35 | 227 | 0 | 0 | 0 | 0 | 8 | 227 | 8 | 226.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 227 |  | 0
63 | Supply and stringing Weasel ACSR conductors with 1.5% sag with all accessories with all leads and lifts, etc. complete and as per the direction of the Engineer-in-charge. | Km | 0.41 | 32632.95 | 13380 | 0 | 0 | 0 | 0 | 0.41 | 13380 | 0.41 | 13379.51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13380 |  | 0
|  |  |  | Total | 11725778 |  | 1619312 |  | 1847220 |  | 2023308 |  | 5623437.31 |  | 2317225 |  | 2046812 |  | 1738289 |  | 6102325 | 11725767 |  | 11
|  |  |  | Cumulative Milestone |  | 5623437.31 | [7 empty] | 11725762.31
[5 empty] | 9887426 |  | 5489840 |  | 6187753 |  | 6387345 |  |  |  | 6102326 |  | 9887426 |  | 7840614 |  | 6102325
The liquidated damages
|  |  |  | For Milestone 1: |  |  | Rs. | 5623.4373 | per day | 0.056234 | Lakhs/Day
|  |  |  | For Milestone 2: |  |  | Rs. | 11725.7623 | per day | 0.11726 | Lakhs/Day
[7 empty] | 1 | 1619312 |  | 3 | 2023308
[7 empty] | 2 | 1847220 |  | 4 | 2317225
[7 empty] | 3 | 2023308 |  | 5 | 2046812
[8 empty] | 5489840 |  |  | 6387345
[7 empty] | 2 | 1847220 |  | 4 | 2317225
[7 empty] | 3 | 2023308 |  | 5 | 2046812
[7 empty] | 4 | 2317225 |  | 6 | 1738289
[8 empty] | 6187753 |  |  | 6102326