## Abstract
HUBLI ELECTRICITY SUPPLY COMPANY LIMITED
Estimate for Providing additional 3rd 5 MVA, 33/11KV power transformer at 33/11KV sub-station Gandigwad in Khanapur Taluk, Belagavi District in 33KV S&L Division, Belagavi on PTK basis (5 MVA Power Transformer will be supplied by departmentally)
ABSTRACT
Sl. No | Particulars | Material | Labour | Civil | Total
1 | Materials cost (Exclusive of GST) | 8754879.204 |  |  | 8754879.204
2 | Labour charges+ Decommissioning (Exclusive of GST) |  | 302761.7186 |  | 302761.7186
3 | Civil Engineering Charges (Exclusive of GST) |  |  | 1048120 | 1048120 |  |  |  | 2.8062
4 | Basic rate | 8754879.204 | 302761.7186 | 1048120 | 10105760.9226
5 | Area Specific Loading @ 5% on labour charges | 0 | 0 | 0 | 0
| Overhead Charges @ 10% on Sl No. 4 & 5 | 875487.9204 | 30276.1719 | 104812 | 1010576.0923
| Contractors Profit @ 10% on Sl No. Sl No. 4 & 5 | 875487.9204 | 30276.1719 | 104812 | 1010576.0923
7 | Cost of the Estimate /APT (Without GST) | 10505855.0448 | 363314.0623 | 1257744 | 12126913.1071 | 50614881.6107 |  | 48828398.671
% age of tender compenents included
[8 empty] | 36701485.5638 |  | 24253826.2142
| Executive Engineer (EL), |  |  | Superintending Enginner (El),
| Projects - 1 , HESCOM, Hubli |  |  | PMC, HESCOM, Hubli
-12126913.1071
-1
24253826.2142

## Material
HUBLI ELECTRICITY SUPPLY COMPANY LIMITED
Estimate for Providing additional 3rd 5 MVA, 33/11KV power transformer at 33/11KV sub-station Gandigwad in Khanapur Taluk, Belagavi District in 33KV S&L Division, Belagavi on PTK basis (5 MVA Power Transformer will be supplied by departmentally)
PART-A (Material portion)
Sl. No. |  | Particulars | Unit | Qty | Rate as per SR 2025-26 | Amout in Rs.
HESCOM PORTION
A.1 |  | Power Transformers:
| a) | 33/11KV, 5 MVA, DELTA/STAR, DY 11, 3Ph, 50Hz,Core type winding with OLTC, RTCC panel etc., complete filled with Transil Oil and 10 % spare Oil in Non Returnable Drums (Power Transformer shall be supplied by departmentaly) (As per ESCOM's CSR- 2025-26 33KV Material. page No- 69 of 81 SL.No-1, Item No-1.01 ,Material Code-1.01) | Nos | 0 | 6597322 | 0
| b) | Deloaded by 21% on Total cost of estimate(6284178.00/1.21=5193535.54)
Total cost
AGENCY PORTION
A.2 |  | 33KV SF-6/ VCB Breakers:
| a) | 66 kV, 40 kA class, SF-6 Circuit Breaker with terminal connector suitable for Al. tube/conductor with spring/semi-pneumatic/pneumatic type operating mechanism and mounting structure etc., as per technical specification. (As per KPTCL SR 2025-26, Page No- 14, SL.No-278 | Nos | 2 | 645000 | 1290000 | 703010 |  | 577170 | 33 kV, 25 kA class, SF-6 Circuit Breaker with terminal connector suitable for Al. tube/conductor with spring operating mechanism and mounting structure etc., as per technical specification. (As per KPTCL SR- 2023-24, Part-01 Major Works Materials/Equipment . Page No- 27, SL.No-3, Item No-3.5 ,HSN Code-8536)
A.3 |  | Control and relay panels Simplex type as per technical specifications (Control Voltage 110V DC) |  |  |  | 0
| a) | 33KV Panel for Overhead Line (KPTCL SR-2023-24, Page No:41,Sl. No-16 Item No:16.2.8,HSN Code,8537 Rs:214170 (33KV Panel rate) | panel | 1 | 178475 | 178475 | Not updated in new SR
| b) | 5MVA, 33/11KV Transformer Panel (KPTCL SR-2023-24, Page No:41, Sl. No-16 Item No:16.2.7,HSN Code,8537 Rs:631620 (66KV Panel rate rate is considered due to non availability for 33 KV Panel in the CSR 2023-24) | panel | 1 | 526350 | 526350 | Not updated in new SR
A.4 |  | 33KV Current Transformers |  |  |  | 0
| a) | 36KV, 20KA CT of ratio 400-200/1-1-1A with rigid terminal connector suitable for Coyote ACSR conductor with marshallling Box for Incomer. (As per ESCOM's CSR- 2025-26 33KV Material. page No- 81 SL.No-6, Item No-2.01) | Nos | 3 | 57030 | 171090
| b) | 36KV, 20KA CT of ratio 200-100/1-1-1A with rigid terminal connector suitable for Coyote ACSR conductor with marshallling Box for power transformer. (As per ESCOM's CSR- 2025-26 33KV Material. page No- 81 SL.No-6, Item No-2.02) | Nos | 3 | 57030 | 171090
| c) | 11kV NCTs 600-300/1-1-1A (for PCVCBs upto 10 MVA Transformer) (As per ESCOM's CSR- 2025-26 33KV Material. page No- 81 SL.No-14, Item No-2.10) | No's | 1 | 66582 | 66582
A.5 |  | 33KV Voltage Transformers |  |  |  | 0
| a) | Voltage Transformers 33 kV/√3 / 110 V/√3 - 110 V/√3 (As per ESCOM's CSR- 2025-26 33KV Material. page No- 81 SL.No-16, Item No-2.12) | No's | 0 | 53234 | 0
A.6 |  | Surge Arrestors, Metal Oxide, as per Technical Specification. |  |  |  | 0
| a) | 30KV, 10KA normal duty Polymeric with terminal connectors suitable for Coyote Conductor (As per ESCOM's CSR- 2025-26 33KV Material. page No- 81 SL.No-18, Item No-3.01) | No's | 3 | 11583 | 34749 | Not updated in new SR
| b) | 10 kV, 5 kA Lightning Arrester Polymeric type with GROUND DISCONNECTOR), (As per ESCOM's CSR- 2025-26 33KV Material. page No- 13 SL.No-184 Item No-19.02) | Set (3 Nos) | 3 | 1735 | 5205
A.7 |  | 33 KV Isolators : |  |  |  | 0
| 1) | 33KV, 800A, 25 KA Class Double Break manually operated isolators with Pad connectors suitable for Coyote ACSR Conductor, as per technical specification with Solid Core, cylindrical post insulators |  |  |  | 0
| a) | a) 33 kV, 800 A, 25 kA Upright without Earth Switch (As per KPTCL SR- 2023-24 Page No.34 SL.No-9, Item No-9.14.1 HSN Code-8535, RS-84700/-) | Nos | 1 | 70583 | 70583 | Not updated in new SR
| 2) | 11 KV Isolators 400A with manually operated isolators with Pad connectors suitable for Lynx ACSR Conductor, as per technical specification with cylindrical post insulators |  |  |  | 0
| a) | 11KV 400A Special Roaster switch with H frame for mounting Structure.(As per ESCOM's CSR- 2025-26. page No- 17 SL.No-220 Item No-24.09) | Set | 3 | 13295 | 39885
| b) | 11KV 400A Double break GOS with H frame for mounting Structure(Dwg No. BESCOM/GM/QS&S/22 Dtd 24.11.2018), (As per ESCOM's CSR- 2025-26 33KV Material. page No- 16 SL.No-215 Item No-24.04) & (As per ESCOM's CSR- 2025-26 page No- 16 SL.No-217 Item No-24.06) | Set | 4 | 23987 | 95948
A.8 |  | 11kV Switch Gear |  |  |  | 0
| a) | 11 kV PCVCB, 350 MVA, 25 kA, 1250 A incomer, 800 A feeder (SCADA compatible) comprising of INCOMER ( MEI MAKE ) (As per KPTCL SR- 2025-26, No- 12, SL.No-218), | No | 1 | 732583 | 732583
| b) | 11 kV PCVCB, 350 MVA, 25 kA, 1250 A Feeder 800 A feeder (SCADA compatible) comprising of Feeder( MEI MAKE ) (As per KPTCL SR- 2025-26, No- 12, SL.No-219), | No | 3 | 559627 | 1678881
| c) | Annunciator Panel for the following combinations (for both MCVCB & PCVCB), 1IC+4F+1CB (As per KPTCL SR-2025-26, No- 13, SL.No-251) | No | 1 | 151922 | 151922
A.9 |  | CAPACITOR BANK with 0.2% Series Reactor & NCT |  |  |  | 0
| a) | Design, engineering, supply, erection of Capacitor Bank with internal fuses, terminal connector, Neutral CTs & 0.2% series reactors on neutral side with elevating/mounting structure and with 10% spare capacitors complete, 12.1 kV, 2.9 MVAr Star connected Capacitor Bank (This does not include breaker, panel, civil works like excavation and foundation concreting works),(As per KPTCL SR 2025-26,Volume-6,Page No.39,Sl.No.12,Item No.12.1.7) | Set | 1 | 448708 | 448708
| b) | 11 kV PCVCB, 350MVA, 25 kA, 1250 A feeder (SCADA compatible) Feeder Panel for Capacitor Bank (As per KPTCL SR- 2025-26, No- 12, SL.No-220) | No. | 1 | 618203 | 618203
A.10 |  | MOUNTING STRUCTURES:With including fabrication and galvanisation. |  |  |  | 0
| a) | Mounting Structure: 33KV, 800A, 25 KA Class Double Break manually operated ISOLATOR Live point height 3750 mm - 2Nos. (As per KPTCL SR- 2025-26, No- 02, SL.No-16) ii) (The weight of structure is 0.240t X2 Nos=480t) | t | 0.48 | 106667 | 51200.16 | #REF!
| b) | Mounting Structures:33KV Potential Trasformers -0.142x 3Nos =0.426 t (As per KPTCL SR 2023-24, Page No-245 Sl.NO:I,Item.No:E (3)(d), As per KPTCL SR- 2025-256 No- 02, SL.No-16) | t | 0.426 | 106667 | 45440.142 | 0.142+
| c) | Mounting Structures:33KV Current Trasformers- 0.142x 3Nos =0.426 t As per KPTCL SR- 2025-26, No- 02, SL.No-16) | t | 0.426 | 106667 | 45440.142
| d) | Mounting Structures:33KV Lightning Arrestors - 0.082 x 3 Nos =0.0.246 tAs per KPTCL SR- 2025-26, No- 02, SL.No-16) | t | 0.21 | 106667 | 22400.07
| e) | Mounting Structures: P.I. Support (33kv side): 0.082x 9 Nos =0.738 t As per KPTCL SR- 2025-26, No- 02, SL.No-16) | t | 0.738 | 106667 | 78720.246
| f) | Mounting Structures:11KV NCT 1 No. 0.146x 1 No =0.146 t As per KPTCL SR- 2025-26, No- 02, SL.No-16) | t | 0.146 | 106667 | 15573.382
| g) | Mounting Structures:High P.I. Support (11kv side) 6 Nos As per KPTCL SR- 2025-26, No- 02, SL.No-16) | t | 1.32 | 106667 | 140800.44
| h) | Bolts & Nuts for all Station Mounting Structures, such as, A)3T1- (0.017t), 3B1 (0.010t), As per KPTCL SR 2023-24, Page No. 244, Sl. No. I; Item No. (D)(i.ii). B)33KV PT (0.010t X 3 =0.030t)Asper KPTCL SR 2023-24, Page No. 245,Sl. No. I; Item No.(E)3 (d). C) 33KV CT (0.010t X 3 =0.030t) Asper KPTCL SR 2023-24, Page No.245,Sl. No.I; Item No.(E)2 (d). D) 33KV LAs( 0.005X3=0.015) Asper KPTCL SR 2023-24, Page No.245,Sl. No.I; Item No. E) 4(d). E) 33KV PI (0.005x 9 =0.045 t) ( Asper KPTCL SR 2023-24,Page No-247 Sl.NO:II, Item.No:E (iv), F)11KV NCT(0.011x 1 No =0.011t) (Asper KPTCL SR 2023-24, Page No-247 Sl.NO:II, Item.No:D(viii), G)11KV High P.I(0.011x 6 No =0.066t). (Asper KPTCL SR 2023-24, Page No-247 Sl.NO:II, Item.No:E(viii), (Bolts & Nuts Rate, As per KPTCL SR 2025-26; Page No-43;Sl.No.18 Item No.18.3) Rs 142780.00t | t | 0.224 | 118983 | 26652.192 | Not updated in new SR
A.11 | a) | S.M. Rail angle for Transformer plinth ( 2 nos. of 3m long) SM rail. (As Per KPTCL SR-2023-24, Page No:116, Sl.No.10, Set Rs=1626.00) and .M.S angle 75 x 75 x 6 mm angle iron 8 mtr long 0.2 MT each.(As Per PWD Electrical SR-2023-24, Page No:19, Sl.No.5.40, Item No:5.41.3, Per Mtr Rs:555 X 8 = Rs.4440.00) ,(1626+4440=6066.00) | Set | 1 | 5055 | 5055 | Not updated in new SR
A.12 |  | Conductors |  |  |  | 0
| a) | Lynx ACSR (30/2.79 mm Al + 7/2.79 mm St), Std Wt: 842 Kg/KM As per KPTCL SR- 2023-24, No- 02, SL.No-23) | Kms. | 0.6 | 187500 | 112500
| b) | Coyote ACSR (26/2.54 mm Al + 7/1.90 mm St), Std Wt: 521 Kg/KM As per KPTCL SR- 2025-26, No- 02, SL.No-24) | Kms. | 0.1 | 135537 | 13553.7
A.13 |  | 11KV ODS: |  |  |  | 0
| a) | 9 Mtr. Long, 145kg RCC pole for 11KV ODS (As per ESCOM's CSR- 2025-26 33KV Material. page No- 3 SL.No-1 Item No-1.01) | Nos | 8 | 6276 | 50208 | Not updated in new SR
| b) | RCC Pole - 8 Mtr Long, 115 Kg WL for LED Light ( ( As per ESCOM's CSR- 2025-26. page No- 3 SL.No-3 Item No-1.03) | Nos | 2 | 4706 | 9412 | Not updated in new SR
A.14 |  | 33 kV side Station Structure |  |  |  | 0
| a) | Station structures Tower - 3T1 with peak and Fabrication, galvanising and supply of Mild Steel tower materials As per KPTCL SR- 2023-24, No- 02, SL.No-16) | t | 0.696 | 106667 | 74240.232 |  |  | 0
| b) | Station structures Beam - 3B1 (6M Width), As per KPTCL SR- 2023-24 No- 02, SL.No-16) | t | 0.184 | 106667 | 19626.728
A.15 |  | 11 KV D.P.Structures: |  |  |  | 0
| a) | D.P. Structures with hardware consisting of double power X-arms, horizonontal cross brace, cross braces, back cleat, strain plate, bolt & nuts, painted with two coats of metal primer and aluminium paint, etc as per drawing. ( As per ESCOM's CSR- 2025-26. page No- 17, SL.No-225 Item No-26.02) | Set | 3 | 7374 | 22122
A.16 |  | Control Cable with Accessories: (With glands/lugs/ferruels) |  |  |  | 0
| a) | 19 Core 2.5 Sq.mm (As per KPTCL SR- 2025-26, No- 10, SL.No-181) . | Kms. | 0.5 | 590833 | 295416.5
| b) | 4 Core 6 Sq.mm (As per KPTCL SR-2023-24, Page No:40 Sl No-13, Item No:13.8, HSN Code:8544, Rs:247*1000=.247000 Total Rs =247000) | Kms. | 0.35 | 205833 | 72041.55
| c) | 4 core 2.5 Sq.mm As per KPTCL SR- 2025-26, No- 10, SL.No-176) | Kms. | 0.25 | 149167 | 37291.75
| d) | 2 core 2.5 Sq.mmAs per KPTCL SR- 2025-26, No- 10, SL.No-175) | Kms. | 0.6 | 92500 | 55500
| e) | 10 Core 2.5 Sq.mm As per KPTCL SR- 2025-26, No- 10, SL.No-179) | Kms. | 0.09 | 340833 | 30674.97
A.17 |  | Insulators & Hardware materials: |  |  |  | 0
| a) | Pad clamp for Coyote ACSR As perESCOM's CSR- 2025-26. page No- 7 SL.No-77 Item No-10.09 | Nos | 0 | 734 | 0
| b) | Pad clamp for Lynx ACSR As per KPTCL SR-2025-26, No- 3, SL.No-45) | Nos | 36 | 725 | 26100
| c) | T clamp for Coyote ACSR As per ( As per ESCOM's CSR- 2025-26. page No- 7 SL.No-75 Item No-10.07) | Nos | 0 | 426 | 0
| d) | T clamp for Lynx ACSR As per KPTCL SR- 2025-26, No- 5, SL.No-87) | Nos | 24 | 527 | 12648
| e) | 33KV CT bimetalic clamps for Lynx ACSR (As per present market rate) | Nos | 6 | 1000 | 6000
| f) | NCT Pad Clamp As per KPTCL SR- 2025-26, No- 5, SL.No-74) | Nos | 2 | 849 | 1698
| g) | Post Insulator Clamps As per KPTCL SR- 2025-26, No- 5, SL.No-74) | Nos | 12 | 846 | 10152
| h) | Terminal Connector Clamps Suitable for 36 kV class bushing to suit Coyote / Lynx conductor for HV Bushings of Power Transformers (Asper KPTCL SR-2023-24, Page No 135, Sl.No-E Item No-viii HSN Code:8536 Total Rs =512) | Nos | 3 | 427 | 1281 | Not updated in new SR
| h) | Terminal Connector Clamps Suitable for 12.1 kV class bushing to suit Drake conductor for Bushings of Power Transformers (As per KPTCL SR-2023-24, Page No 135, Sl.No.2E Item No-ix HSN Code:8536 Total Rs.1113/-) | Nos | 4 | 928 | 3712 | Not updated in new SR
| i) | Strain Clamp for Lynx ACSR, ( As per ESCOM's CSR- 2025-26. page No- 5 SL.No-46 Item No-5.16) | Nos | 54 | 588 | 31752 | Not updated in new SR
| j) | Solid Core Bus Post Insulator 33 kV As per KPTCL SR- 2023-24, No- 11, SL.No-186) | Nos | 12 | 3060 | 36720
| k) | 70 KN Disc Insulators Ball and socket type ( As per ESCOM's CSR- 2025-26. page No- 82 SL.No-25 Item No-6.03) | Nos | 60 | 390 | 23400
| l) | I bolts (As per present market rate) | Nos | 42 | 55 | 2310
A.18 |  | Ground Mat & Earthing : |  |  |  | 0
| a) | Grounding of equipment by providing Cast iron pipe of 100 mm ID 13 mm thickness, 2.75 metre long with 2 part clamp out of G.I. Flat 50 X 6 mm continuously welded alround the pipe using cast iron welding electrodes as per drawing including the cost of excavation (All materials to be supplied by the contractor) (As per KPTCL SR-2023-24, Page No:115, Sl.No-6 Item No:c Material Rs-12792+3491 Labour | Set | 51 | 13569 | 692019 | Not updated in new SR
| b) | Supplying & providing 450 mm dia 450 mm height 1.5" to 2" thick hume pipe collar (non pressure type) for earth pits including all lead and lifts etc.,.(As per KPTCL SR-2023-24, Page No:124, Sl.No-26 Item No:i Material Rs-1499.00 | Each | 51 | 1249 | 63699 | Not updated in new SR
| c) | Grounding of equipment with 50X6 mm GI flat & connecting equipment to the earth mat / ground pit. Each point of Earthing with all formation works like bending, twisting, drilling of holes & conncting by welding (inclusive of all T & P consumables) to the earth mat/ ground pit/point of earth connection, all the materails supplied by the contractor (As per KPTCL SR-2023-24, Page No:123, Sl.No-26 Item No:i Material Rs-335.00 | Rmt | 305 | 279 | 85095 | Not updated in new SR
| d) | Supplying and laying of MS Flats of various sizes, welding and applying ACB paint to welded portion and covering with sodium bentonite clay as per the drawing/standard specification and consolidation (MS Flat of size 50x6 ) (As per KPTCL SR-2023-24, Page No:123, Sl.No-26 Item No:f Material Rs-404.00 | m | 368 | 337 | 124016 | Not updated in new SR
A.19 |  | Miscellaneous items: |  |  |  | 0
| a) | Caution/Danger Board (As per KPTCL SR- 2025-26, No- 31 of 50, SL.No-687) | Nos | 6 | 131 | 786 | Not updated in new SR | #VALUE! | 131 | 157.2
| b) | Phase plates (As per KPTCL SR 2023-24, Page No.43, Sl. No.19, Item No,19.1, Rs.528/- | Set (3 Nos) | 3 | 440 | 1320 | Not updated in new SR
| c) | Name Plates for equipment/Earth Pit (As per present market rate due to non availability of rates in the current SR) | Nos | 65 | 250 | 16250
| d) | Name plate for feeders and banks (As per present market rate due to non availability of rates in the current SR) | Nos | 4 | 250 | 1000
A.20 | a) | Station yard LED outdoor light fitting Higher end Philips / Havells / Equivalent complete fitting set. |  |  |  | 0
|  | Supply of 90W LED yardlight with pressure die cast aluminium housing body with optimal heat sink for better thermal dissipation. Lamp compartment comprising of anti glare clear diffuser with Injection moulded polycarbonate material, delivering superior light output. Rated life Burning Hrs 50000 hr & Lumen Mainanance of 70%, maximum light intensity should be between 60 degrees to 70 degrees. CCT > 5500K, IP 66 optiical and electrical compartment & impact resistance of complete luminare > IK08. Power Factor > 0.9 with mains Surge Protection - Min 5KV along with over Voltage / Overload, short circuit / miswiring protection. Compatible for pole mounting with outer dia of 40mm to 50mm. Universal Voltage driver to operate wide voltage range from 100V to 270V 50/60 Hz application. Overload & Short circuit protection ensures reliable operation in spite of problem in output side. Compliance to IS 10322/IEC 60598, LM 79 & LM 80 Adherence with RoHS. UL approved MCPCB. Top access street light with single screw to ensure ease of maintanance at the sight location with minimized minimal tools. LED light fixture with ...90 W System Power Consumption. LED Efficiency>130lm/w nominal CRI. 75. LImunaire manufacturer should have in-house facilitty accredited by NABL/CPRI & any Government certified agency & Design & Development facility certified by ISO 9001:2008. Housing with supplier word mark /name shall be Engraved / Embossing on the die cast housing / Body part. warranty of 2 Years against any manufacturing defect working under standard electrical conditions as mentioned above should be given by LED manufacture & Cree/Nichia/Lumileds/Osram make LED Source. Elec. KPWD Ele SR 23-24 (Pg No.45 of 105, item No 11.8.4) | Nos | 2 | 7383 | 14766
| b) | 2 Core , 6 Sq. mm, 1.1KV class armoured Al. Cable including PVC pipes for Yard Lighting complete. ,Material Page No: 4 of 28, Sl No.1,item no.1.12.2,Material Rate Rs.120.32 | Mtrs | 30 | 129 | 3870
| c) | 32 Amps, DP Switch for Yard Lighting complete.(As per PWD SR 2023-24 Pg no.9 of 105,Sl.no.3.6,item no.3.6.9)Supplying and fixing. Rs-326 | Nos. | 2 | 272 | 544
| d) | MCB 6-32 A DP (Supplying & fixing miniature circuit breakers on existing MCB distribution boards using necessary fixing materials and 'C' Type curve, indicator ON/OFF, energy cross-3 with Short circuit breaking capacity of 10K and complete wiring as required confirming to IEC 60898 ) (As per PWD SR 2023-24 Pg no.17 of 105,Sl.no.5.18,item no.518.4). Rs-739.00 | Nos. | 2 | 616 | 1232
A.21 |  | Station Service Equipments: |  |  |  | 0
| a) | Single line diagram Photo sheet paper (Size 20x20 inch) (As per present market rate) | Nos | 2 | 1167 | 2334
| b) | First Aid Emergency Medical Kit Box (As per PWD SR 2023-24, Page No.93 of 105 Sl.No.15, Item No,15.114, Rs600/-) | Nos | 2 | 500 | 1000 | Not updated in new SR
| c) | Supplying of FIRST AID CHART with lamination. Complete (As per PWD SR 2023-24, Page No.93 of 105 Sl.No.15, Item No,15.116, Rs 400/-) | Nos | 2 | 333 | 666 | Not updated in new SR
| c) | Supplying and installation of Rubber mat 1mtr x 1mtr -1Omm thick.complete including cost of materials, labour, usage charges of machinery complete as per specifications. (As per PWD SR 2023-24, Page No.93 of 105 Sl.No.15, Item No,15.117, Rs 1900/-) | Nos | 8 | 1583 | 12664 | Not updated in new SR
A.22 |  | Furniture: |  |  |  | 0
| a) | Steel Almirah 6/3 feet | Nos | 1 | 12500 | 12500
| b) | Officer Table | Nos | 1 | 4167 | 4167
| c) | Steel slotted angle rack | Nos | 2 | 2500 | 5000
| d) | Steel dust bins. | Nos | 2 | 208 | 416
| e) | Executive S Type chair | Nos | 1 | 4167 | 4167
| f) | Plastic Moulded chair | Nos | 6 | 375 | 2250
A.23 |  | Maintenance Tools and Plant: |  |  |  | 0
| a) | Portable (mobile) Oil Pump (1/2 HP Air Pump 500 to 1000 gallons (As per KPTCL SR-2023-24, Page No:53, Sl.No:35, Item No:35.1 HSN code- 8413 Rs-20247 | Nos | 1 | 16873 | 16873
| b) | Telescopic ladder aluminium 6 mtr. Height. (As per KPTCL SR-2023-24, Page No:53, Sl.No:35, Item No:35.2 HSN code- 7306 Rs-22622 | Nos | 1 | 18852 | 18852
| c) | Ring spanners - 12 nos. per set (As per KPTCL SR-2023-24, Page No:53, Sl.No:35, Item No:35.3 HSN code-8207 Rs-880.00) | Set | 1 | 733 | 733
| d) | Double end spanner - 12 nos. per set (As per KPTCL SR-2023-24, Page No:53, Sl.No:35, Item No:35.7 HSN Code-8207 Rs829.00) | Set | 1 | 691 | 691
| e) | Pipe wrench 18 inches size (As per KPTCL SR-2023-24, Page No:53, Sl.No:35, Item No:35.6 HSN Code-8207 Rs-692.00) | Nos | 1 | 577 | 577
| f) | Rubber hand gloves (15KV tested) SEAMLESS, Confirming to ISS (Sample to be verified for seamless before approval) for electrical purpose (As per ESCOM SR- 2025-26, Page No- 29 of 50, SL.No-635) | pairs | 4 | 244 | 976
| g) | Screw driver 12 inch (As per KPTCL SR-2023-24, Page No:53, Sl.No:35, Item No:35.16 HSN Code-8207 Rs-75.00) | Nos | 4 | 63 | 252
| h) | Hammer 2 lbs (As per KPTCL SR-2023-24, Page No:53, Sl.No:35, Item No:35.18 HSN Code-8205 Rs-249.00) | Nos | 2 | 208 | 416
| i) | Grounding sticks extendable upto 18 ft - 3 nos. of each 6 ft Sticks of 3 phase R, Y, B (3 nos. of 1 set) (As per KPTCL SR-2023-24, Page No:54, Sl.No:35, Item No:35.51 HSN Code-7215 Rs-1755.00) | Set | 4 | 1463 | 5852
Total material cost | [5 empty] | 8754879.204

## Erection
HUBLI ELECTRICITY SUPPLY COMPANY LIMITED
Estimate for Providing additional 3rd 5 MVA, 33/11KV power transformer at 33/11KV sub-station Gandigwad in Khanapur Taluk, Belagavi District in 33KV S&L Division, Belagavi on PTK basis (5 MVA Power Transformer will be supplied by departmentally)
PART-B (Electricals Erection Works)
Sl. No. |  | Particulars | Unit | Qty | Rate as per SR 2025-26 | Amout in Rs.
1 | 1 |  | 3 | 4 |  | 6
B.1 | a) | Power Transformers: Moving the Transformer to the plinth. (15 MT for 20 mtrs) on ramp. (As per KPTCL SR-2023-24 Page No-116, Sl.No-9, Item No-(a)) Rs-80/- | per MT/ mtr | 300 | 67 | 20100
| b) | Assembly of Transformer parts like bushings, radiators, filling oil into Transformer etc., for the total weight of the Transformer. (As per KPTCL SR-2023-24 Page No-116, Sl.No-9, Item No-(b)) 1134.00 | MT | 15 | 945 | 14175
| c) | Filtration of oil using filter set of the contractor, to bring the insulation value to I.E. Specifications.(As per KPTCL SR-2023-24 Page No-116, Sl.No-9, Item No-(d)) Rs-7.00 | ltrs | 3500 | 6 | 21000
| d) | 5 MVA to 6.3/8 MVA Tr Wiring: Identification of wires,Wiring of Transformer marshalling box, bucholtz relay, OLTC upto control panel Ferruling crimping and termination of wires. Wiring of Protective Devices, OLTC, RTCC , fixing Thermometer, etc.,including assisting in Testing & Commissioning: (As per KPTCL SR-2023-24 Labour,Page No-116, Sl.No-9, Item No-(f&i)) 6708 | per transfor mer | 1 | 5590 | 5590
| e) | Fabrication of Transformer railing & embedding in Transformer plinth. (As per KPTCL SR-2023-24 Labour, Page No-116, Sl.No-10,Rs-1626 | Set | 1 | 1355 | 1355
B.2 | a) | 33KV SF-6/ VCB Breakers: Breaker Erection, assembly, alignment & wiring of breakers with its connected equipments including movement from the point of unloading to the point of erection. (As per KPTCL SR-2023-24 Labour,Page No-117, Sl.No-13, Item No-(a) Rs-5934 | Per Set | 2 | 4945 | 9890
| b) | Assisting in Testing & Commissioning: (As per KPTCL SR-2023-24 Labour, Page No-117, Sl.No-13, Item No-(b) Rs-1938.00 | Set | 2 | 1615 | 3230
| c) | Wiring : Identification, Ferruling crimping and termination of wires in Breaker & Wiring up to control panel/Relay panels. (As per KPTCL SR-2023-24 Labour,Page No-117, Sl.No-13, Item No-(c) Rs-8487 | Set | 2 | 7073 | 14146
B.3 | a) | Control Panels : Erection of control panel, auxilary panel, carrier cabinet etc., alignment and fixing properly to foundation base including movement from the point of unloading to the point of erection.(As per KPTCL SR-2023-24 Labour,Page No-120, Sl.No-23, Item No-(a) Rs-4191 | Nos. | 2 | 3493 | 6986
| b) | Wiring & Assisting in Testing & Commissioning: (As per KPTCL SR-2023-24 Labour,Page No-120, Sl.No-23, Item No-(b) Rs-7612.00 | Nos. | 2 | 6343 | 12686
B.4 | a) | Erection of CTs and wiring including movement from the point of unloading to the point of erection. (As per KPTCL CSR 23-24, Labour, Page No: 118, Sl No.: 14 a) Rs-2199 | Set (3 Nos) | 2 | 1833 | 3666
| b) | Assisting in Testing & Commissioning: (As per KPTCL CSR 23-24, Labour, Page No: 118, Sl No.: 14 (b) Rs-768.00 | Set (3 Nos) | 2 | 640 | 1280
B.5 | a) | Erection of NCT's including movement from the point of unloading to the point of erection with grounding connections (As perKPTCL CSR 23-24, Labour, Page No: 118, Sl No.:15(a) Rs-733.00 | Set | 1 | 611 | 611
| b) | Assisting in Testing & Commissioning:(As per KPTCL CSR 2023-24, Labour, Page No: 118, Sl No.:15(c) Rs-99.00 | Set | 1 | 83 | 83
B.7 | a) | Erection of Lightning arrestors and wiring including movement from the point of unloading to the point of erection (33 KV) (As per KPTCL CSR 23-24, Labour, page No119, Sl.No:18 )Rs.333/- | Set | 1 | 278 | 278
| b) | 9 KV, 5 KA class (Station type) (11kv) (As per ESCOM'S SR 23-24, Labour, page No: 48 of 81, Sl.No:101, item no: 13.06) Rs-119.00 | Set (3 Nos) | 9 | 99 | 891
B.8 | 1) | 33 KV Isolators : |  |  |  | 0
| a) | Erection of Isolators (33 KV) Assembly, Errection alignment and wiring including movement from the point of unloading to the point of erection.(Upright type),( As per KPTCL CSR 23-24, Labour, Pg No: 119, Sl No.: 17 A(i) ,) Rs-1319.00 ) | Set | 1 | 1099 | 1099
| b) | Assisting in Testing and Commissioning ( KPTCL CSR 23-24, Labour, Pg No:119 , Sl No.: 17 E(i) ,) Rs-191/- | Nos | 1 | 159 | 159
| 2) | 11KV Isolators: |  |  |  | 0
| a) | Erection of 400A, special roster switch with H-frame & clamps to be mounted on DP (As per ESCOM SR- 2025-26, Labour, Pg No:58 Sl No.: 37 ,itme no: 2.09) (Rs - 288) (Total - 1082+288=1370) | Nos | 3 | 1370 | 4110
| b) | Erection of 11 kV, 400 Amps Double Break GOS (As per ESCOM SR- 2025-26, Labour, Pg No:58 Sl No.: 37 ,itme no: 2.09) (Rs - 288) (Total - 1082+288=1370) | Nos | 4 | 1370 | 5480
B.9 | a) | 11 KV Switchgear : Erection, alignment and fixing to the foundation, indoor/outdoor 11KV switchgear Panel/unit including movement from the point of unloading to the point of erection. (1Bank+3 feeders) (As per KPTCL SR 23-24, Labour, page No: 121, Sl.No:24 a (i) ) Rs-2081/-) | Per Panel | 4 | 1734 | 6936
| b) | Wiring and assisting in Testing & Commissioning: (As per KPTCL SR 23-24, Labour, page No: 122, Sl.No:24 b (i) ) Rs-941.00 | Per Panel. | 4 | 784 | 3136
B.10 | a) | 33KV Station structures: |  |  |  | 0
|  | Erection, alignment & assembly of fabricated steel lattice structure, pedestal structures & Mounting structures, for G.O.S., CTs, PTs LAs etc. (As per KPTCL SR 23-24, Labour, Page No: 116, Sl No.: 8, (b) , Rs-5723.00 | MT | 4.626 | 4769 | 22061.394
B.11 | a) | Bus Formation |  |  |  | 0
|  | Formation of cross bus in each individual bay using Lynx/Coyote -Single/Double conductor with fixing of insulators, spacers, levelling the strung conductors to the required height above the equipment including providing jumps to inter-connect different segments of the main bus. ( As per KPTCL SR 23-24, Labour, Page No: 122, Sl No.: 25) Rs-7364.00 (Incuding 33KV Bus Formation) | Per bay | 4 | 6137 | 24548
B.12 | a) | 11KV ODS: |  |  |  | 0
|  | 1) Digging of Pit 1.8 Mtr depth (Hard Soil) for errection of 9Mtr 11KV ODS pole- ESCOMs Labour SR-23-24 Page No- 43 of 81 Sl.No-2 Item No-1.1.2 RS- 11322) Errection of 9 Mtr. Long, 145kg RCC pole for 11KV ODS.(As per ESCOMs Labour SR-2025-26 Page No- 57 Sl.No-1 Item No-1.1.1 RS- 561) 2) Errection of 9 Mtr. Long, 145kg RCC pole for 11KV ODS. (As per ESCOMs Labour SR-2025-26 Page No- 58 Sl.No-30 Item No-2.02) RS-991 (Total Rs 561+9991=1552) | Nos | 8 | 1552 | 12416
| b) | 1) Digging of Pit 1.6 Mtr depth (Hard Soil) for erection of 7.5/8 Mtr Long Steel/RCC pole for LED Light ( As per ESCOMs Labour SR-23-24 Page No- 43 of 81 Sl.No-6 Item No-1.2.2 Rs.1006/- ) 2) Errection of RCC Pole - 8 Mtr Long, 115 Kg WL. (As per ESCOMs Labour SR-23-24 Page No- 44 of 81 Sl.No-29 Item No-2.01 RS-922 Total Rs-1928 | Nos | 2 | 1270 | 2540
| c) | Supplying and fixing angle iron frame work fabricated out of M.S. angle iron.. and M.S. Flat......with bolts, washers etc., and painted with 2 coats of red oxide and then two coats of approved paint for 11 KV ODS mounting structure using 50 x 100 x 50 x 6 mm C channel MS, each 4.0 mtr long , As per PWD Electrical Page 19 Sl.No-5.41.4 Rs-Per Mtr-756.00 28NosX4Mtr=112 Mtr | Mtr | 100 | 630 | 63000 |  | 112
B.13 |  | Erection of station structure 3T1 Tower and 3B1 Beams Asper KPTCL Labour SR-2023 -24 Page No-113, Sl.no-1, item No 1.1© Rs-5723.00,(3T1 Tower T-0.730+3B1-0.194=0.924) | t | 0.924 | 4769 | 4406.556
B.14 |  | Erection of 2 Pole DP Structure using RCC/PSCC Pole 9 to 10 Mtr long (As per ESCOMs Labour SR-2025-26 Page No- 58 Sl.No-34 Item No-2.06) | Per Structure | 3 | 3682 | 11046 | 1403 only dp |  | 1341
B.15 |  | Laying of control cables from equipments to control panels. |  |  |  | 0
| a) | 19 Core 2.5 Sq.mm (As per KPTCL SR 23-24, Labour, page No: 120, Sl.No:22, (b) Rs- Per Mtr-15.00 | Rmtr | 500 | 13 | 6500
| b) | 4 Core 6 Sq.mm (As per KPTCL SR 23-24, Labour, page No: 120, Sl.No:22, (b) Rs- Per Mtr-15.00 | Rmtr | 350 | 13 | 4550
| c) | 4 core 2.5 Sq.mm (As per KPTCL SR 23-24, Labour, page No: 120, Sl.No:22, (b) Rs- Per Mtr-15.00 | Rmtr | 250 | 13 | 3250
| d) | 2 core 2.5 Sq.mm (As per KPTCL SR 23-24, Labour, page No: 120, Sl.No:22, (b) Rs- Per Mtr-15.00 | Rmtr | 600 | 13 | 7800
| e) | 10 core 2.5 Sq.mm (As per KPTCL SR 23-24, Labour, page No: 120, Sl.No:22, (b) Rs- Per Mtr-15.00 | Rmtr | 90 | 13 | 1170
A.17 |  | Miscellaneous items |  |  |  | 0
| a) | Fixing Caution/Danger Boards (As per KPTCL SR- 2023-24, Page No- 34 of 50, SL.No-2, 35 of 50, SL.No-30) | Nos | 6 | 198 | 1188
| b) | Fixing Phase Plates As per KPTCL Labour SR 23-24,Pg No.113 ,Sl No.3(c) Rs-238 | Set (3Nos) | 3 | 45 | 135 | 71.5986
| c) | Fixing Name Plates for equipment/Earth Pit ,KPTCL SR 21-22, page No-09 of 27 Sl No-7 Item No:- (d), Labour Charge Rs.54 | Nos | 10 | 45 | 450
| d) | Name plate for feeders and banks KPTCL SR 21-22 , Labour Charge No-09 of 27 Sl No-7, Item No:- (d),Rate Rs.54 | Nos | 4 | 135 | 540
A-18 |  | Fixing halogen/metal halide /SVL/IL/LED floodlight fitting over existing pole / wall ceiling including clamps, bolts, nuts and wiring using suitable capacity wires. As per PWD Ele SR 2-2023-24 Page No-56 Of 105,Item No:13.5 | Each | 2 | 133.8843 | 267.7686
A-19 | a) | Existing 63KVA Auxillary Transformers |  |  |  | 0
|  | Releasing of Existing 63KVA station Auxillary TC Asper BESCOMs SR-2023-24 Labour Charge Cast Data sheet No-25 Sl No-5, Rate Rs.1193X90%=1073.70 | No | 0 | 1371 | 0 | 1073.7
| b) | Re-Erection of Existing 63KVA Station Auxillary TC (As per KPTCL SR- 2023-24, Page No-35 of 50, SL.No-46) | No | 0 | 1523 | 0
Total Labour cost | [5 empty] | 302761.7186 |  |  | 359066.65

## GNDWD Civil (2)
HUBLI ELECTRICITY SUPPLY COMPANY LIMITED
Estimate for Providing additional 3rd 5 MVA, 33/11KV power transformer at 33/11KV sub-station Gandigwad in Khanapur Taluk, Belagavi District in 33KV S&L Division, Belagavi on PTK basis (5 MVA Power Transformer will be supplied by departmentally)
PART-C-(CIVIL WORKS)
Sl No. | Item Description |  | Unit | Qty | Unit Price (Rs) | Total Price (Rs)
1 | 2 |  | 3 | 4 |  | 6
C |  | SCHEDULE OF ITEMS FOR ASSOCIATED CIVIL WORKS AND STRUCTURES:
C.1 |  | Cable Trenches including road crossing :
| a) | RCC Cable duct for laying of control cables with cable tray.(Duct size:1 mtr WidthX 1 mtr DepthX 26 Mtr Length including 33 KV and 11 KV side) | Mtrs | 26 | 6387.5 | 166075
| b) | b) Providing and Laying RCC Hume pipe sub ducts using NP 2 class 300mm dia Hume pipe including cost of Excavation, laying charges and back filling wherever required as per technical specification and enclosed drawings including cost of all materials, labour, etc., complete. | Rmtrs | 0 | 710.8333 | 0
| c) | Cable duct covers RCC made with suitable size to cover the duct length of 35 Mtrs ( of Size 1m x 1m x 0.15m) | Nos | 52 | 1411.6667 | 73406.6667
C.2 |  | SITE SURFACING: Jelly Spreading (20-25 mm) : Supplying and providing jelly in the station yard of uniform thickness of 100 mm including the cost of materials, labour charges, required tools and plants etc., complete. Work shall be carried out as per the instructions of Engineer- in-charge of works as per the standard procedure(As per KPTCL SR 2023-24,Page No.158,Sl.No.1) | Cmt | 60 | 1477.5 | 88650
C.3 |  | Foundations: Engineering, supply of all labour,material and construction of RCC footing including the cost of excavation, cement concreting, reinforcement, backfilling, waterproof cement painting, for all works, grouting underpinning etc ,for the following works |  |  | 0 | 0
| a) | 9 mtrs long RCC poles for ODS (As per ESCOM's SR 2023-24,Base concreting Rs.312+Pole concreting Rs.3434,Coping Rs.312) | No's | 8 | 3381.6667 | 27053.3333
| b) | 8 mtrs long RCC poles for station Yard lights (As per ESCOM's SR 2023-24,Base concreting Rs.312+Pole concreting Rs.1498+Coping Rs.312) | No's | 2 | 1760 | 3520
| c) | 33KV CT support structure (0.95 mtrX0.55 mtr X 1mtr Depth) | Nos | 3 | 4708.3333 | 14125
| d) | 33KV Surge arrestor support structure (0.95 mtrX0.55 mtr X 1mtr Depth) | Nos | 3 | 4708.3333 | 14125
| e) | PI support structure (0.95 mtrX0.55 mtr X 1mtr Depth) | Nos | 11 | 4708.3333 | 51791.6667
| f) | 11 KV NCT mounting structure (1.1 mtrX0.55 mtr X 1mtr Depth) | Nos | 1 | 4950.8333 | 4950.8333
| g) | 33KV Isolators support structure(0.95 mtr X 0.45 mtr X 1mtr) | Set | 1 | 4728.3333 | 4728.3333
| h) | PI support structure for raising the U.G cable | No. | 0 | 4708.3333 | 0
| i) | 3T Tower Foundation (1.5 m X .9 m x 2.5 m ) | Nos | 2 | 29958.3333 | 59916.6667
C.4 |  | Transformer foundation and associated rail track: |  |  | 0 | 0
|  | Design, Engineering,supply of material / equuipment, labour and construction of Tr. Foundation by providing all associated works, rail tracks jacking pads, anchor block RCC, PCC misscellanellaneous structural steel including MS, grouting gravel filling pylon support system and other items not mentioned herein, but required for the completion of the work as per the technical spcfication and drawings |  |  | 0 | 0
| a) | 5 MVA, 33/11 KV Transformer (3.3 mtr Width X 3.3 mtr Length X 3 mtr Depth) | Nos | 1 | 256005.8333 | 256005.8333
C.5 | a) | SF-6 Breaker foundation, 33KV SF-6 Breaker foundation as per approved design and drawing including supply of material and labour | Nos | 2 | 21872.5 | 43745
C.6 |  | Providing PVC ringtite pipes conforming to IS 4985:2000 with latest amendments and conveying to worksite, rolling and lowering into trenches, laying true to line and level and perfect linking at joints, testing and commissioning, including loading unloading at both destinations and cuts of pipes wherever necessary including jointing of PVC pipes and specials (excluding cost of specials) with jointing of approved type, with all labour with all lead & lift including encasing the pipe alround to a depth of not less than 15 cms. with soft gravel or selected earth available from the excavation etc. complete and giving necessary hydraulic test to the required pressure as per ISS (Contractor will make his own arrangements for procuring water for testing) etc. complete For: |  |  | 0 | 0
| a) | PVC pipes 63mm dia., 6 kg/sqcm & class 3 | Mtrs | 100 | 134.1667 | 13416.6667
| b) | PVC pipes 75mm dia., 6 kg/sqcm & class 3 | Mtrs | 50 | 183.3333 | 9166.6667
C.7 | a) | Earth mat formation : |  |  | 0 | 0
|  | Excavation, formation, refilling. | CMT | 304 | 168.3333 | 51173.3333
C.8 | a) | Design, Engineering,supply of material / equuipment, labour and construction of 11 KV out door PCVCB foundation by providing all associated works as per standard and approved specification. | No's | 4 | 36021.6667 | 144086.6667
| b) | Design, Engineering,supply of material / equuipment, labour and construction of 11 KV out door Capacitor Bank cells foundation by providing all associated works as per standard and approved specification. | Set | 1 | 22183.3333 | 22183.3333
C.9 | a) | Road Works : |  |  | 0 | 0
|  | Providing and forming 5 mtr wide Road including providing walk ways, fixing RCC kerb stones, RCC Road with M20 concrete within sub-station as per technical specification, layout and sectional detailed drawing etc., complete in all respect. | Rmtrs | 0 | 12811.6667 | 0
C.10 |  | Station security fencing with foundation | Rmtrs | 0 | 4461.6667 | 0
|  | Total Civil cost |  |  |  | 1048120