## Sheet1
NIT Schedulefor Shifting of 33 KV line, 4 Pole Structure, Transformer, 11 KV Line & LT Line due to road widening work Route from Rajim-Choubebandha-Nawagaon District Gariyaband under P.W.D. (E/M) Sub-Division Gariyaband PAC = 17.15 Lacs
SERIAL No. | Department | SOR | Year | Item Code | Description | UOM | QTY | Ref Serial No | CREDIT ITEM (0/1) | Calc Field (Y/N)
1 | PWD | ELECT | 2020 | 12.1 | Earthing with G.I. earth pipe 4.5 metre long, 40 mm dia including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe etc. with charcoal and salt as per specification and IS Code 3043: 1987(R 2016) | Set | 1 | 0 | 0 | N
2 | PWD | ELECT | 2020 | 12.12 | Supplying and laying 6 SWG G.I. wire at 0.50 metre below ground level for conductor earth electrode, including soldering, excavation and refilling the trench etc. as per specification. | Metre | 20 | 0 | 0 | N
3 | PWD | ELECT | 2020 | 12.17 | Providing and fixing 6 SWG dia G.I. wire on surface or in recess for loop earthing as per specification. | Metre | 10 | 0 | 0 | N
4 | PWD | ELECT | 2020 | 14.5 | Supplying and fixing G.I. pipe along with wall or pole/ support with 2 Nos MS clamps for protection of under ground cable in approved manner including bolts and nuts or metal dash fasteners complete as per specification. 14.5.2 40 mm dia | Metre | 10 | 0 | 0 | N
5 | PWD | ELECT | 2020 | 15.29 | Supplying fixing and cramping suitable size and all type Copper ferule / lugs to following size 1.1 KV grade power cable core/ lead, pressed with high pressure cramping tool including connection to switch gear / MCCB etc as per specification. 15.29.10 150 sq. mm | Each | 4 | 0 | 0 | N
6 | PWD | ELECT | 2020 | 15.29.13 | 300 sq. mm | Each | 8 | 0 | 0 | N
7 | PWD | ELECT | 2020 | 19.1 | Suppy of "H" beam steel pole as per IS specification in stander length for over head linw work. 19.1.2 "H" beam steel polw 152x152x7x12 mm standard rate 37.1 kg /meter | Metre | 74 | 0 | 0 | N
8 | PWD | ELECT | 2020 | 19.1 | Erection of STEEl TUBULAR or "H" BEAM /ISMB pole in cement concrete 1:3:6 (1 cement :3 coarse sand : 6 graded stone aggregate 40 mm nominal size) foundation and cement concrete collar of size 0.4 meter dia and 0.50 meter height from ground level including excavation and refilling etc. as per specification of length. 19.10.5 11 meter to 12 meter | Each | 2 | 0 | 0 | N | 0
9 | PWD | ELECT | 2020 | 19.10.6 | 13 meter to 14 meter | Each | 4 | 0 | 0 | N
10 | PWD | ELECT | 2020 | 20.1 | Supply and fixing following overhead line accessories. 20.1.1 Stay rod (19/20mm dia 1.8 metre long) with anchor plate 300x300x6.4mm in CC | Each | 36 | 0 | 0 | N
11 | PWD | ELECT | 2020 | 20.1.2 | Stay wire 7/4.0mm dia | kg | 50 | 0 | 0 | N
12 | PWD | ELECT | 2020 | 20.1.3 | Stay wire 7/3.15mm dia | kg | 155 | 0 | 0 | N
13 | PWD | ELECT | 2020 | 20.1.7 | MV Shackle insulator 75x90mm with G.I. bolts and nuts | Each | 192 | 0 | 0 | N
14 | PWD | ELECT | 2020 | 20.2 | Supplying and erection of stay set complete (galvanized) with 19/20mm dia x 1.8 metre long stay rod, anchor plate of size 300mm x 300mm x 6.4 mm, thimble stay clamps, turn buckle (19/20mm x 600mm), strain insulator and specified G.I. stay wire etc. in cement concrete 1:3:6 (1 cement : 3 coarse sand : 6 graded stone aggregate 40 mm nominal size) foundation including excavation and refilling etc. as per specification. 20.2.1 With 7/4.15 mm dia G.I. stay wire | Each | 1 | 0 | 0 | N
15 | PWD | ELECT | 2020 | 20.2.2 | With 7/3.15 mm dia G.I. stay wire | Each | 20 | 0 | 0 | N
16 | PWD | ELECT | 2020 | 20.6 | Supplying and erection of angle/channel iron cross arms/ bracket/ other fitting of approved size and shape including drilling of holes for insulator pins, bolts and nuts etc as per specification. | kg | 200 | 0 | 0 | N
17 | PWD | ELECT | 2020 | 20.15 | Supplying and fixing guard insulator or split insulator complete 20.15.1 25x25 mm | Pair | 44 | 0 | 0 | N
18 | PWD | ELECT | 2020 | 20.17 | Supplying and erection of MV horn gap lightening arrester. | Each | 4 | 0 | 0 | N
19 | PWD | ELECT | 2020 | 20.20 | Supplying and erection of 11 KV gang operated air break switch on existing two pole structure with insulators and all other accessories complete including locking arangement as per specification. | Set | 5 | 0 | 0 | N
20 | PWD | ELECT | 2020 | 20.21 | Supplying and erection of 11 KV D.O. fuse unit on existing two pole structure with insulators and all other accessories complete including locking arangement as per specification. | Set | 6 | 0 | 0 | N
21 | PWD | ELECT | 2020 | 20.30 | Supplying and erection of G.I wire of size 8 SWG to 4 SWG including binding etc. as per specification. | kg | 246 | 0 | 0 | N
22 | PWD | ELECT | 2020 | 20.32 | Supply and erection standard ACSR (aluminium conductor steel reinforced) confirming to IS 398-1961 of approved make at existing insulator at height upto 14m from ground level including stringing, binding with insulator, jointing wherever required, jumpering, tearing off connection etc complete etc. as per specification including clearing off obstacle if any: 20.32.3 Rabbit 6/1/3.35 mm dia with calculated aluminium aria 52.88 sq mm rate weight 214 kg / km (100 amps) | Km | 5.2 | 0 | 0 | N
23 | PWD | ELECT | 2020 | 20.32.4 | Raccoon 6/1/4.09mm dia with calculated aluminium area 78.83 sq.mm , weight 319 kg/ km (198 amps) | Km | 2.95 | 0 | 0 | N
24 | PWD | ELECT | 2020 | 20.32.5 | Dog 6/4.72 (AL), 7/1.57 (S) mm dia with calculated aluminium area 105 sq.mm , weight 394 kg/km (248 amps) | Km | 0.12 | 0 | 0 | N
25 | PWD | ELECT | 2020 | 20.33 | Supplying and erection DANGER BOARD made MS sheet duly painted and maked as per IE rules and specification. | Each | 25 | 0 | 0 | N
26 | PWD | ELECT | 2020 | 20.34 | Supply and errection of following Polymer Insulator with G.I. Bolt, Nuts and Straps etc. as per specification. 20.34.2 33 KV polymer Disc Insulator {45 KN } | Each | 15 | 0 | 0 | N
27 | PWD | ELECT | 2020 | 20.34.3 | 11 KV Disc Insulator | Each | 51 | 0 | 0 | N
28 | PWD | ELECT | 2020 | 20.34.4 | 33 KV Pin Insulator with Pin | Each | 7 | 0 | 0 | N
29 | PWD | ELECT | 2020 | 20.34.5 | 11 KV Pin Insulator with Pin | Each | 71 | 0 | 0 | N
30 | PWD | ELECT | 2020 | 29.13 | Dismantling of angle iron board/ cubical panel including repairing the wall, shifting of dismantled material to department store. (front area to be measured) | sqm | 11.7 | 0 | 0 | N
31 | PWD | ELECT | 2020 | 29.14 | Dismantling of steel pole, R.S. Joist from the cement concrete foundation with bracket, insulators, stay wires etc, refilling the pit upto geound level including shifting of dismanted material to department store. | Each | 4 | 0 | 0 | N
32 | PWD | ELECT | 2020 | 29.15 | Dismantling of stay set from the cement concrete foundation, refilling the pit upto ground level including shifting of dismantled material to department store. | Each | 30 | 0 | 0 | N
33 | PWD | ELECT | 2020 | 30.1 | Earth work in all type soil except soft rock / hard rock with all lead and 1.5 metre lift, dressing, stacking excavated strata including refilling of excavated soil in trench / pit to ground level complete as per specification. | cum | 7.6 | 0 | 0 | N
34 | PWD | ELECT | 2020 | 30.13 | Providing and laying Cast-in-situ cement concrete 1:3:6 (1 cement : 3 coarse sand : 6 graded stone aggregate 40mm including mixing with mechanical mixer, compacting with vibrator, finishing and currying etc. complete but excluding form work. | cum | 32.76 | 0 | 0 | N
35 | PWD | ELECT | 2020 | 31.14 | Painting new steel and other metallic surface with red oxide zinc chromide primer paint complete with supply of material labour etc. including preparation of surface. | sqm | 34.5 | 0 | 0 | N
36 | PWD | ELECT | 2020 | 31.15 | Painting wood steel and other metallic surface with Aluminium Paint complete with material and labour including preparation of surface. | sqm | 40.6 | 0 | 0 | N
37 | PWD | ELECT | Non SOR | Rate Approved by SE PWD(E/M) Circle,Raipur, vide memo No. 188 / work-E/M Rpr. Dtd 30.01.2026 | Supplying and fixing of 33 kv MS V cross arm of size 75x75x6 mm weighing 25.7 kg including drilling of holes for insulator and clamping with nuts and bolts but excluding insulator, clamp,nuts and bolts etc as per REC specifications. | No. | 3 | 0 | 0 | N
38 | PWD | ELECT | Non SOR | Rate Approved by SE PWD(E/M) Circle,Raipur, vide memo No. 188 / work-E/M Rpr. Dtd 30.01.2026 | Supplying and fixing of 33KV top clamp (33 kV Top m.s. angle 65x65x6 mm, 5.8 kg/m with two nos. 16 mm dia hole for fixing of back clamp. and m.s. channel 100x50x6.4 mm, 65 mm long welded with angle with 20 mm dia hole for pin insulator.) as per REC specifications. | NO. | 5 | 0 | 0 | N
39 | PWD | ELECT | Non SOR | Rate Approved by SE PWD(E/M) Circle,Raipur, vide memo No. 188 / work-E/M Rpr. Dtd 30.01.2026 | Supplying and fixing of 33 kV Guarding Channel 100x50 mm, 2210 mm long with 6 nos 18 mm dia holes for fixing of 16 mm Eye bolt and back clamp as per REC specifications. | Set | 2 | 0 | 0 | N
40 | PWD | ELECT | Non SOR | Rate Approved by SE PWD(E/M) Circle,Raipur, vide memo No. 188 / work-E/M Rpr. Dtd 30.01.2026 | Supplying and Fixing of AL Jointing sleeve for Dog Conductor as per REC specifications. | Each | 6 | 0 | 0 | N
41 | PWD | ELECT | Non SOR | Rate Approved by SE PWD(E/M) Circle,Raipur, vide memo No. 188 / work-E/M Rpr. Dtd 30.01.2026 | Supplying and fixing of 33 KV Strain hardware fittings. (Strain H/W for Raccon & Dog) as per REC specifications. | Each | 12 | 0 | 0 | N
42 | PWD | ELECT | Non SOR | Rate Approved by SE PWD(E/M) Circle,Raipur, vide memo No. 188 / work-E/M Rpr. Dtd 30.01.2026 | Supplying and Fixing of G.I. WIRES: - Barbed wire 4mm 8 SWG confirming to IS:2781978 as per REC specifications. | KG | 52 | 0 | 0 | N
43 | PWD | ELECT | Non SOR | Rate Approved by SE PWD(E/M) Circle,Raipur, vide memo No. 188 / work-E/M Rpr. Dtd 30.01.2026 | Supplying and Fixing of 11 kV MS V Cross Arm angle type 65x65x6 mm Weighing 11.48 Kg 1150 mm long with 18 mm dia hole for pole back clamp and 22 mm dia hole for pin insulator including drilling of holes for insulator and clamping with nuts and bolts but excluding insulator, clamp,nuts and bolts etc as per REC specifications. | No. | 9 | 0 | 0 | N
44 | PWD | ELECT | Non SOR | Rate Approved by SE PWD(E/M) Circle,Raipur, vide memo No. 188 / work-E/M Rpr. Dtd 30.01.2026 | Supplying and fixing of 11 kV m.s. Top Clamp Angle type 65x65x6 mm 385 mm long as per REC specifications. | NO. | 13 | 0 | 0 | N
45 | PWD | ELECT | Non SOR | Rate Approved by SE PWD(E/M) Circle,Raipur, vide memo No. 188 / work-E/M Rpr. Dtd 30.01.2026 | Supplying and Fixing of MS Single Pole Cut Point Fitting 100x50x6 mm, 1800 mm long (33 kV Cut point channel) as per REC specifications. | Each | 4 | 0 | 0 | N
46 | PWD | ELECT | Non SOR | Rate Approved by SE PWD(E/M) Circle,Raipur, vide memo No. 188 / work-E/M Rpr. Dtd 30.01.2026 | Supplying and Fixing of Single Pole m.s. Cut Point Fitting 100x50x6 mm, 1800 mm long (11 kV Cut point channel) as per REC specifications. | Each | 9 | 0 | 0 | N
47 | PWD | ELECT | Non SOR | Rate Approved by SE PWD(E/M) Circle,Raipur, vide memo No. 188 / work-E/M Rpr. Dtd 30.01.2026 | Supplying and fixing of Earthing Coil (Coil of 115 turns of 50 mm dia. & 2.5 Mtrs lead of 4.0 mm GI wire) (EARTHING COIL 8SWG GI WIRE 50 MM DIA 450MM height) as per REC specifications. | Each | 25 | 0 | 0 | N
48 | PWD | ELECT | Non SOR | Rate Approved by SE PWD(E/M) Circle,Raipur, vide memo No. 188 / work-E/M Rpr. Dtd 30.01.2026 | Supplynig and fixing of m.s. Nuts and bolts of verious sizes 16x200 mm / 16x250 mm/ 16x300mm/ 20x75 mm/ 20x90 mm/ 20x110mm/ 24x120mm/ 16x100mm/ 16x140mm/ 16x160mm as per REC specifications. | Kg | 31.5 | 0 | 0 | N
49 | PWD | ELECT | Non SOR | Rate Approved by SE PWD(E/M) Circle,Raipur, vide memo No. 188 / work-E/M Rpr. Dtd 30.01.2026 | Supplying and fixing of 11 KV Strain hardware fittings. (Strain H/W up to Rabbit.) as per REC specifications. | Each | 51 | 0 | 0 | N
50 | PWD | ELECT | Non SOR | Rate Approved by SE PWD(E/M) Circle,Raipur, vide memo No. 188 / work-E/M Rpr. Dtd 30.01.2026 | Supplying and fixing of M.S. Stay Clamp (50 mmx6 mm) and 246 mm length between 2 nos 18 mm dia holes for 16 mm bolts as per REC specifications. | Pair | 61 | 0 | 0 | N
51 | PWD | ELECT | Non SOR | Rate Approved by SE PWD(E/M) Circle,Raipur, vide memo No. 188 / work-E/M Rpr. Dtd 30.01.2026 | Supplying and fixing of Aluminium binding wire and tape as per REC specifications. | Kg | 8 | 0 | 0 | N
52 | PWD | ELECT | Non SOR | Rate Approved by SE PWD(E/M) Circle,Raipur, vide memo No. 188 / work-E/M Rpr. Dtd 30.01.2026 | Supplying and fixing of 11 kV M.S. Guarding Channel 100x50 mm 2210 mm long (1.1 MTR DPDC CROSS ARM) with 6 nos 18 mm dia holes for fixing of 16 mm Eye bolt and back clamp as per REC specifications. | Set | 2 | 0 | 0 | N
53 | PWD | ELECT | Non SOR | Rate Approved by SE PWD(E/M) Circle,Raipur, vide memo No. 188 / work-E/M Rpr. Dtd 30.01.2026 | Supplying & Erection of PCC Pole 11 Mtr Long 365 kg top Cross section 225 mm X 100 mm Bottom Cross section 395 mm X 100 mm ( conforming to IS 1678-1998) Including fixing of Earthing Coil Size 8 SWG GI wire but excluding Earthing Coil as per REC specification | Each | 19 | 0 | 0 | N
54 | PWD | ELECT | Non SOR | Rate Approved by SE PWD(E/M) Circle,Raipur, vide memo No. 188 / work-E/M Rpr. Dtd 30.01.2026 | Supplynig and fixing of m.s. Nuts and bolts of verious sizes 16x65 mm / 16x90 mm as per REC specifications. | Kg | 7 | 0 | 0 | N
55 | PWD | ELECT | Non SOR | Rate Approved by SE PWD(E/M) Circle,Raipur, vide memo No. 188 / work-E/M Rpr. Dtd 30.01.2026 | Supplynig and fixing of m.s. Nuts and bolts of verious sizes 12x65 mm / 12x100 mm / 16x40 mm as per REC specifications. | Kg | 13 | 0 | 0 | N
56 | PWD | ELECT | Non SOR | Rate Approved by SE PWD(E/M) Circle,Raipur, vide memo No. 188 / work-E/M Rpr. Dtd 30.01.2026 | Supplynig and fixing of m.s. Nuts and bolts of verious sizes 12x120 mm / 12x140 mm as per REC specifications. | Kg | 7 | 0 | 0 | N
57 | PWD | ELECT | Non SOR | Rate Approved by SE PWD(E/M) Circle,Raipur, vide memo No. 188 / work-E/M Rpr. Dtd 30.01.2026 | Supplying and Fixing of Transformer mounting m.s. cross arm DC channel 100x50x6 mm, 2.4 mtr long 8' centre as per REC specifications. | Set | 3 | 0 | 0 | N
58 | PWD | ELECT | Non SOR | Rate Approved by SE PWD(E/M) Circle,Raipur, vide memo No. 188 / work-E/M Rpr. Dtd 30.01.2026 | Supplying and Fixing of D.O. / LA Mounting M.S. channel 75x40x6 mm, 2800 mm long as per REC specifications. | No. | 6 | 0 | 0 | N
59 | PWD | ELECT | Non SOR | Rate Approved by SE PWD(E/M) Circle,Raipur, vide memo No. 188 / work-E/M Rpr. Dtd 30.01.2026 | SUPPLYING AND FIXING OF ALUMINIUM CABLE 1C 70 SQ MM UNARMOURED LT PVC as per REC specifications. | KM | 0.2 | 0 | 0 | N
60 | PWD | ELECT | Non SOR | Rate Approved by SE PWD(E/M) Circle,Raipur, vide memo No. 188 / work-E/M Rpr. Dtd 30.01.2026 | SUPPLYING AND FIXING OF ALUMINIUM CABLE 1C 150 SQ MM UNARMOURED LT PVC as per REC specifications. | KM | 0.24 | 0 | 0 | N
61 | PWD | ELECT | Non SOR | Rate Approved by SE PWD(E/M) Circle,Raipur, vide memo No. 188 / work-E/M Rpr. Dtd 30.01.2026 | SUPPLYING AND FIXING OF ALUMINIUM CABLE 1C 300 SQ MM UNARMOURED LT PVC as per REC specifications. | KM | 0.03 | 0 | 0 | N
62 | PWD | ELECT | Non SOR | Rate Approved by SE PWD(E/M) Circle,Raipur, vide memo No. 188 / work-E/M Rpr. Dtd 30.01.2026 | Supply and Fixing of L.T. Distribution Box for 200 kVA X'mer (400 A, isolator & 6 SP MCCB of 120A) as per REC specifications. | Each | 1 | 0 | 0 | N
63 | PWD | ELECT | Non SOR | Rate Approved by SE PWD(E/M) Circle,Raipur, vide memo No. 188 / work-E/M Rpr. Dtd 30.01.2026 | Supplying and Fixing of m.s. D.C.Cross arm 4' Centre 100x50x6 mm Channel 2 Nos, 1.2 mtr long as per REC specifications. | Set | 6 | 0 | 0 | N
64 | PWD | ELECT | Non SOR | Rate Approved by SE PWD(E/M) Circle,Raipur, vide memo No. 188 / work-E/M Rpr. Dtd 30.01.2026 | Supplying and fixing of Aluminium bobbin(Earth knob) as per REC specifications. | Each | 50 | 0 | 0 | N
65 | PWD | ELECT | Non SOR | Rate Approved by SE PWD(E/M) Circle,Raipur, vide memo No. 188 / work-E/M Rpr. Dtd 30.01.2026 | Supplying & Erection of PCC Pole 9 Mtr Long 200 kg top Cross section 115 mm X 105 mm Bottom Cross section 315 mm X 105 mm ( conforming to IS 1678-1998) Including fixing of Earthing Coil Size 8 SWG GI wire but excluding Earthing Coil as per REC specification | Each | 11 | 0 | 0 | N
66 | PWD | ELECT | Non SOR | Rate Approved by SE PWD(E/M) Circle,Raipur, vide memo No. 188 / work-E/M Rpr. Dtd 30.01.2026 | Supplying and fixing of I Bolt M 20 x 128 mm Thread portion 50 mm as per REC specifications. | Each | 16 | 0 | 0 | N
67 | PWD | ELECT | Non SOR | Rate Approved by SE PWD(E/M) Circle,Raipur, vide memo No. 188 / work-E/M Rpr. Dtd 30.01.2026 | Supplying and fixing MS LT 5 pin cross arm size 50x50x6 mm, weighing 10.03 kg including drilling of holes for insulator and clamping with nuts and bolts but excluding insulator, clamp,nuts and bolts etc as per REC specifications. | Nos. | 41 | 0 | 0 | N
Sub- Engineer
P.W.D. (E/M) Sub Division.
Gariyaband (C.G.)
Sub- Divisional Officer
P.W.D. (E/M) Sub Division
Gariyaband (C.G.)
Executive Engineer
P.W.D. (E/M) Division
Nava Raipur (C.G.)