# CONTRACT NO.

GUJARAT WATER SUPPLY & SEWERAGE BOARD

GANDHINAGAR

(A WHOLLY OWNED GOVERNMENT OF GUJARAT UNDERTAKING)

Bid documents for Supply, Installation, Testing and commissioning of VCB panel with required accessories at Hindoliya Intake well of  Hindoliya RWSS , Including Comprehensive  Maintenance & repair of Electro-Mech works for 24 Months. Ta:Lunawada, Dist: Mahisagar

VOLUME – II

TECHNICAL SPECIFICATIONS

Name of Division:

Executive Engineer,

P. H. Mechanical Division,

1st Floor, Jal Bhavan,

B/H Jilla Panchayat Office,

: 99784-43278

GENERAL TECHNICAL CONDITIONS & REQUIREMENTS

1	SCOPE OF CONTRACT:

1.1	This  specification covers the manufacturing, testing at manufacturer’s site, delivery at site, unloading, handling and storage at site, complete erection, final checkup, painting, testing and commissioning of HT VCB panel & accessories at Hindoliya Intake well pumping station with electrical & mechanical equipments like power and control cable wiring and grounding (earthing) systems, lighting systems, safety accessories etc. to be supplied under this contract to achieve a guaranteed performance coordinated with commercial conditions of the contract to the entire satisfaction of GWSSB.

1.2	Any minor hidden item of work either supply and / or erection of materials / equipment which have not been specifically mentioned in the specifications but are necessary to complete the work for trouble free and efficient operation and guaranteed performance of the entire plant / system / equipment offered shall deemed to be included within the scope of this contract and shall be provided by contractor without any extra price to the GWSSB.

1.3	The project information is indicated in the enclosed specification. It is advisable that the bidder should visit the site and apprise himself of all the site conditions prior to preparing the bid.

2	EQUIPMENT AND SERVICES TO BE INCLUDED BY CONTRACTOR UNDER THESE SPECIFICATIONS:

2.1	Electrical works required Hindoliya Intakewell Pumping Station, District: Mahisagar under  Hindoliya regional water supply scheme.

2.2	HT panel at Pumping Station with all the accessories as per specifications and data sheets.

2.3	Power (LT) and control cables etc as per specifications and requirement for the Pumping Station.

2.4	Earthing systems for the pumping station as per specification and requirement.

2.5	L. T. electrical wiring with required cable etc.

2.6	The contractor shall take the responsibility for all the testing and inspections at manufacturers’ works to be conducted in manner as specified in this specification in the presence of GWSSB's representative. The inspection will be at the cost of contractor. The third party inspection shall also be carried out in the presence of the GWSSB representative i.e. jointly. Inspection charges shall be initially paid to designated third party inspection agency by the contractor, which shall be reimbursed by GWSSB on production of original bill (s) / money receipt (s) given by the TPI to the contractor.

2.7	Transportation of all equipments packed in the specified way from the manufacturer’s works to the project site inclusive of all intermediate handling.

2.8	Unloading of equipments from railway wagons / trucks at site handling and proper storing at site in the approved way under security.

2.9	Opening of package, checking, tallying, sorting out and inspection of equipment received at the site and lodging of insurance claims if any.

2.10	Taking delivery of equipments / materials from contractor’s site stores, transportation to erection site. If erection is delayed arrange for proper storage of the equipment / material in approval ways.

2.11	Erection inspection testing start up and running of the equipment and complete plant at guaranteed performance.

2.12	Furnishing all erection and commissioning supervision service. The contractor shall also arrange for maintenance & repairs (if required) of equipment(s) during guarantee and commissioning period.

2.13	The contractor shall also arrange technical expert of equipment from proprietary supplier to site as and when felt necessary until the commissioning & trial run of the plant is completed.

2.14 	Required Nos. of all relevant drawings, data and instruction manuals.

2.15	All ancillary work as per price bid.

2.16	Any  item  of  work  either  supply  and  /  or  erection  of  material  equipment  which  have  not  been  specifically  mentioned  in  the  specification  but  if necessary  to complete  the  work  for  trouble  free  and  efficient  operation  and  performance  of  the  entire  plant  /  system  /  equipment  offered,  shall  deemed to  be  included  within  the  scope  of  his  contract  and  shall  be  provided  by  contractor  without  any  extra  cost  to  the  GWSSB.

  - RESPONSIBILITY:

It is the intention of the GWSSB to achieve coordinate effect. The installation erection of machinery is linked up with civil construction of pumping station testing and  commissioning  work  is  linked  up  with  the  obtaining  of  electrical connection / power. GWSSB no doubt will be doing his best to see that these inter connected activities are completed at appropriate time. However, contractor is not entitled for any claim, escalation of whatsoever commissioning at a date later than the stipulated time. Necessary extension of time will be granted in case if it is established that the erection / testing / commissioning could not be achieved in stipulated time on account of reasons beyond control of contractor. This factor should be carefully noted as no claim what so ever nature will be entertained on an account of such situations.

  - GUARANTEE:

The contactor has to furnish guarantee for all the equipments supplied by him and complete pumping station for a period of 12 months from the date of handing over the pumping station to GWSSB.

  - DELIVERY:

The contractor has to furnish the BAR – Chart & PERT Chart for the pumping station and the same followed strictly so as to commence the pumping station as per the schedule.

  - CO ORDINATION BETWEEN DIFFERENT AGENCIES:

It is the responsibility of the contractor to coordinate with different agencies i.e. sub supplier and civil contractor so as to commissioning the pumping station in scheduled time.

3.0	EQUIPMENT & SERVICE TO BE EXCLUDED FROM THIS CONTRACT:

3.1	Rising main beyond the vendor's scope of supply.

3.2	Construction of the pumping station and M.C.C. Room.

4.0	THIRD PARTY INSPECTION:

Inspection and testing of the major electro - mechanical equipments such as VCB Panel shall be carried out by third party inspection agency in the presence of GWSSB's representative (i.e. jointly) at manufacturers’ works. QAPs along with manufacturers’ cross sectional drawings, characteristic curves (if any), material(s) of construction etc. for all items shall have to be submitted by the bidder & get them approved prior to their procurement invariably.  Executive Engineer, P. H. Mechanical Division, Vadodara shall scrutinize all QAPs etc. & approve them as per technical specifications & requirements of the governing standards. In case of deviation from the approved technical specifications, QAPs etc. shall be submitted to the Superintending Engineer, P. H. Mechanical Circle, Vadodara for acceptance & approval if found suitable.

4.1	 That the equipment installed complies with specification in all particulars and is of the correct rating for the duty and site conditions.

4.2	That all items operate efficiently and quietly to meet the specified requirements.

4.3	That all noncurrent carrying metal work is properly and safely grounded in accordance with the specifications.

The contractor shall provide all necessary instruments and labour for testing and shall make adequate records of test procedures and readings, shall repeat any test requested by the consultant / GWSSB and shall provide test certificates signed by a properly authorised person such test certificates shall Cover all works.

4.4	It tests fail to demonstrate the satisfactory nature of the installation or any part thereof then no claims for the extra cost of modifications, replacements, or retesting will be considered. GWSSB's decision as to what constitutes a satisfactory test shall be final. The above general requirements as to testing shall be read in conjunction with any particular requirements specified elsewhere.

5	GWSSB reserves right to ask for the corporate guarantee from any or all the bidder for the performance and overall completeness in accordance to GWSSB’s requirements. Specifically, for in time completion of contractual works in accordance to the technical requirements in best workmanship manner.

5.1	GWSSB reserves the right to spilt the work / distribute the works among bidders.

5.2	GWSSB  reserves  the  right  to  accept  or  reject  the  tenders  with  technical  deviation,  at  the  discretion  of  competent  authority.

GENERAL SPECIFICAITONS FOR SUPPLY OF EQUIPMENTS:

1.0	GENERAL:

This part covers conditions pursuant to the contractor and will form an integral part of the contract. The following provisions shall supplement general conditions, detailed specification and requirements.

2.0	LIMIT OF CONTRACT:

Equipments furnished shall be complete in every respect with all mountings, fittings, fixtures and standard accessories normally provided with such equipments and / or needed for erection, completion and safe operation of the equipments as required by applicable codes though they may not have been specifically detailed in the technical specification, unless included in the list of exclusions. All similar standard components / parts of similar standard equipments provided shall be interchangeable with one another.

3.0	ENGINEERING DATA:

3.1	The  contractor  shall  furnish complete engineering  data  of  each  sets  of equipment  such  as  name  of  manufacturer,  the  type  of  model  of  each principal  item  of  equipment  proposed  to  be  furnished  and  erected  in  the annexure,  standard  catalogues  design,  the  specification  number  and   the  name  of  the  project.  If  the  standard  catalogue  pages  are  submitted  the  applicable  items  shall  be  indicated  there  in.  All  titles,  noting,  markings,  and  writing  on  the  drawing  shall  be  in  English.  All dimensions should be in metric units.

3.2	All  manufacture  fabrication  works  in  connection  with  equipment  prior  to  the approval  of  the  drawing  shall  be  at  the  contractor's  risk.  The  contractor  may make  any  changes  in the design  which  are  necessary  to  make  any  equipment  confirm  to  the  provisions  and  intent  of  the  contract  and  such  changes  will  again  be  subject  to  the  approval  by  the  GWSSB.  Approval  the  contractor's  drawing  or  works  by  the  GWSSB  shall  not  relieve  the  contractor  from  any  of  the  responsibility  and  liabilities  under  the  contract.

3.3	Drawings  shall  include  all  installation  and  detailed  piping  drawings  wherever  applicable.  All  piping  100  millimetre  and  larger  shall  be  routed  in  detail  and smaller  pipe  shall  be  shown  schematically  or  by  isometric  drawings.  All drawings  shall  be  fully  corrected  to  agree  with  actual  "As  Built"  construction.

4.0	DESIGN IMPROVEMENTS:

4.1	GWSSB  may  propose  changes  in  the  specification  of  the  equipment  or quality  thereof  and  if  the  parties  agree  upon  any  such  changes  the  specification  shall  be  modified  accordingly.

4.2	If  any  such  agreed  upon  change  is  such  that  it  affects  the  price  and  schedule  of  completion,  the  party  shall  agree  in  writing  as  to   the  extent  of any  change  in  the  price  and / or  schedule  of  completion  before  the  contractor proceeds  with  the  change.  The  following  such  agreement   provision  thereof shall  be  deemed  to  have  been  amended  accordingly.

5.0	The  following  documents  shall  be  sent  by  registered  post  to  the  GWSSB  by  contractor  within  3  days  from  the  date  of  dispatch,  to  enable  the  GWSSB  to make  progressive  payments  to  the  contractor.

INVOICE  (3  copies)

PACKING  LIST  (3  copies)

TEST  CERTIFICATE  (3  copies)

5.1	The contractor shall prepare detailed packing list of all packages and containers, bundles & loose material forming each and every consignment dispatched to site. The contractor shall further be responsible for making all necessary arrangements or loading, unloading and other handling right from his work till the site and also till the equipment is erected, tested and commissioned. He shall be solely responsibility for proper storage and safe custody of all equipments.

5.2	All fine, rental, demurrages, warfare and other expenses incurred due to delayed clearance of the material or any other reason shall be to the account of the contractor.

6.0	PROTECTION TO PLANT:

6.1	All  coated  surface  shall  be  protected  against  abrasions  impact,  discolorations and  any  other  damages.  All  exposed  threaded  portion  shall  be  suitably  protected  with  either  a  metallic  or  non-metallic  protecting  device.  All  ends  of  all valves  and  piping  and  conduit  equipment  connections  shall  be  properly  sealed  with  suitable  device  to  protect  them  from  damage.  The  parts  which are  likely  to  get  rusted  due  to  exposure  to  weather,  shall  also  be  properly treated  and  protected  in  a  suitable  manner.

7.0	MATERIALS HANDLING AND STORAGE:

7.1	All  the  equipment  furnished  under  the  contract  and  arriving  at  the  site  shall be  properly  receive,  un loaded  transported  and  stored  in  the  storage  spaces  by  the  contractor  at  his  cost.

7.2	Contractor  shall  be  responsible  for  examining  all  the  dispatches  and  notify  the  GWSSB  immediately  of  any  damage,  shortage   discrepancy  etc  for  the purpose of  the  GWSSB  information  only.  The  contractor  shall  submit  to  the  GWSSB  every  week  a  report  detailing  all  the  receipts  during  the  work.  However  the  contractor  shall  be  solely  responsible  for  any  shortages  or damage  in  transit,  handling  and / or in storage  and  erection  of  the  equipment at  the  site.

7.3	The  contractor  shall  maintain  and  accurate  and  exhaustive  record  detailing  out  the  list  of  all  equipment  received  by  him  for  the  purpose  of  erection  and  keep  such  record  open  for  the  inspection  of  the  GWSSB  at  any time.

7.4	All  equipment  shall  be  handled  very  carefully  to  prevent  any  damage  or  loss  No  bare  wire  ropes,  string  etc  shall  be  used  for  unloading  and/or  handling  of the  equipment  stored  shall  be  properly  protected  to  prevent  damage  either  to  the  equipment  or  to  the  floor  where  they  are  stored.  The  equipment  from the  store  shall  be  moved  to the  actual  location  of  the  appropriate  time  so  as  to  avoid  damage  of  such  equipment  at  site.

7.5	All  electrical  panels,  control  gears and  such  other  devices  shall  be properly  dried  by  heating  before  they  are installed and energised.

All the electrical equipment shall be tested for insulation resistance at least once in three months from the date of receipt till the date of commissioning and record of such measured insulation values maintained by the contractor.  Such records shall be kept open for inspection by the GWSSB.

7.6	The  consumables  and   other  supplies  likely  to  deteriorate  due  to  storage  must  be  thoroughly  protected  and  stored  in a  suitable  manner  to  prevent  damage  or deterioration  in  quality  by  storage.

7.7	All  the  materials  stored  in  the  open  or  dusty  location  must  be  covered  with suitable  water  proof  and  flame  proof  covering  material  wherever  applicable.

7.8	The  contractor  shall  be  responsible  for  making  suitable  indoor  storage  facilities to  store  all  equipments  which  require  indoor  storage. Normally  all  the  electrical equipment,  such  as   motors,  control  gears,  generators  exciters  and  consumable  like  electrodes,  lubricants, etc  shall  be  stored  in  the  closed  storage  space. The  GWSSB  in  addition  may  direct  the  contractor  to  move  certain  other materials  which  in  GWSSB  opinion  will  require  indoor  storage,  to  indoor  storage  areas  which  the  contractor  shall  strictly  comply  with.

8.0	CONTRACTOR'S MATERIALS AT GWSSB SITE(s):

8.1	The contractor shall bring to site all equipment, component, parts, materials,  including construction equipments,  tools  and  tackles for the  purpose of the works  under  intimation  to  the  GWSSB  all  such  goods  from  the  time  of  their being  brought  shall  not  on  any account  be  removed  or  taken  away  by  the contractor  or  his  subcontractor  without  the  written  permission  of  the  GWSSB The  contractor  shall  nevertheless  be  solely  liable  and  responsible  for  any  loss or  destruction  thereof  and  damage  thereto.

8.2	The GWSSB shall have the lien on such goods for any sum or sums which may at any time be due to owing to him by the contractor, under in respect of or by reasons of the contract. After giving a fifteen (15) days notice in writing of his intention to do  so,  the owner shall be at liberty to sell and dispose of any  such  goods in such  as  be shall think fit  including  public auction or private treaty and to apply  the  proceeds  in  or  towards  the  satisfactions  of  such  or  sums  due  as  aforesaid

After  the  completion  of  the  works,  the  contractor  shall  remove  from  the  site under  the  direction  of  the  purchaser  the  materials  such  as  construction  equipments,  erection  tools,  and  tackles  scaffolding  etc  with  the  written  permission  of  the  GWSSB  if the  contractor  fails  to  remove  such  materials GWSSB  to  do  so  then  the  GWSSB  shall  have  the  liberty  to  dispose  of  such materials  and  credit  the  proceeds  thereof  to  the  account  of  the  contractor.

9.0	FACILITIES TO BE PROVIDED BY THE GWSSB:

9.1	SPACE:

The  contractor  shall  advise  GWSSB  within  fifteen  (15)  days  from  the  date  of  acceptance  of  the  letter  of  intent,  about  his  exact  requirements  of  space  for his  office,  mess  rooms,  storage  area,  pro-assembly  and  fabrication  areas, labour  colony  area,  toilets,  etc  the  above  requirement  shall  be  reviewed  by the  GWSSB  and  land  if  available  will  be  given  to  the  contractor  for  construction  of  his  temporary  structures  like  office,  storage  sheds,  labour  and  staff colony  and  other  utilities,  etc  for  his  own  as   well  as  his  sub  use.  It  will  not  be  binding  to  owner  GWSSB  to  spare   the  land   if  not  available.  In  that  case  contractor  shall  have  to   make  his  own  arrangements. The material once supplied shall have to be stored and preserved by agency up till the commission Agency may deploy the person to protect the materials supplied by agency at their own cost.

10.0	CONSTRUCTION MANAGEMENTS:

10.1	Time  is  the  essence  of  the  contract  and  the  contractor  shall  be  responsible for  performance  of  his  works  in  accordance  with  the  specified  construction schedule.  If  at  any  time  the  contractor  is  falling  behind  schedule,  he  shall  make  necessary  action  to  make  good  for  such  delays  by  increasing  his  work force  or  by  working  overtime  or  over wise  accelerate  the  progress  of  the  work to  comply  with  the  schedule  and  shall  communicate  such  action  in  writing to  the  GWSSB  satisfying  that  his  action  will  compensate  for  the  delay . The contractor  shall  not  be  allowed  any  extra  compensation  for  such  action.

11.0	CONTRACTOR’S COOPERATION WITH THE GWSSB:

In  case  where  the  performance  of  the  erection  work  by  the  contractor  the  operation  of  the  system  facilities of  the GWSSB  such  erection  work  of  the contractor  shall  be  scheduled  to  be  performed  only  in the manner stipulated  by  GWSSB  and  the  same  shall  be  acceptable  at  all  times  to  the contractor. The  GWSSB may important such restrictions on the facilities if provided to the  contractor  such  as  electricity,  water  etc  as  the  GWSSB  may think fit in the  interest  of  the  itself  and the  contractor  shall strictly  adhere  to  such  restrictions  and  cooperate  with  the  GWSSB  it  will be  the responsibilities  of  the contractor  to  provided  all  necessary  temporary  instrumentation  and  other  measuring  devices  required    during  the  start-up  and  operation of  equipment  systems  which  are  erected  by  him.  Before  commission of any   machine  all  old  lubricants,  greases  etc  shall  be  thoroughly  removed, the  part cleaned  of all  deleterious  material  and  shall  be  freshly  lubricated  by  sealed   lubricants,  of  exact  pacifications.

12.0	COOPERATION WITH OTHER CONTRACTORS & FOR GWSSB:

The contractor shall agree to cooperate with the GWSSB other contractor and consultants of GWSSB and freely exchange with them such technical information and economical design features to avoid unnecessary duplication of efforts .The contractor  shall  attend  design  coordination  meetings  at  his own  cost  whenever  required.

13.0	FIELD OFFICE RECORDS:

13.1	The  contractor  shall  maintain at  his  site  office  up  to  date  copies of all  drawings specifications and other contract documents and any other supplementary data  complete with all  the  latest  revisions thereto. The  contractor  shall  also  maintain in addition,  the  continuous  records of all  changes to the above contract documents,  drawings, specifications, supplementary  data etc. affected  at  the field  and  on  completion of his  total  assignment  under  the contract shall incorporate all such  changes on the  drawings  and  other  engineering  data to  indicate as  installed  conditions of  the  equipments  furnished  and  erected under  the  contract.  Such  drawings  and engineering  data  shall  be  submitted  to  the  GWSSB  in  required  number  of  the  copies.

14.0	DESIGN COORDINATION:

14.1	The  contractor  shall  be  responsible  for  the  selection  and  design  of appropriate equipments  to  provide  the  basic  coordinated  performance  of  the entire  system They  also  design  requirement  are  detailed  out  in  technical  specifications. The design of various components, sub assemblies and  assemblies  shall  be  not  got  done,  such  that  it  facilities  easy  field  assembly  and  maintenance.  All  the  relating  components  shall  be  so  selected  that  the   natural  frequency  of  the  compact  unit  is  not  critical  at  or  close  to  the operating  range  of  the  unit.

15.0		QUALITY ASSURANCE PROGRAMME:

To ensure that the equipment and services under scope of this contract whether  manufactured or performed within the contractor's work or at his sub contractor's  premises or at the owner's site or at any other place of work are in accordance with the  specifications. The contractor shall adopt suitable quality assurance programme to such  activities at all points, necessary such programme shall be outlined  by  the  contractor  and  shall  be  finally  accepted by the purchaser after  discussions  before  the  start  of  contract,  and  such agreed  programme  shall  form  part  of  the  contract.

16.0	DEFECTS IN WORK OF OTHER CONTRACTOR:

16.1	The GWSSB shall be notified promptly by the contractor of any defects in the other  contractor works, the GWSSB shall determine the corrective measures if  any  required  to  rectify  this  situation  after  joint  inspection work and such decision by  the  GWSSB  shall  be  binding  on  the  contractor.

17.0	UNFORSEEN WORKING CONDITIONS:

17.1	The  contractor  shall  confirm  all  his  field  operations  to  those  works  which  can  be  performed  without   subjecting  the  equipment  and  materials  to  adverse effects,  during  inclement  weather  conditions,  monsoon,  storms,  etc  and  during other  unfavorable  construction  condition. No  field  activities shall  be  performed by  the  contractor  under  conditions  which  might  adversely  affect  the  quality and  efficiency  thereof,  unless  special  precaution  or  measures  are  taken  by the  contractor  in  a  proper  and  satisfactory   manner  in  the performance  of such  works  and  with  the  concurrence  of  the  purchaser.  Such unfavorable  construction  conditions  will in  no  way relive the contractor  of  his  responsibility  to  perform  the  works  as  per  schedule.

18.0	PROTECTIVE GUARDS:

18.1	Suitable guards shall be provided for protection of personal on all exposed rotating and / or moving machine parts. All  such  guards  with  necessary  spaces  and  accessories  shall  be  designed  for  easy  installation  and  removal  for maintenance  purposes.

19.0	WELDING:

19.1	If the manufacture has special requirement relating to the welding procedures for welds at the terminals of the equipment to procedure procured by the owned separate specifications. The requirement shall  be  submitted  to  the GWSSB  in  advance  of  commencement  of  erection  work.

20.0	NOISE AND VIBRATIONS:

20.1	The equipment supplied and erection by the  bidder  will  comply  with  best  design  and  erection  and  its  working  shall within  permissible  noise and vibration levels.

21.0	EQUIPMENT BASES:

21.1	A  cast  iron  or  welded  steel  base  plate  shall  be  provided  for  the equipment  which  is  to  be  installed  on  a  concrete  base  unless  otherwise agree  by  the  GWSSB  each  base  plate  shall  support  the  unit  and  its  drive  assembly  shall  be  of  a  neat  design  with  anchoring  the  units.

22.0 	SHAFT ALIGNMENTS:

All  the  shafts  of  rotating  equipment  shall  be  properly  aligned  to  these  of  the machine  equipments  to  as  perfect  and  accuracy  as  practicable.  The  equipment  shall  be  free  from  excessive  vibration  so  as  to  avoid  over  heating of  bearing  or  other  conditions  which  may  tend  to  shorten  the  life  of the equipment.  All  bearings  shafts  and  other  rotating  parts  shall  be  thoroughly   cleaned  and  suitable  lubricated  before  starting.

23.0	DOWELLING:

All  the  drive motors and  other  equipment  shall  suitable  dowelled  after alignment  of  shaft  with  tapered  machine  dowels  as  per    direction  of  the  GWSSB.

24.0	PAINTING:

All  exposed  metal  parts  of  the  equipments  including  piping,  structures  railings etc.  Wherever  applicable  after  installation  unless  otherwise  specified  shall  be surface  protected and  shall  be  first  painted  with  at least  primer  paint  used,  after thoroughly  cleaning  all  such  parts  of  all  dirt,  rust  Axles  greases,  oils  and other  foreign  materials  by  wire  brushing, scraping  or  sand  blasting  and  the  same  being  inspected and  approved  or  sand  blasting  and  the  same  being  inspected  approved  by  the  board  for  painting.  Afterwards  the  above  parts  shall  be  finished  with  two  coats  of  alloyed  resin  machinery  enamel  paints  The  quality  of  the  finished  paints  shall  be  as  per  standards  of  I.S.I  or  equivalent  and  shall  be   of  the  colour  as  approved  by  the  GWSSB

25.0	COLOUR CODE FOR PIPE SERVICES:

25.1	All  pipe services  wherever  applicable  are  to  be  painted  accordance  with  the owner's  standard  colour  scheme  by  the  contractor.

26.0	LUBRICATION:

Equipments  shall  be  lubricated  by  system  suitable  for  duty  of  the  equipment Lubricant  level  indicators  wherever  provided  shall  be  furnished  and  parked  to indicate  proper  levels  under  both  stand  steel  and  operating  conditions.

27.0	FIRST FILLING OF CONSUMABLES OIL AND LUBRICANTS:

All the first fill of consumables such as oils, lubricants and essential chemicals etc. which will be required to put the equipment covered under the scope of the specifications into successful trial operation. They shall be furnished  by  the  contractor  unless  specifically  excluded  under  the  in  these  specification  and  documents.

CHECKOUT CONTROL SYSTEMS:

After  completion of wiring and cable furnished under separate specifications and laid  as per the terms noted by the board  the  contractor  shall  check  out  the  operation  of  all  control  system  for  the  equipments  furnished  and  installed under  these  specification  and  documents.

28.0	EQUIPMENT PERFORMANCE GUARANTEE:

The performance guarantees of the equipments under the scope of the contract are detailed separately in the technical specifications. These guarantees shall supplement the general performance guarantee provisions covered under general terms and conditions.

29.0	GUARANTEE:

In the event of any emergency where in the judgment of the board delay would cause serious loss or damage, repairs or adjustments may be made by the GWSSB or a third party chosen by the GWSSB without notice to the contractor or by surety. In the event such action is taken by the purchaser the contractors will be notified promptly and he shall assist whenever possible in making the necessary corrections. This shall not extinguish the contractor's liability under the terms and conditions of the contractor.

The cost of any special or general overhaul rendered necessary during the maintenance period due to the defect in the plant or defective work carried out the contractor the same shall be borne by the contractor.

In  case  of  this  effective  parts  which  are  not  repairable  at  site  but  are  essential  for  the  commercial  operation  of  the  equipment,  the  contractor  and the  GWSSB  shall  naturally  agree  to  a  programme  of  replacement  of  renewal which  will  minimise  interruption  to  the  maximum  extent,  in   to  operation  of the  equipment.  At  the  end  of  guarantee  period  the  contractors  liability  except  for  the  latest  defects  in  respect  of  goods  supplied  by  sub  contractor to  the  contractor  where a  longer  guarantee  ( More  than  12  months )  is  provided  by  sub - contractors,  the  owner  shall  be  entitled  to  the  benefit  of such  longer  guarantee. Then provisions contained in this clause will not be applicable.

If  the  owner  has  not  operated  the  equipment  according  to  generally  approved industrial  practices  and  in  accordance  with  the  conditions  of  operation  specified  and  in  accordance  the  operating  manuals,  if  any.

30.0	RECOMMISSIONING TRIALS - TESTS START – UP:

On completion of erection of the equipment and before start up each items of the equipment shall be thoroughly cleaned and then inspected jointly by the GWSSB and the contractor for correctness and completion of installation and acceptability for start up, loading to initial pre-commissioning tests at site.

The list of pre-commissioning tests to be performed shall be as mutually agreed and include in the contractor's quality assurance programme. The contractors commissioning / start up board specifically identified as far as possible and the contractor shall be responsible for carrying out all pre-commissioning tests. On completion of inspection checking after pre-commissioning tests are satisfactorily over, the complete shall be placed on initial operation during which period the complete equipment shall be operated integral with sub systems and supporting equipments as complete plant.

31.0	TRIAL RUN & OPERATION	:

The plant shall then be on trial operation during which period all necessary adjustments shall made while operating over the full load range enabling the plant to be made ready for performance and guarantee tests.

The duration of trial operation of the complete equipment should be 30 days of initial operation or any other duration as may be agreed to between the contractors. The trial operation shall be considered successful provided that each item of equipment can operate continuously at the specified operating characteristics, for the period of trial operation.

For the period of trial operation, the time of operation with any load shall be counted.  Minor interruptions not exceeding four (4) hours at a time caused during the  continuous  operation  shall  not  affect  the  total  during  of  trial operation.

However, if in the opinion of the, purchaser, the interruption is long, the operation shall be prolonged for the period if interruption. A trial report comprising of observations and recordings of various parameters to be measured in respect of the above trial operation shall be prepared by contractor. This report, besides recording the details of the  observation during trial run shall also including the dates of starts and finish  of  the  trial  operation   and  shall  be  signed  by  the  representative  of  both  the  parties.

The report shall have sheets, recording all the details of interruptions occurred adjustment made and any minor repairs done during the trial operation, based on the observation necessary modification/repairs to the plant shall be carried out by the  contractor to the full satisfaction of the GWSSB, to enable the latter on to accorded  permission  to  carry  out  performance  and  guarantee tests  on  the  plant.

32.0	PERFORMANCE AND GUARANTEE TEST:

32.1	The final test as to the performance and guarantees shall be conducted at site by the GWSSB. The contractor's shall make the equipment ready for such tests and assist by the GWSSB conducting such tests free of cost, such test shall be commenced after the successful completion of  trial operation.

32.2	These trends shall be binding on both the parties of the contract to determine compliance of the equipment with the performance guarantee.

32.3	The available instrumentation and control equipment will be used during such tests and the GWSSB will be calibrate, all such measuring equipment and devices as far as practicable. However, immeasurable parameters shall be taken into account in a reasonable manner by the G.W.S.S.B, for the requirement of these tests. The tests will be conducted for the specified duty and as near to the specified conditions as practicable. The GWSSB will apply proper correction in calculation to take into account condition, which should not correspond to the specified condition.

32.4	Any special equipment, tools tackles required for the successful completion of the performance and guarantee tests shall be provided by the contractor, free of cost.

32.5	The  guaranteed  performance  figure  of the  equipments  shall  be  provided  by the contractor during these performance and  guarantee  cost should the results of  these  tests show any depressed from the guaranteed values, the contractor shall modify  the equipments as required to enable them to meet the guarantees. In such case  performance and guarantee tests shall be repeated one month,  from  the  date  of  equipment is ready for re-tests and  all  cost  for modification  including  labour  materials  and  the  cost  of  additional  testing  prove  that  the  equipment  meets  the  guarantees  shall  be  borne  by  the  contractor.

32.6	The specific tests to be conducted on equipments have been brought out in the technical specifications.

32.7	Performance  and  guarantee  tests  shall  make  allowance  for  instrumentation error  as  may  be  decided  by  the  GWSSB.

33.0	REGISTRATION AND STATUTORY INSPECTION:

33.1	All registration and statutory inspection fees if any in respect of this work pursuant to this contract shall be to the account of the contractor.  However,  any  registration  statutory inspection fees lawfully payable under the provision of statutory laws and it's  amendments  from time to time during erection in respect of the plant equipment  ultimately  to  be owned  by  the  owner  shall  be to  account of the  owner. Should any  such inspection or registration need to be rearranged due to the fault of the contractor  or his sub-contractor the additional fees  for  such  inspection  and /or  registration  shall be  borne  by  the  contractor.

34.0	WORKS AND SAFETY REGULATION:

34.1	The  contractor  will  notify  the  GWSSB  of  his  intention  to  bring  on  the  site  any  equipment  or  any  container  with  liquid  or  gaseous  fuel  or  other  substance  which  may  create  hazard.  The  GWSSB  shall  have  the  right  to  prescribe the  conditions  for  un keep  of  such  hazardous  equipments.

Before  the  contractor  connects  any  electrical  appliances  to  any  plug  or  socket  belonging  to  the  other  contractor  or  owner  he  shall:

- Satisfy  the  Engineer in charge of  GWSSB  that  the  appliance  is  in  good working  conditions.

(b)	Inform  the GWSSB  of  the  maximum  current  rating  voltage  and  phases  power factor  the  appliances.

(c)	Obtain  permission  of  the  Board  detailing  the  sockets  to  which  the  appliances  may  be  connected.

34.2	The  GWSSB  shall  not  grant  permission  to  connect  until  it  is  satisfied  that

(a)	The  appliance  is  in  good  condition  and  is  fitted  with  suitable  plug

(b)	The appliance is fitted with a suitable cable having two earth conductors, one of which shall be an earthed metal sheet surrounding the cores.

34.3	No  electrical  cable  in  use  by  the  contractor / GWSSB  shall  be  disturbed  without  prior  permission.  No weight  of  any  description  will  be  placed  on  any such cable  and  no  ladder  or  similar   equipment  will rest  against  or  be attached to it, under  which  such  equipment  or  container  may  be  handled and used during the  performance  of  the  work  and  the  contractor  shall  strictly adhere  to   such  instruction.  The  GWSSB  shall  have  the  right  to  inspect  any construction  plant  and  to  forbid  its  use  if in  its  opinion  it  is  unsafe. No  claims due  to  such  prohibition  shall  be  entertained  by  the  GWSSB.

34.4	Where it is necessary to provide and / or store petroleum products petroleum mixtures and explosives, the contractor shall be responsible for carrying  out  such  provision  and  / or  storage  in  petroleum  Act  explosives  Act  1948  and  petroleum  inspector  of  Explosives  of  India.  All  such  storage  shall  have  prior  approvals  of  the  GWSSB  in  case  any  statutory authority  the  contractor  shall  be  responsible  for  obtaining  the  same.

35.0	ELECTRICAL SAFETY REGULATIONS:

35.1	In  no  circumstances  shall  the  contractor  interfere  with fuse and electrical   equipment  belonging  to  the  GWSSB  or  other  contractors.

35.2	No work shall be carried out on any live equipment. The equipment shall  be made  safe  by  the  GWSSB  and  a  permit  to  work  be  issued  before  work  is  carried  out.

35.3	The contractor shall  employ  the  necessary  number  of  qualified  full  time  electricians  to  maintain  temporary  electrical  installation.

###### GENERAL REQUIREMENTS (ADDITIONAL)

1.	Employer’s Drawings (if any):

1.1.	The drawings listed in the tender document are the Employer’s drawings and are provided by the Employer as illustrative of the specification.

1.2.	All data and information furnished in the drawings by the Employer is given in good faith but the Employer does not accept the responsibility for the completeness and accuracy thereof. The same shall be verified by the contractor promptly pointing out errors or discrepancies thereof to the Engineer.

2.	Drawings Furnished by the Employer:

2.1.	The contractor shall carefully check all drawings and / or instructions furnished by the Engineer in charge before commencing any Work, and shall inform the EIC in writing, within a day from the receipt of the same, of any errors or omissions discovered, or of the difficulty to execute any works or part thereof in compliance with these drawings and / or the written instructions received from the EIC. Failing to do this, he shall be liable to execute at his own cost the necessary alterations to any works resulting from these errors or omissions.

2.2.	The contractor will be furnished with 2 copies of any such drawings prepared by the Engineer. The contractor will also be furnished with two copies of all instructions as may be issued by the Engineer. One copy of all such drawings and instructions issued to the contractor shall be kept in his office at the site. No drawing or instruction shall be considered valid unless it has been signed by the Engineer.

3.	Drawing Sheet Format:

3.1.	All drawings provided by the contractor shall be on standard size sheets, prepared on computer with Auto Cad 14 and shall show the following particulars in a title block located in the lower right hand corner, in addition to the name of contractor and equipment manufacturer, date, scale, drawing number, revision number (R0 for drawings submitted initially, R1, R2, etc. for drawings submitted subsequently) and title:

Gujarat Water Supply & Sewerage Board / Name of Project: A-4  Regional Water Supply Scheme

A blank space of 90 mm x 100 mm shall be provided for the Engineer’s approval stamp and provision shall be made for details of revisions to be recorded.

3.2.	All drawings submitted by the bidder / contractor shall use the English language and preferably SI units. All drawings shall be clearly and fully cross referenced to the other drawings as relevant.

4.	Tender / Contract Drawings:

4.1.	Drawings submitted by the bidder shall show all the essential items of the plant offered together with sufficient details to enable the general arrangement of the Plant to be determined.

4.2.	The outline dimensional drawings submitted by the contractor shall include the following in addition to overall dimensions:

Parameters of equipment

Load details

Support details

Foundation pocket details

5.	Submission and Approval of Drawings:

5.1.	The following shall be the procedure for submission and approval of drawings:

5.1.1.	The contractor shall submit 3 copies of the drawings to the Employer. All the drawings are to be signed by the contractor or his authorized representatives

5.1.2.	The Engineer in charge’s (EIC) representative will review the drawings and, if found fit for approval, the Employer will return 2 copies to the contractor duly approved.

5.1.3.	In case the drawings / documents are not fit for approval but worth for review, the EIC’s representative will mark the comments on the drawings and return 2 copies to the contractor. In such case, the contractor shall resubmit the revised drawings within two weeks as per sub clause 5.1.1 above and the same shall be repeated till the drawings are finally approved as per sub clause 5.1.2 above.

5.1.4.	If the submitted drawings / documents are not worth for review, the contractor will be informed accordingly.

5.1.5.	On receipt of the approved drawings as per sub clause 5.1.2 above, the contractor shall submit floppy and documents to the employer.

5.1.6.	After tests on completion, the contractor shall submit, within 15 days of the conclusion of the tests, CD’s of the “As Built Drawings” to the Employer.

5.2.	When the drawings are received by the EIC’s representative after revision by the contractor, he will only review the revision made and hence the contractor shall carefully identify all the revised details / dimensions and also describe the revisions in the revision block.

5.3.	No drawings, with corrections made after taking the prints, will be accepted.

5.4.	Approval of drawings by the Engineer shall not relieve the contractor of his responsibility in terms of the contract.

6.	Operation and Maintenance Manuals:

6.1.	The operation and maintenance manuals shall be arranged to provide separate volumes for each principal section of the Works and they shall relate to as built conditions and shall include all necessary drawings and diagrams for a proper understanding of the works.

6.2.	The operation and maintenance manual shall be approved in draft form initially prior to commencement of erection by the EIC’s representative and shall cover all items of the Works. For this purpose, three draft copies shall be submitted to the EIC’s representative. A mere collection of manufacturers’ descriptive leaflets will not be acceptable in satisfaction of this clause. The operation and maintenance manual shall comprise both operating instructions and maintenance instructions.

6.3.	The manuals shall include, but not be limited to the following information:

6.3.1.	Descriptive overview of the whole of the works.

6.3.2.	Descriptions of all systems installed, including mechanical, electrical, instrumentation, control systems with relevant design and operating parameters.

6.3.3.	Descriptions of all equipment supplied including manufacturer’s leaflets, which shall be scheduled for easy reference.

6.3.4.	Schedules and manufacturer’s catalogues for all equipment supplied, giving duties, electrical load, etc.

6.3.5.	Schedules of all equipment suppliers (and their local agents) including names, addresses, telephone & facsimile numbers and e-mail ID.

6.3.6.	Start up, operation and shut down instructions for all parts of the works.  These shall include step by step directions on setting the plant to work listing all adjustments and settings necessary for the current functioning of the plant.

6.3.7.	Instructions on monitoring of plant performance and sample log sheets for each plant item, to be filled by operators on a routine basis.

6.3.8.	“Dos” and “Don’ts” in plant operation: Operator’s attention shall be drawn to all operations considered to be dangerous to operators or likely to cause damage to the plant.

6.3.9.	Procedures to deal with breakdown and emergencies

6.3.10.	Safety requirements

6.3.11.	Checking, testing and replacement procedures to be carried out on all plant items on a daily weekly and monthly basis or at longer intervals to ensure trouble free operation. Full maintenance instructions for all equipment including planned maintenance schedules or charts giving daily, weekly, monthly, quarterly, half yearly, annual overhaul instructions together with recommended lubricants and spares. These shall also include details of routine maintenance work that will be within the competence of the normal maintenance staff and notification of maintenance work that will have to be done by the manufacturer, his agent or other specialist operator.

6.3.12.	Fault locations and remedy charts to facilitate tracing the cause of malfunctions or break down and correcting faults.

6.3.13.	Complete list of recommended lubricants and lubrications charts.

6.3.14.	A ‘spares schedule’ which shall consist of a complete list of item wise spares for all plant items with ordering references and part numbers.

6.3.15.	A complete list of manufacturer’s instructions for operation and maintenance of all bought out equipment. The list shall be tabulated in alphabetical order giving the name of supplier / manufacture, identification of the Plant item giving the model number and the literature provided including instruction leaflets and drawing numbers.

6.3.16.	Step by step procedure for the dismantling, repair and re assembly of all items of equipment.

6.3.17.	Part list and drawings or exploded diagrams for each item of plant with construction particulars, materials of construction, mating components, clearances and tolerances, maximum wear permitted before replacements are to be done, etc

6.3.18.	Record drawings of all systems installed, including general arrangements, conduit and wiring trunking systems, wiring diagrams, control schematics and valve charts, etc., to a reduced scale.

6.4.	The contractor shall furnish 3 copies of the Operation and Maintenance Manual for each station.  Each volume shall be durable and permanently bound within a stiff binder of a design to be approved by the Employer.  They shall permit the subsequent incorporation of revisions to be necessary during the defect liability period.

7.	Protection and Packing for Transportation:

7.1.	Before any plant is dispatched from manufacturer’s works it shall be properly prepared and packed and the contractor shall give the Employer at least 14 days notice that these preparations are to commence.

7.2.	Prior to dispatch the  plant shall be adequately protected by painting or by other approved means for the whole period of transit, storage and erection, against corrosion and incidental damage, including the effects of vermin, sunlight rain, high temperatures and humid atmospheres. The contractor shall be responsible for the plant being so packed and / or protected as to ensure that it reaches the Site intact and undamaged. The plant shall be packed to withstand rough handling in transit and all packages shall be suitable for storage including possible delays in transit.

7.3.	The contractor shall be deemed to have included in the schedule of prices for all materials and packing cases necessary for the safe package, conveyance and delivery and storage of the plant with all protective and preservation measures.

7.4.	Cases containing rubber rings, bolts and other small items shall not normally weigh more than 50 kg gross per case.  No one package or bundle shall contain items of plant intended for incorporation in more than one section of the works.  All items of plant shall be clearly marked for identification against the packing list.

7.5.	Eye bolts, lifting hooks and brackets shall be provided for lifting the boxes, crates and packages. Every crate or package shall contain a packing list in a waterproof envelope. A duplicate copy of the packing list shall be sent by post to the EIC’s representative at site.

7.6.	All crates, packages, etc. shall be clearly marked with a waterproof material to show the weight and where the slings should be attached, and shall also have an indelible identification mark relating them to the packing lists. Packing cases shall be nonreturnable. Contractor shall have to clear the site including packing material.

7.7.	Electrical equipment shall be enclosed in sealed air tight package with hygroscopic material, before being placed in packing cases on shock absorbent materials and secured by means of battens.

8.	Delivery, Unloading and Storing at Site(s):

8.1.	The Contractor shall be responsible for checking all materials delivered to Site and shall keep the EIC or his representative fully informed of the state of deliveries. The contractor shall carry out, at his cost, all instructions of EIC or his representative for proper unloading, preservation, maintenance, storage and security of materials delivered to site until he fulfils all his obligations under the contract.

8.2.	The contractor shall erect and maintain on the Site any temporary storage facility as required and approved by the EIC. If built up shed or area is provided by the Employer depending upon availability, the contractor shall have to pay rent as finalised by the EIC.

8.3.	Multiple handling and movement of materials during storage and retrieval shall be avoided.

MATERIALS AND WORKMANSHIP

1.	Introduction:

1.1.	This part of the specification sets out the general standards of materials to be supplied and the workmanship required to be ensured by the contractor.  All component parts of the Works shall, unless otherwise specified, comply with the provisions of this part or be subject to the approval of the Employer. Particular attention shall be paid to a neat, orderly and well arranged installation carried out in a methodical competent manner.

2.	Reference Specifications and Standards:

2.1.	Where reference is made in the Specification to a British Standard Specification (hereinafter abbreviated to `B.S’) issued by the British Standards Institution of 2, Park street, London W.I., or to an Indian Standard Specification (I.S.) issued by the Bureau of Indian Standards, (earlier known as Indian Standard Institution), Manak Bhavan, 9 Bahadur shah Zafar Marg, New Delhi 110 002, or American Society for Testing and materials (ASTM) issued by ASTM 1916 Race Street, Philadelphia, P.A., 19103, U.S.A. or American National Standards Institute (ANSI) issued by ANSI 1430, Broadway, New York, N.Y., 10018, U.S.A. or Japanese Industrial Standards (JIS) issued by Japanese Standards Association, 4-1-24, Akasaka, Minato-Ku, Tokyo 107, Japan or to any other equivalent Standard it shall be to the latest revision of that Standard at the tender opening date.

2.2.	The contractor may propose at no extra cost to the Employer, the use of any relevant authoritative internationally recognized Reference Standard.

2.3.	All details, materials and equipment supplied and workmanship performed shall comply with the specified Standards. If bidder offers equipment to other Standards, the equipment / material should be equal or superior to those specified and full details of the difference shall be supplied.

2.4.	In the event of conflict between this specification and the codes for equipment, provisions of this specification shall govern. Certain specifications issued by national or other widely recognised bodies are referred to in this specification. In referring to the Standard Specifications the following abbreviations are used:

IS		:	Indian Standard

ANSI	:	American National Standards Institute

API		:	American Petroleum Institute

ASME	:	American Society of Mechanical Engineers

ASTM	:	American Society of Testing and Materials

AWS	:	American Welding Society

AWWA	:	American Water Works Association

ISO		:	International Organisation for Standardisation

DIN		:	Deutsches Institute fur Normung

BS		:	British Standard

IEC		:	International Electro technical Commission

IEE		:	Institution of Electrical Engineers

IEEE	:	Institute of Electrical and Electronic Engineers

NEMA	:	National Electrical Manufacturers Association

AGMA	:	American Gear Manufacturer’s Association

3.	Materials General:

3.1.	All materials incorporated in the works shall be the most suitable for the duty concerned and shall be new and of reputed make / approved quality, free from imperfections and selected for long life and minimum maintenance. Non destructive tests, if called for in the Specification, shall be carried out.  All submerged moving parts of the plant, or shafts and spindles or faces etc. in contact with them shall be of corrosion resistant materials.  All parts in direct contact with various chemicals, shall be completely resistant to corrosion, or abrasion by these chemicals, and shall maintain their properties without aging due to the passages of time, exposure to light or any other cause.

4.	Workmanship General:

4.1.	Workmanship and general finish shall be of first class quality and in accordance with best workshop practice.

4.2.	All similar items of the plant and their component parts shall be completely interchangeable. Spare parts shall be manufactured from the same materials as the originals and shall fit all similar items. Machining fits on renewable parts shall be accurate and to specified tolerances so that replacements can be readily installed.  All equipment shall operate without excessive vibration and with minimum noise. All revolving parts shall be truly balanced both statically and dynamically so that when running at normal speeds at any load up to the maximum there shall be no vibration due to lack of balance.

4.3.	All parts which can be worn or damaged by dust shall be totally enclosed in dust proof housings.  All materials incorporated in the works shall be the most suitable for the duty concerned, free from imperfections and selected for long life and minimum maintenance.  All necessary accessories required for satisfactory and safe operation of the plant shall be supplied by the contractor unless it is specifically excluded from his scope. Suitable provision by means of eyebolts or other means are to be provided to facilitate handling of all items that are too heavy or bulky for lifting and carrying by two men.

4.4.	If, after installation, the operation or use of the materials or equipment furnished by the contractor proves to be unsatisfactory. The Employer shall have the right to operate or use such materials or equipment until correction of defects, errors or omissions, by repair or by partial or complete replacement, can be made without interfering with the plant operations.  Except for any warranty provided for elsewhere in this contract or unless otherwise agreed upon in advance, the period of such operation or use, pending correction of defects, will not exceed 1 year.

5.	Welding:

5.1.	Welding shall comply with the latest revision of the BS 5135 Code.

5.2.	Welders shall be qualified in accordance with the requirement of the appropriate section of BS 4871.  The Engineer shall have the right to call for further qualification from time to time from any welder who in the opinion of the EIC does not produce weld in accordance with the qualification. Each welder shall be assigned a number and letter. Each welded end shall clearly be identified as to its welder marking the welder’s code adjacent to the welds.  A record chart shall be maintained for each welder showing the procedures, for which he has qualified, the date of such qualification, the type of defects produced and their frequency. The EIC shall disqualify the welder whose work requires a disproportionate amount of repairs. All procedures where required shall be qualified as per BS EN 283-3.

5.3.	Inspection and quality of surveillance shall not be limited to the examination of finished welds.  The techniques employed shall be based on methods which are known to produce good results and which have been verified at Site by actual demonstration.

5.4.	Haphazard striking of the electrodes for establishing an arc shall not be permitted.  The arc shall be struck either on the joint or on a starting tag. The starting tag shall be of the same material or a material compatible with the base metal being welded. In case of any inadvertent strike on place other than the welding, the area affected shall be ground flushed and examined by liquid penetration method.

5.5.	Generally, a stringer bead technique shall be used with a slight oscillation of necessary to avoid slag and to minimise the number of beads needed to fill exceed 3 times the wire diameter. Vertical welds shall be made in upward direction. For all pipes above 300 mm dia., welding shall be done whenever possible, by 2 welders working simultaneously along both sides of the pipe.

5.6.	The root pass shall have less than 1.5 mm internal reinforcement. Defects like icicles, burn through and excessive “such back” etc. shall be cause for rejection of welds.

5.7.	Final welds shall be suitable for appropriate fabrication of the non-destructive examination of the weld. If grinding is necessary, the weld shall be blended into the parent metal without gouging or thinning of the parent metal in any way. Uneven and excessive grinding may be a cause for rejection. Fillet weld shall preferably be convex and free from undercutting and overlap at the toe of weld. Convexity and concavity shall not exceed 1.5 mm. The leg lengths shall not exceed the specified size by more than 1.5 mm.

5.8.	All attachments such as lugs, brackets and other non pressure parts shall also be done by qualified welders in accordance with the design details and materials specifications.  Temporary attachments shall be removed in a manner that will not damage the parent metal. Areas of temporary attachments shall be dressed smooth and examined by ultrasonic or liquid penetration methods.

5.9.	All tack welds shall be made using qualified procedure and welders, the number of size of tack welds shall be kept as small as to consist of adequate strength and joint alignments. All tack welds shall be examined visually for defects and if found defective shall be completely removed. As welding proceeds, tack welds shall be either removed completely or shall be properly prepared by grinding or filling their starting ends so that they may be satisfactorily incorporated in the welds. Unacceptable defects shall be removed by grinding machine or chipping or gouging. Flame gouging may be permitted provided gouged surfaces are ground at least by 1.0 mm below the deepest indentation.

5.10.	All weld repairs shall be carried out using the approved welding procedures and welders. Re welded areas shall be re examined by the methods specified for the original welds and repair procedures shall be duly qualified by the EIC’s representative.

6.	Pre heating and Post heating Treatment:

6.1.	Pre heating and post heating treatment shall conform to the relevant application codes. Preheating not exceeding 1210 C for all carbon steel construction above 25 mm thickness would be mandatory. Such pre heating would be maintained during flame cutting, flame or arc gouging,   welding and repairs and may be done by gas heating by gas torches / gas rings with neutral flame. The temperature shall be checked by temperature indicating crayons. However, such pre heating will not be necessary for welds less than 6 mm size. In large diameter pipe fabricated out of plate materials, production control test plates in accordance with the BS 4870 part 1 Table 6 to represent 30 % of the long seams and each welder’s performance would be mandatory.

7.	Electrodes:

7.1.	All electrodes shall be stored in their original sealed containers under dry conditions.  Electrodes shall remain identified until consumed. All electrodes shall be dried before use.  Drying ovens shall be provided in work areas for drying purposes. Electrodes withdrawn from oven shall be promptly used and excess unused electrodes shall be promptly returned to oven.

8.	Examination / NDT / Radiography:

8.1.	The various stages of examination and types shall be as stipulated in the respective fabrication Codes. Radiographic examination shall be carried out as per provisions of BS 2600 or BS 2910. Ultrasonic tests where called for shall be carried out as per provisions of BS 3926, magnetic particle tests shall be carried out as per BS 6072. Liquid penetration tests shall be carried out as per BS 6443.

9.	Stainless Steel Welding:

9.1.	All welding consumable such as electrodes, filler weirs, argon gas for shielding and purging shall be of high quality and the proposed brand shall be furnished for approval of the EIC. Weld deposits shall have similar or higher physical properties and similar chemical composition to the members joined.

9.2.	All electrodes shall be purchased in sealed containers only and stored in their packing intact. The packets opened shall be consumed as early as possible. The electrodes removed from the containers shall be kept in holding ovens at temperatures recommended by electrode manufacturer. Special care shall be taken in avoiding mixing of electrodes in the oven.  The electrodes and filling wires shall be free from rust, oil, grease, earth and other foreign matter.

9.3.	Argon gas with purity 99.5 % shall be used for shielding and purging. The purity of gas shall be certified by the gas manufacturers.

9.4.	Non destructive examination of the welds shall be carried out to ensure quality of weld.

9.5.	The electric current for welding shall be direct current, straight polarity (electrode negative). The welding current shall be kept minimum possible to ensure minimum heat affected zone in the parent material. Other side of the weld joint shall be periodically flushed with argon gas.

10.	Castings:

10.1.	Cast iron shall be of standard grey close grained quality. The structure of the castings shall be homogeneous and free from non metallic inclusions and other injurious defects. All surfaces of castings which are not machined shall be smooth and shall be carefully fettled to remove all foundry irregularities.

10.2.	Minor defects in depth not exceeding 12.5 percent of total metal thickness and which will not ultimately affect the strength and serviceability of the casting may be repaired by approved welding techniques. The EIC shall be notified of large defects and no repair welding of such defects shall be carried out without prior approval of the EIC. If the removal of metal for repair should reduce the stress resisting cross section of the casting by more than 25 percent, or to such an extent that the computed stress in the remaining metal exceeds the allowable stress by more than 25 percent, then casting shall be rejected. Test coupons cast simultaneously with the main castings shall be identified to check physical, chemical analysis of casting.  Major defects on casting are not acceptable. Castings repaired by welding for minor defects shall be stress relieved after such welding. Non destructive tests as directed by the EIC will be required for any casting containing defects whose extent cannot otherwise be judged, or to determine where repair welds have been properly made.

11.	Forging:

11.1.	All major stress bearing forging shall be made to a Standard specifications. Forging shall be subjected to magnetic particle testing or dye penetration test at the areas of fillets and change in section. The testing shall be conducted after rough machining (10 microns). Any defect which will not machine out during the final machining, will be gouged out fully, inspected by dye penetration or magnetic particle inspection to ensure that the defect is fully removed and repaired using an approved repair procedure. Any indication, which proves to penetrate deeper than 2.5 % of the finished thickness of the component, shall be reported to the EIC giving the details like location, length, width and depth. For the magnetic particle inspection the choice of wet or dry particles shall be at the Contractor’s discretion.

11.2.	All forging shall be demagnetised after test and shall be heat treated for the relief of residual stresses.

12.	Design Life:

12.1.	The works as a whole shall be new, of sound workmanship, robustly designed for a long reliable operating life and shall be capable of 24 hours per day continuous operation for prolonged period in the climatic and working conditions prevailing at the Site, and with the minimum of maintenance. Particular attention shall be given to temperature changes, the stability of paint finish for high temperatures, the rating of engines, electrical machinery, thermal overload services, cooling systems and the choice of lubricants for possible high and prolonged operating temperatures. The contractor shall be called upon to demonstrate this for any component part either by service records, or evidence of similar equipment already installed elsewhere or relevant type tests. Routine maintenance and repair shall as far as possible not requires the services of highly skilled personnel.

12.2.	The plant shall be designed to provide easy access to and replacement of component parts which are subject to wear, without the need to replace whole units. No parts in contact with water shall have a life from new to replacement or repair of less than five years.

12.3.	Design features shall include the protection of plant against damage caused by vermin, dirt, dust and dampness and to reduce risk of fire. Plant shall operate without undue vibration, and parts shall be designed to withstand the maximum stresses under the most severe condition of normal service. Materials shall have a high resistance to change in their properties due to the passage of time, exposure to light, temperature and any other cause which may have a detrimental effect upon the performance or life of the Works.

12.4.	Plant located outside lockable areas / building shall have additional features to prevent unauthorised operation.

13.	Lubrication:

13.1.	A complete schedule of recommended oils and other lubricants shall be furnished by the contractor. The number of different types of lubricants shall be kept to a minimum. The schedule and the name of the supplier of the lubricants shall be submitted to the EIC.

13.2.	Contractor shall indicate indigenously available equivalent lubricants with complete specification, to enable the Employer to arrange for regular supply.

13.3.	Where lubrication is effected by means of grease, preference shall be given to a pressure system which does not require frequent adjustment or recharging. Frequent, for this purpose, means more than once in a month and grease systems having shorter periods between greasing should be avoided. Where necessary for accessibility grease nipples shall be placed at the end of the extension piping, and, when a number of such points can be grouped conveniently, the nipples shall be brought to a battery plate mounted in a convenient position. All grease nipples shall be of the same size and type for every part of the plant. Arrangements shall be provided to prevent bearings being overfilled with either grease or oil.

13.4.	Where more than one type of special grease is required a grease gun for each special type shall be supplied and permanently labelled.

13.5.	Oil containers shall be supplied complete with oil level indicators of the sight glass type, or where this is not practicable, with dipsticks. The indicators shall show the level at all temperatures likely to be experienced in service. The levels shall be clearly visible in the sight glass type from the normal access floor to the particular item of Plant and they shall be easily dismantled for cleaning. All sight glasses shall be firmly held and enclosed in metal protection in such manner that they cannot be accidentally dislodged.

13.6.	All lubrication systems shall be designed so as not to cause a fire or pollution hazard and particular care shall be taken to prevent leakage of lubricants and to avoid leaking lubricants coming into contact with any electrical equipment, heated surfaces or any other potential source of fire.

14.	Name Plate:

14.1.	Each item of the plant shall have permanently attached to it in a conspicuous position, a nameplate and rating plate.  Upon these shall be engraved or stamped, the manufacturer’s name, type and serial number of plant, details of the loading and duty at which the item of plant has been designed to operate, and such diagrams as may be required by the EIC. All indicating and operating devices shall have securely attached to them or marked upon them designations as to their function and proper manner of use.

14.2.	Name plates, rating plates and labels shall be of a non-flame propagating materials, either non hygroscopic or transparent plastic with engraved lettering of a contrasting colour.  Fixing shall be by means of non corrosive screws, drive rivets or adhesives shall not be used.

14.3.	Warning labels shall be provided where necessary to warn of dangerous circumstances or substances. Inscriptions or graphic symbols shall be black on a yellow background.

14.4.	Instruction labels shall be provided where safety procedures such as wearing of protective clothing are essential to protect personnel from hazardous or potentially hazardous conditions. These labels shall have inscriptions or graphic symbols in white on a blue background.

15.	Nuts, Bolts, Studs and Washers:

15.1.	Nuts, bolts, studs and washers for incorporation in the plant shall conform to the requirements of the appropriate standard. Nuts and bolts shall be of the best quality of specified grade, machined on the shank and under the head and nut

15.2.	Fitted bolts shall be a light driving fit in the reamed holes they occupy, shall have the screwed portion of such a diameter that it will not be damaged in driving and shall be marked in a conspicuous position to ensure correct assembly at site.

15.3.	Washers, locking devices and anti vibration arrangements shall be provided where necessary.   Jointing hardware for the entire Plant shall be provided with sufficient spares to cater for site losses.

15.4.	Where bolts pass through structural members taper washers shall be fitted, where necessary, to ensure that no bending stress is caused in the bolt. Where there is a risk of corrosion, bolts, nuts and studs shall be designed so that the maximum stress does not exceed half the yield stress of the material under any conditions. All bolts, nuts and washers which are subject to frequent adjustment or removal in the course of maintenance and repair shall be made of nickel bearing stainless steel.

15.5.	The contractor shall supply all holding down, alignment and levelling bolts complete with anchorages, nuts, washers and packing required to attach the plant to its foundations, and all bed plates, frames and other structural parts necessary to spread the loads transmitted by the plant to concrete foundations without exceeding the design stresses.

16.	Allowance for Wastage:

16.1.	The contractor shall supply reasonable excess quantities to cover wastage of those consumable which will be normally subject to waste during erection, commissioning and setting to Work.

17.	Painting – General:

17.1.	The contractor shall be responsible for the cleaning, preparation for painting, and priming or otherwise protecting, as specified, all parts of the plant at the place of manufacture prior to packing.

17.2.	Parts may be cleaned but surface defects may not be filled in before testing at the manufacturer’s works. Parts subject to hydraulic test shall be tested before any surface treatment. After test, all surfaces shall be thoroughly cleaned and dried out, if necessary by washing with an approved de watering fluid prior to surface treatment. Except where the specification provides to the contrary all painting materials shall be applied in strict accordance with the paint manufacturer’s instructions.

17.3.	All protective coatings shall be suitable for use in warm humid climates. All primers, under coats and finishes shall be applied by brush or airless spray, except where otherwise specified. Consecutive coats shall be in distinct but appropriate shades. All paints shall be supplied from the store to the painters, ready for application, and addition of thinners or any other material shall be prohibited.

18.	Painting at Place of Manufacture:

18.1.	Steel and cast iron parts shall be sand blasted to near white cleaning before painting. Edges, sharp covers etc. shall be ground to a curve before sand blasting.  A primer coat of a zinc rich epoxy resin based coating with at least 75 microns dry film thickness is to be provided. In addition the parts are to be provided with adequate number of coats of coal tar epoxy polyamine coating to a dry film thickness of 175 microns including primer coating.

19.	Painting at Site(s):

19.1.	Immediately on arrival at the site, all items of plant shall be examined for damage to the paint coat applied at the manufacturer’s works, and any damaged portions shall be cleaned down to the bare metal, all rust removed, and the paint coat made good with similar paint.

19.2.	After erection, such items which are not finish painted shall be done so and, items that have been finish painted at the manufacturer’s works shall be touched up for any damaged paint work. For finish painting, two coats of synthetic enamel conforming to IS: 2932 shall be applied. Dry film thickness of each coat shall be at least 25 microns.

19.3.	The dry paint film thickness shall be measured by Electrometer or other instruments approved by the Employer.  In order to obtain the dry film thickness specified, the contractor shall ensure that the coverage rate given by the paint manufacturer will enable this thickness to be obtained.  Strength of adhesion shall be measured with an adhesion tester and this value shall not be less than 10 kg/cm2.  Painted fabricated steel work which is to be stored prior to erection shall be kept clear of the ground and shall be laid out or stacked in an orderly manner that will ensure that no water or dirt can accumulate on the surface.  Suitable packing shall be laid between the stacked materials. Where cover is provided, it shall be ventilated.

20.	Noise and Vibration:

20.1.	The Contractor shall provide a quiet installation. All items of plant and equipment shall be carefully chosen with a view to minimizing sound levels.

20.2.	The Contractor shall provide and fix all material for the prevention of transmission of noise and vibration through the structure.  Where appropriate all fans, A/C package unit, compressors and other motif plant shall be mounted on resilient mountings.  All rotating plant shall be statically and dynamically balanced.

21.	Galvanising:

21.1.	Wherever galvanising has been specified the hot dip process shall be used. The galvanised coating shall be of uniform thickness. Weight of zinc coatings for various applications shall not be less than those indicated below:

- Fabricated steel

| i | Thickness less than 2 mm but not less than 1.2 mm | 340 gms / sq mm |
| --- | --- | --- |
| ii | Thickness 2 mm and above | 460 gms / sq mm |

- Fasteners

| i | Up to nominal size M10 | 270 gms / sq mm |
| --- | --- | --- |
| ii | Over M10 | 300 gms / sq mm |

21.2.	Galvanising shall be carried out after all drilling, punching, cutting, bending and welding operations have been carried out. Burrs shall be removed before galvanising. Any Site modification of galvanised parts should be covered well by zinc rich primer and aluminium paint.

DETAILED TECHNICAL SPECIFICATIONS

PART I: ELECTRICAL

HV 11 KV SWITCHGEARS PANEL

Applicable Standards

- The design, material, construction, manufacture, inspection and testing of switchgear shall conform to the latest applicable standards & comply with all currently applicable statutes, regulations and safety codes in the locality where the equipment will be installed.

- The equipment shall also conform to the latest standards specified below. In case of conflict between the standards and this specification, this specification shall govern.

| Circuit Breakers Vacuum Contactors above 1 KV and up to 12 KV | IS: 13118/ IEC: 56, 694, 62271 IEC: 60470, 529, 721 |
| --- | --- |
| Metal Enclosed Switchgear | IS: 3427/ BSEN: 60298/ IEC: 298/ IEC 265 |
| Current Transformers | IS: 2705/ BS: 7626 |
| Voltage Transformers | IS: 3156/ BS: 7625/ IEC: 186 |
| Arrangement for switchgear bus bars, main connections and auxiliary wiring | IS: 5578, 11353 |
| Busbar Support Insulators | IS: 2544/ BS: 3297/ IEC: 273 |
| Degree of Protection | IS: 13947 (Part 1)/ IEC: 947-1/ IEC: 60529 |
| Electrical Relays for power system protection | IS: 3231, 3842/ BS: 142/ IEC: 255 |
| Electrical Indicating Instruments | IS: 1248/ BS: 89/ IEC: 51 |
| High Voltage Fuses | IS: 9385/ BS: 2692/ IEC: 282 |
| AC Electricity Meters | IS: 722, 8530/ BS: 5685/ IEC: 145, 211 |
| Specification for copper rods and bars for electrical purposes | IS: 613 |
| Code of practice for phosphating iron and steel | IS: 6005/ BS: 3189 |
| Alternating current switches for voltages above 1000 V | IS: 9920/ IEC: 129, 265 & 298 |
| Low Voltage Fuses | IS: 13703/ BS: 1362/ IEC: 269 |
| Toggle Switches | IS: 3452/ BS: 3676 |
| Code of practice for selection, installation and maintenance of switchgear and control gear | IS: 10118 |
| Control Switches HV Cable Termination | IS: 6875/ BSEN: 60947/ IEC: 947 IEC: 62329 |

The switchgear shall be metal enclosed, indoor type with vacuum circuit breakers fully draw out type. Circuit breakers of same ratings shall be completely inter-changeable with one another. Separate metal enclosed compartments for (a) control, metering & relaying devices, (b) circuit breaker, (c) phase bus bars, (d) Instrument transformers & (e) input/ out power cable terminations and each section shall be in conformance with Loss of Service Continuity LSC 2B.

The rated capacity of the breaker & switchgear configuration (no. of incomer & outgoing breakers, minimum ratings, protections, indications, annunciations, instruments etc.) shall be as per reference electrical Single Line Diagram & this specification given in table below:

| Sr. No. | Description | Rating |
| --- | --- | --- |
| a) | Rated Voltage (KV) | 11 |
| b) | Bus Bar Rating (A) | As per data sheet & specifications |
| c) | Short Circuit Rating(kA for 1 sec) | 26.2 |
| d) | Type of breakers | VCB |
| e) | One-minute power frequency withstand capacity(KV rms) | 28 |
| f) | Lightening Impulse withstandvoltage (kVp) | 75 |
| g) | Bus Bars Material | Electrolytic Copper (Silver plated at Joints) |
| h) | Degree of Protection (Indoor/ Outdoor) | IP 4 X / IP 5 X (as minimum) |

Auxiliary relays for multiplication of contacts for following transformer protections shall be provided for oil type Transformer feeders

- Buchholz Protection Alarm & Trip

- Winding Temperature Alarm & Trip

- Oil Temperature Alarm & Trip

- Pressure Relief Device Trip

- Oil level gauge (MOG) Alarm

- Surge arrestor of suitable capacity 	Oil Surge Relay (OSR) Trip:The circuit breakers should be able to carry the rated current continuously under site conditions without exceeding the permissible temperature rise for design ambient temperature outside the switchgear cubicle as specified.

Bus bar material for switchgear panel shall be electrolytic Copper. Bus bars shall be fully insulated, supported on insulators capable of withstanding dynamic stresses due to short circuit. Maximum temperature of the main bus bars and bus bar connections, under operating conditions, when carrying rated normal current at rated frequency shall not exceed 900/ 1050C for non-silver plated/ silver plated joints as per IEC: 60694. Bus bar temperature limits shall be adhered to without forced cooling method. The continuous current ratings of the droppers in each switchgear cubicle shall at least be equal to the corresponding breaker rating. However short time current rating shall be same as the short time current rating of the bus-bars.

The circuit breaker shall be fully drawn out type in horizontal with test, service and isolated positions. In test position, the circuit breaker shall be capable of being tested for operation without energizing power circuits. Additional 2 (Two) normally open (NO) contacts of test and service positions shall be available for Client's use, after meeting all the interlocks/ permissive.

Switchgear shall comprise rigid welded structural frame enclosed completely by sheet steel - minimum 2.5 mm thick (hot rolled) or 2.0 mm thick (cold rolled), smooth finished, levelled and free from flaws. Switchgear cubicles shall be provided with bottom sheet steel plates of 2.5 mm thickness. Cable compartments shall be fitted with removable plates of minimum 2.5 mm thickness for fixing cable glands. Cable gland shall be double compression type.  For single core cable, removable plates of non-magnetic material shall be provided.

The switchgear panel shall be powder coated with shade RAL-7032 with minimum thickness80 microns with structured finish and height not exceeding 2300 mm.

For vacuum circuit breakers necessary hardware for surge suppression shall be provided to take care of switching surge.

Circuit breaker shall be provided with a minimum of 6NO + 6NC contacts per pole exclusively for the GWSSB's use. All spare contacts of the circuit breaker shall be wired up to the terminal block.

The breaker closing coils, tripping coils, indications, annunciations shall be rated for 24/ 30V or 110V DC. The spring charging motor shall be suitable for 240V AC. Space heater, power socket, panel illumination lamp shall be fed from 240V, 50 Hz, 1 phase raw power supply.  All lamp test facility shall be provided with push button.

The current transformers shall be mounted in the fixed portion of the switchgear expansion panel. The CTs shall withstand momentary and short time current ratings of the associated switchgear. CTs & VTs shall be of the cast resin type and completely encapsulated. Adequate space shall be available for termination using heat shrinkable type cable termination in CT compartment.

The switchgear shall have complete interlocking arrangement at the fully inserted and fully drawn out position of the breaker. Withdrawal of circuit breaker shall not be possible unless it is in open position and operation of circuit breaker shall not be possible unless it is fully in-service position, or is fully drawn out. Comprehensive interlocking system to prevent any dangerous or inadvertent operation shall be provided. Breaker trolley as required shall be provided with breaker.

Automatic safety shutters shall cover live parts when the breaker is withdrawn and all other standard safety features shall be provided.

All the high voltage compartments i.e. Circuit Breaker, Bus Bar, and Cable Compartments shall be separated from each other by metallic partitions in line with IEC: 62271-100/200. These compartments must have pressure relief flaps for exit of gas due to internal arc to ensure operators safety. All the HV design must ensure conformity to IEC: 62271-100/200 and must be type tested for internal arc tests.

All non-current carrying metal work of the switchgear panel shall be effectively bonded to the earth bus. Earth bus-bar shall be extended outside the switchboard at the ends. All hinged doors & bolted joints in the body of switchgear shall be earthed through flexible copper earthing braid of adequate cross section.

Terminal blocks shall be of stud & nut type, 1100V volts grade, 10 amps rated complete with insulated barriers. Terminal blocks for CTs and VTs shall be provided with test links and isolating facilities and CT terminals with short circuiting and earthing facility. All spare contacts and terminals of cubicle mounted equipment and devices shall be wired to terminal blocks with 20% spare terminals. All terminals of different control voltages shall be separate from each other. Stud type terminals and ring type lugs shall be used for control cables.

The sizes of wire for CT circuit shall be minimum 2.5 mm² multi-stranded copper conductor PVC insulated and for others minimum 1.5 mm² multi-stranded copper conductors PVC insulated. Ring type lugs suitable for termination of 2.5 sq. mm copper wires shall be used. Colours of the secondary/ auxiliary wiring should conform to IS: 375/ 1963 and latest amendments thereof.

All wiring shall be neatly run and group of wiring shall be securely fixed with clips so that wiring can be checked without necessity of removing the clamps. Ferrules with number shall be provided on both end of the wiring i.e. straight + cross ferruling shall be done. Printed ferrules (tubular type- cut to size after printing) white with black lettering shall be provided. Printing shall be done with the indelible ink.

All protective relays shall be in draw out cases with built in test facilities. All auxiliaryrelays and timers shall be supplied in non-draw out cases. Externally operated hand reset indicators shall be provided on all electro-mechanical relays and timers. Timers shall be of electromagnetic or electronic type only. All spare contacts of all relays/ timers shall be wired to terminal block. All relays shall be of self-reset type, unless otherwise specified.

Main protection relays shall be microprocessor based with latest version software without any extra cost. Relays and protection shall be enabled for PLC based system / SCADA with IEC: 61850 protocol & Modbus RS485.

    - Breaker control switches shall be of pistol grip type and selector switches shall be oval or knob. Breaker control switches shall be 3 position spring returns to neutral.

    - Indicating lamps shall be panel mounting type of the colour specified and of multi-chip/ cluster LED type only.

    - Each circuit breaker panel shall be complete with the following:

- T-N-C control switch, spring return to neutral position.

- Key operated local/ remote selector switch stay put type.

- Red, green, amber, white and blue coloured clustered type LED indicating lamps for breaker- ON, OFF, auto trip, trip circuit healthy and spring charged and breaker in Test/ Service position shall be provided.

- Push Button for all lamp test facility.

- 8 window (for Incomer Panel) or ICOG/ 16 window (for each Outgoing (transformer feeder panel) annunciator with all associated accessories as per detailed in data sheet & specifications.

- Double pole control supply switch with MCB.

- Electrical anti pumping relay.

- Panel illumination lamp (CFL) with MCB/ switch.

- Space heater with adjustable thermostat& MCB.

- 5/ 15A 1 Phase receptacle with MCB.

- Potential indicating multichip/ clustered type LED lamps (R, Y, and B) for incomer/ ICOG breakers.

- Components as per electrical SLD.

- Emergency trip push button (ETPB- Mushroom type, Red coloured latch-able type)

- Test Terminal Block (TTB)

- Mechanical trip push button to trip the breaker when control supply is lost. The push button shall be shrouded type. Mechanical close push button provided shall be accessible only after opening of the front door.

- The panel front of the circuit breaker truck shall have following devices/ indications

- Mechanical push button for breaker open

- Mechanical indications for spring charge / discharge

- Mechanical indications for breaker test/ service position

- Mechanical indication for breaker ON/ OFF

- Operation Counter

- Device for manual charging of closing spring

All analogue indicating meters shall be 144 x 144 mm size taut band with 240⁰ Scale. All indicating meters shall be provided as per enclosed electrical Single Line Diagram.Multi-Function Meter (MFM) shall be micro-processor based electronic meter and shall have facility for on line monitoring, reading display of each parameter and shall be provided with RS485 communication port. Analogue Ammeter & Voltmeter shall also be provided as per data sheet & specifications.No extra charges shall be payable to Contractor in the event of any change in the contact configuration of relays i.e. from normally open (NO) to normally closed (NC) and vice versa. All wiring and necessary hardware for the completeness of the schemes shall be included in the scope of Contractor.All operating switches shall be accessible without opening the compartment door.All transformer outgoing feeders shall be suitable for interrupting transformer magnetizing currents. The breaker shall be electrically interlocked with downstream LV breaker such that if HV breaker trips, LV breaker shall also trip, and LV breaker cannot be closed until HV breaker is closed.Withdrawal or engagement of circuit breakers or disconnecting switch shall not be possible unless it is in the open position.Operation of circuit breaker or disconnecting switch shall not be possible unless it is fully in- service position, or in test position or in fully drawn-out.It shall be entirely responsibility of the Contractor to ensure that characteristics of CTs, VTs and all other devices offered by him/ her are such as to be suitable for the purpose for which they are intended.Switchgear shall be suitable for easy extension on both the sides. It shall be possible at a later stage to add cubicles on both the sides of the switchgear by extending the bus-bars.All power and control cables entry shall be from bottom or as to suit the site condition. The cable compartment shall house all power cable connections along with associated cable terminations.All control cabling/ wiring shall be done using 1.1 KV grade, multi-stranded, Cu conductor, PVC insulated FRLS cables. Panel wiring shall be securely supported, neatly installed by lacing, and tying, readily accessible and connected to equipment terminals and terminal blocks. All the accessories such as cable troughs, cable ties, covers etc. shall be of fire-retardant material.Breaker handling trolley shall be provided as required. This shall be complete with all necessaryaccessories.Earthingswitch shall be provided for bus-bar earthing for incomer panel and for cable earthing on the outgoing breaker panel with necessary interlocks. The panel earthing shall be extended up to cable alley for armour earthing.Required suitable cable/ extension adopter boxes for power cables shall be a part of HV panel. The termination kit shall be heat shrinkable type only. Cable lugs for all power,control & instrumentation cables connections shall be supplied. The lugs shall be tinned copper/ Aluminium depending on cable conductor and of solder less crimping type.

Padlocking facilities shall be provided for locking the shutters positively in closed position in all the panels. All door locks shall be provided with special keys to ensure opening by authorized personal only.

Caution name plate, “Caution Live Terminal” shall be provided at all the points where the terminals are likely to remain live and isolation is possible only at remote end i.e. incomer to the switchboard.

Danger notices in three languages (Hindi, English & Gujarati) and in line with the requirements of IS: 2551 shall be riveted & not pasted at appropriate locations of the switchgear.

Feeder and board name plates to be provided at front and rear of switchboard.

Panel illumination lamp shall be 9/ 11W LED with fixture & shall be provided with door limit switch.

Relays

- All relays as indicated in data sheet, specifications & as per requirement shall be mounted on the switchgear panels. The relays shall be in draw-out case, flush mounted type.

- All the unit protection relays such as 51NS shall be separate relays & elements (50/ 50N, 51/ 51N, 51NS etc.) available in numerical relays shall not be used for this purpose.

- In case the primary protection relays offered by Contractor do not have adequate number of contacts for protection/ interlock schemes. Contractor shall supply suitable contact multiplying auxiliary relays as required. All necessary auxiliary relays as required to meet the GWSSB’s final control/ protection/ interlock schemes shall also be provided by the Contractor.

- Relays shall be microprocessor based. Test terminal block for testing shall be provided. Relays shall be suitable for 1/ 5A CT secondary rating as indicated in respective Single Line Diagram. Relays shall be suitable for PLC based system / SCADA with IEC: 61850 protocol & Modbus RS485.

- Relay & Metering used shall be as per following Make & model Nos. “OR equivalent” shall be construed as Equivalent from the approved Makes mentioned elsewhere in the specifications.

| RELAYS |  |
| --- | --- |
| Microprocessor based relay with historical data logging facility with Over-current &earth fault protection | GWSSB Approved Make / Standard & Reputed |
| Master Trip/ Lock out Relay (86) | GWSSB Approved Make |
| Stand by Earth Fault Relay (51NS) | GWSSB Approved Make |
| Contact multiplication relay | GWSSB Approved Make |
| Trip Circuit Supervision Relay | GWSSB Approved Make |
| Comprehensive Motor Protection Relays | GWSSB Approved Make |
| METERING |  |
| Analogue Ammeter | GWSSB Approved Make |
| Analogue Voltmeter | GWSSB Approved Make |
| Multi-Function Meter (MFM) | GWSSB Approved Make |

Lockout relay-86 shall be having minimum 6 NO + 6 NC contacts.

All relays shall have clear identification on the associated panel by well-written inscription plates. Where indications are provided by flag relays or LEDs, these shall also be specifically identified by permanently fixed inscription adjacent to them.

The final relay ranges of each relay shall be decided at detailed engineering stage, if it is found that the offered relay range is not suitable for the intended application, the Contractor shall change the relay of appropriate range without any commercial / delivery implications whatsoever. The relay shall be subject to approval of GWSSB's representative.

Contractor shall furnish recommended relay settings with backup calculations & approval for the same has to be obtained from GWSSB. Entire Relay co-ordination shall be carried out in ETAP 12.5 version or latest available during detailed engineering. The Contractor shall obtain all interface data from all concerned.

- All relay/ auxiliary relay coils shall operate satisfactorily between85% and 115% of the rated control voltage range.

- It is responsibility of the Contractor to include accessories like auxiliary CTs, VTs and all other necessary devices as required for satisfactory performance of relay and protection scheme even if not indicated in drawings/ data sheets. Testing facilities like test switches / test plugs shall be provided for testing of each individual relays.

- Performance tests shall be conducted at site and also supervised by Contractor for all the equipment’s to prove the guarantee.

- Prices quoted shall include the cost of all routine tests specified in relevant standard & as mentioned below. As regards type tests, copies of the earlier test certificates carried out on equipment of similar or higher ratings but not older than five (5) years shall be furnished along with the offer.

Current Transformer

Current Transformers shall satisfy following requirements

- Current transformers for metering & protection shall be cast resin (class of insulation B or better). The CT ratios/ protection class shall be as per data sheet & specification.

- Rated VA burden for metering/ protection CTs shall not be less than 15VA or 120% of total VA burden whichever is higher.

- The accuracy class for metering CT shall be 1.0 or better.

- It shall be responsibility of Contractor to ensure that CTs are suitable for correct and satisfactory operation of the instruments/ relays connected across them.

- Short time current rating and momentary withstand rating of CTs shall be as per breaker short time current withstanding capacity.

- All CTs shall have secondary rating of 1A or 5A.

Voltage Transformers

Voltage Transformers shall satisfy following requirements

- Potential transformers for metering/protection shall be suitable for operation on 11 KV, 50 Hz system. The VT ratios shall be as shown in respective electrical Single Line Diagram.

- Rated VA burden for metering/ protection VTs shall not be less than 100VA or 120% of total VA burden whichever is higher.

- The accuracy class for metering VT shall be Class 1.0/ 5 P as required.

- It shall be responsibility of Contractor to ensure that VTs are suitable for correct and satisfactory operation of the instruments connected across them.

- Fuses on primary side shall have rupturing capacity equal to the switchgear rating.

- For VT’s MCB shall be provided on secondary. MCB trip contact to be wired up for annunciation.

Maintenance Requirements

- Contractor shall supply maintenance tools including special tools (as required) for attending to the equipment supplied at no extra cost. As far as practicable, the equipment and accessories shall be so designed that no special tools are necessary for installation and maintenance of the equipment. However, if special tools are required, the Contractor shall supply one complete set for each type of equipment for the purpose.

- Contractor shall include supply of start-up and essential spares.

- Contractor shall furnish detailed inter-panel diagrams, terminal connection wiring diagram, and detailed component layout drawings to carry out maintenance work.

- Contractor shall ensure the use of calibrated test equipment having valid calibration test certificates from standard laboratories traceable to national standard.

Earthing

- An earthing bus shall be provided at the bottom and extend throughout the length of the switchgear. It shall be bolted / welded to the frame work of each unit and each breaker earthing bus.

- All non-current carrying metal work of the switchgear shall be effectively bonded to the earth bus. Hinged doors shall be earthed through flexible earthing braid of adequate size.

- Positive earthing of the circuit breaker frame shall be maintained both in service and test position.

Annunciators

- Microprocessor based alarm annunciators shall be provided for generating audio visual alarms for each abnormal condition. Facia annunciators, suitable for operation on 24/ 30V or 110V DC (as applicable) shall be provided.

- Each alarm shall initiate the operation of both visual and audible devices equipped with ‘Mute’, ‘Acknowledge’ and ‘Reset’ push buttons common to annunciators on all switchgear aligned together and a ‘Lamp test’ push button for each annunciator on individual panels.

- Annunciator shall be of facia type with translucent plastic window for each alarm point. Annunciator facia plates shall be engraved in block lettering with respective alarm inscriptions. The inscriptions shall be clearly readable and visible when the respective facia light is lighted provided with two lamps connected in parallel on each facia window with series resistors. Lamps shall be clustered LED type.

- All facia annunciator points shall be suitable to accept external contacts of either ‘NO’ or ‘NC’ self or hand reset type for initiating the annunciation sequence.

- Annunciators shall be suitable for accepting fleeting faults of duration as less as 15 milliseconds annunciating subsequent faults with the specified sequence immediately after acknowledging the previous fault.

- Facia Window shall be of minimum size of 35 mm x 50 mm.

- During lamp test, if a fault occurs, the corresponding lamp circuit shall be automatically disconnected from the “lamp test” circuit and shall start flashing.

- The sound intensity of each audible device shall be suitable for the maximum sound level of its environment.

- The sequence of alarm should be user selectable by dip switch. The operation or acceptance of one alarm shall not inhibit the operation of the audible device or the flashing of the appropriate alarm indicator if a future alarm condition occurs

- Annunciator shall be designed for an operating sequence indicated below

| Alarm Condition | Fault Contact | Audible Alarm | Visual Alarm |
| --- | --- | --- | --- |
| Normal | Open | Off | Off |
| Abnormal | Closed | On | Flashing |
| Acknowledge | Open | Off | Steady on |
| Reset | Open | Off | Off |
| Lamp Test | Open | Off | Steady on |

Cable Terminations

- Necessary number of cable glands shall be supplied for terminating auxiliary power and control cables. Glands shall be of heavy-duty brass castings, machine finished and complete with check nut, washers, neoprene compression ring.

- Cable lugs for all power and control cable connections shall be supplied. The lugs shall be tinned Copper/ Aluminium depending on cable conductor and of solder less crimping type.

- All necessary materials required for terminating the power cables such as tapes, fillers, binding wires, armour clamps, brass glands etc., shall be supplied.

Tests

- Routine tests and acceptance tests as per the applicable IS/ IEC standards shall be carried out in the presence of GWSSB's representative.

- Type test certificates for internal arc test, SC withstand & Impulse test shall be furnished with the Bid (not older than five (5) years) from CPRI or any other independent agency

- The test equipment, meters, instruments etc. used for testing shall be calibrated at recognized test laboratories at regular intervals and valid certificates shall be made available to the GWSSB's representative at the time of testing. The calibrating instruments used as standards shall be traceable to national/international standards.

Drawings/ Documents Required

The following drawings/ documents to be furnished by the Contractor for GWSSB’s approval

- Technical Data Sheet

- General Arrangement Drawing

- Wiring Schematic

- Bill of Quantities

- Quality Assurance Plan

Earthing and Lightning Protection System:

1.	Scope:

a)	The scope includes collection of data, design of the system as per relevant National/International Standards preparation of layout drawing supply of earthing conductors, earth electrode, installation and approval to the satisfaction of electrical inspector under this tender specification.

b)	Earthing system shall be provided to ensure equipment safety, personnel safety and facilitate designed operation of protective switching during earth fault conditions in the associated system.

2.	Applicable Standards:

The earthing and lightning protection system shall conform to the Indian Electricity rules, and the latest applicable standards indicated below:

| Sr. No. | Description | Standards |
| --- | --- | --- |
| 1 | Code of Practice for Earthing | IS: 3043 |
| 2 | Code of Practice for the protection of building and allied structure against lightening | IS: 2309 |
| 3 | Hot dip galvanizing | IS: 2629, 2633, 4759 |
| 4 | Structural steel | IS: 2062 & 808 |
| 5 | Welding | IS: 816 |

3.	Earthing System:

The design basis for designing earthing conductor is indicated under design criteria for electrical system. Earthing system shall be provided in plant as per the latest edition including all official amendments and revisions of IS 3043 and Indian Electricity Rules, 1956. All materials and fittings used in the earthing installation shall conform to the relevant Indian Standards or shall be approved by the Engineer's representative.

The material of earthing conductor shall be as follows:

i.	Conductor above ground shall be galvanised steel to prevent atmospheric corrosion.

ii.	Conductor buried in ground or embedded in concrete shall be mild steel.

INSTALLATION, TESTING AND COMMISSIONING:

1.	Erection - General

1.1.	 The Contractor’s staff shall include adequate and competent erection engineers with proven, suitable, previous experience on similar contracts to supervise the erection of the works and sufficient skilled, semi skilled and unskilled labour to ensure completion of works in time. The contractor shall not remove any representative, erector or skilled labour from the site without prior approval of the Engineer-In-Charge (EIC) or Engineer-In-Charge’s representative.

1.2.	The Contractor shall ensure that no installation or erection work shall commence until full and unconditionally approved working drawings, signed and stamped by the EIC are available at site.

1.3.	The Contractor’s erection staff shall arrive on the site on dates to be agreed by the EIC. Before they proceed to the site, however, the contractor shall first satisfy himself, as necessary, that sufficient plant of his (or his sub contractor’s) supply has arrived on site so that there will be no delay on this account.

1.4.	One erection engineer who shall be required to be the contractor’s representative shall be conversant with the erection and commissioning of the complete works. Should there be more than one erector, one shall be in charge and the contractor shall inform the EIC in writing which erector is designated as his representative and is in charge. Erection engineer is to report to project manager.

1.5.	The Contractor shall be responsible for setting up and erecting the plant to the line and levels of reference and of the positions, levels dimensions and alignment, appliances and labour in connection therewith. The checking of setting out of any line or level by the EIC or EIC’s representative shall not in any way relieve the contractor of his responsibility for the correctness thereof.

1.6.	Erection of plant shall be phased in such a manner so as not to obstruct the work being done by other contractors or operating staff who may be present at the time. Before commencing any erection work, the contractor shall check the dimension of structures where the various items of Plants are to be installed and shall bring any deviations from the required position, lines or dimensions to the notice of the EIC. Plant shall be erected in a neat and workmanlike manner on the foundations and at the locations shown on the approved drawings. Unless otherwise directed by the EIC, the contractor shall adhere strictly to the aforesaid approved drawings. If any damage is caused by the contractor during the course of erection to new or existing plant or buildings or any part thereof, the contractor shall, at no additional cost to the Employer, make good, repair or replace the damage, promptly and effectively as directed by the EIC and to the EIC’s satisfaction.

1.7.	The contractor shall align all equipment and holding down bolts and shall inform the Employer before proceeding with grouting in the items concerned. The contractor shall ensure that all equipment is securely held and remains in correct alignment before, during and after grouting in.

1.8.	The approval by the Employer of the contractor’s proposals for rigging and hoisting any items of the plant into final positions shall not relieve the contractor from his responsibility for damage to completed structures, parts or members thereof or other installed equipment. He shall at his own cost make good, repair or replace any damaged or injured items, whether structural, electrical, architectural, or of any other description, promptly and effectively to the satisfaction of the Employer.

1.9.	No plants or other loads shall be moved across the floors of structures without first covering the floors with timber of sufficient size so that applied loads will be transferred to floor beams and girders of steel or concrete. If it is required to reduce bending stresses and deflection, the beams and girders shall be provided with temporary supports.

1.10. During erection of the plant the EIC will inspect the installation from time to time in the presence of the contractor’s site representative to establish conformity with the requirements of the specifications. Any deviations and deficiencies found or evidence of unsatisfactory workmanship shall be corrected as instructed by the EIC.

2.	Levelling and Grouting of Machinery

2.1.	He shall undertake sufficiently in advance chipping of any unevenness of concrete on foundations, anchor bolt pockets, cut outs etc. to achieve uniform level of reference for erection.  All concrete surfaces receiving grout shall be hacked as required to ensure better bonding with grouting.

2.2.	Contractor shall undertake the inspection of all components to be erected sufficiently in advance to check their soundness and conformity to drawings and the inspection records shall be signed by the Engineer as approval for undertaking the installation of the components.  Any damage, shortfalls etc. shall be made good to the satisfaction of the EIC.

2.3.	All grout for equipment shall be carried out using non shrinkable continuous grout materials with suitable frame work of at least 12 mm thickness.  Surfaces to receive the grout shall be hacked and roughened and laitance shall be removed by wire brushing or blast of air.  Concrete surface shall be blown off by compressed air before commencing grouting.  Grouting shall be done in one continuous operation from one side such that grout flows in a single wave until grout reaches all confined spaces with no air pockets and air form all confined spaces is expelled.  A hydro static head of 150 mm shall be maintained during grouting operations.  All grouting shall be carried out in the presence of the EIC’s representative.  All lines and levels shall be checked up after grout is set.  Block outs shall be closed using cement concrete of the same grade as that of the parent structure.

3.	Records, Procedures and Reports

3.1.	The Contractor shall maintain records pertaining to the quality of installation / erection work and inspection, testing, compliance with all technical requirements in respect of all his works as described in the previous paragraphs.  The reporting formats shall be in the approved formats.  The contractor shall submit such records to the Engineer after the completion of any particular work before submitting the bill of supply / progress of work.  Such report shall comprise shop inspection reports, shop testing reports, material test reports, based on which dispatch clearances are provided, all the quality control reports of welding, erection and alignment records.

3.2.	All the above mentioned records shall be submitted in the final form duly countersigned by the EIC’s representative attesting conformity to specifications and his approval of installation, and duly incorporating all the additions, alternations, and information as required by the EIC on the basis of preliminary reports giving the progress of the work.  Such records notwithstanding, any records submitted earlier with bill of supply / progress etc. shall be duly bound and submitted to the EIC in six copies by the contractor on his notification of the mechanical completion of erection.

4.	General Preparations before Completion of the Plant

4.1.	The following documents should be completed in accordance with the contract schedule before completion of erection. The Employer and the contractor shall preserve and control these documents in a safe and appropriate place on Site in order the both parties personnel can make use of them at any time.

4.1.1.	Technical Documents

a)	Operation and Maintenance manual

b)	Design documents including the contractor’s design data, drawings and specifications.

c)	Tools and test equipment list

d)	Spare parts list

e)	Lubricant list

4.1.2.	Procedures

a)	Mechanical testing procedure

b)	Electrical testing procedure

c)	Instrumentation testing procedure

d)	Detailed Pre commissioning and commissioning procedure

e)	Detailed Performance Test procedure

4.1.3.	General and Coordination Documents.

a)	Detailed organisation charts for pre commissioning and commissioning showing lines of authorities and responsibility and functions of all key personnel.

b)	The job description of the members of the team.

c)	The scheduled dates of assignment of each member to pre commissioning and commissioning Organisation.

d)	A detailed schedule showing the time sequence which the contractor anticipates to follow for the various steps in completion of erection, pre commissioning and commissioning of each unit and equipment.

e)	The regulations for safety, hygiene and discipline.

f)	The practical organisation of the relationship (meetings, reports, etc.) between the contractor and the Employer at the phases of pre commissioning and commissioning.

g)	Emergency communication route.

4.2.	Manpower

4.2.1.	Required manpower shall be provided as agreed between the contractor and the Employer in a manpower mobilisation plan which shall include the number and qualifications of the operator and maintenance personnel to be furnished by the Employer for the plant.

5.	Completion of Erection

5.1.	The completion of plant under erection by the contractor shall be deemed to occur, if all the units of the plant are structurally and mechanically complete and will include among other such responsibilities the following:

5.1.1.	Plant in the scope of the contract has been erected, installed and grouted as per specifications.

5.1.2.	Installation checks are completed and approved by the EIC.

5.1.3.	The erected plants are totally ready for commissioning checks.

5.2.	At the stage of completion of erection, the contractor shall ensure that all the physical, aesthetic and workmanship aspects are totally complete and the Plant is fit and sound to undergo tests on completion and subsequent pre commissioning checks.

5.3.	Upon achieving the completion as described above the contractor shall notify the EIC by a written notice intimating completion of erection and notify the EIC for inspection. The EIC / EIC’s representative shall proceed with the inspection of such units within 14 days of such a notice.

5.3.1.	The EIC shall certify completion when there are no defaults in the works or

5.3.2.	The EIC shall inform the contractor list of deficiencies for rectification hereinafter referred as Punch list and the contractor shall complete the rectification work within a jointly agreed period before pre commissioning activities and obtain the EIC’s acceptance or approval of the same before proceeding with the same.

5.3.3.	The EIC may inform the contractor that the works are accepted with the ‘Punch’ list (items which do not hamper operability, safety or maintainability) and allow the Contractors to proceed with the pre commissioning checks when the contractor undertakes to complete such outstanding works within an agreed time during defects liability period.  Taking over shall be based on rectification of all deficiencies as advised by Punch lists.

5.4.	The erection period indicated by the contractor would be deemed to cover all the activities up to completion as stipulated in previous paragraphs, notice of completion by the contractor, inspection by the EIC for completion and contractor rectification of all deficiencies as noticed by the deficiency / Punch list, and acceptance by the EIC of such rectification’s prior to tests on completion.

5.5.	Minor defects, which in the opinion of EIC which do not hamper operability and maintainability will not be taken into account for deciding mechanical completion.  Such defects shall be rectified concurrent to commissioning checks before tests on completion.  However, the EIC’s decision in this regard is final.

5.6.	The commissioning period as notified by the contractor shall be deemed to occur beyond the date of completion and shall include all periods of pre commissioning, trials and tests on completion.

5.7.	It is in the contractor’s interest to offer the sections / units / systems progressively under identified milestones within overall erection period, duly completed for rectification of any deficiencies pointed out by the Engineer and to achieve mechanical completion before undertaking the tests on completion within the specified erection period.  The EIC also reserves the right to withhold the cost as estimated to be equivalent to the rectification of deficiencies pointed out to the Contractor until such a time such deficiencies are rectified to the satisfaction of the EIC.

6.	Pre commissioning

6.1.	After the completion of erection, pre commissioning activities listed below shall be carried out to make the plant ready for commissioning. All instruments, materials and provisions necessary for conducting site tests shall be provided by the contractor at his own cost.

6.2.	Upon completion of erection of each piece of equipment, facility or discrete part of the plant, mechanical checks and tests shall be carried out according to the contractor’s check list. The mechanical checks and tests shall be to establish that:

6.2.1.	The Plant is erected in accordance with the contractor’s construction drawings, pipe work drawings, instrument diagrams, etc. issued for the plant.

6.2.2.	The materials are installed and mechanically function in accordance with the contract and

6.2.3.	Applicable codes as listed in the contract are followed for materials and workmanship.

6.3.	Items such as painting, thermal insulation and final clean up which do not materially affect the operation or safety of the Plant will be excluded. All these items shall be listed and completed after pre commissioning or commissioning at the discretion of the contractor but before acceptance.

6.4.	The contractor shall prepare and maintain at site test forms and records which shall include:

6.4.1.	Description of type of test or check

6.4.2.	Date and times of test or check

6.4.3.	Identification of equipment and facilities

6.4.4.	Test pressure, test data and results, including remarks, if any

6.4.5.	Signature of the contractor’s personnel attesting to data recorded, if any, checks, tests and records thereof shall be carried out by the contractors’ construction forces.

6.5.	Wherever the Employer’s witness or attesting of the check or test is required, the Employer’s personnel shall attend such check and test. For this purpose, the contractor shall keep the Employer informed of a day to day test plan schedule. The test plan schedule may be revised from time to time to reflect the actual progress of the work and test.

6.6.	Any items found incomplete or requiring repair or adjustment shall be marked as such on the test records and then reported by the contractor to the Employer and the contractor’s personnel in charge of the relevant construction area.

6.7.	Checking procedures shall be repeated until all the items on the check list are cleared.

6.8.	A complete set of test records shall be handed over to the Employer on completion.

6.9.	The tests on the different mechanical and electrical equipment shall include but not limited to:

7.	Commissioning

7.1.	After the completion of pre commissioning activities the final checks and preparations necessary for start up of the plant shall be carried out. The contractor shall submit to the Employer a written notice of mechanical completion which shall include:

7.1.1.	Identity of a part of the plant considered mechanically complete,

7.1.2.	A copy of all relevant completed test reports,

7.1.3.	The date on which the completion of the tests was achieved,

7.1.4.	Check list and

7.1.5.	A request for issuance of a mechanical completion certificate in respect of that part.

7.2.	Within fourteen (14) days from the date of receipt of the contractor’s written notice, the Employer shall:

7.2.1.	In the case of acceptance, issue a mechanical completion certificate.

7.2.2.	In the case of objection, submit a rejection statement setting forth remaining items to be completed or defects or deficiencies to be corrected before mechanical completion status can be accepted.  When the Employer rejects the contractor’s notice the contractor shall take any necessary action to complete or correct the items marked and give the Employer a second notice of mechanical completion.

7.3.	After the issuance by the Employer of a mechanical completion certificate, commissioning activities listed below shall be carried out to enable the start up and operation of the plant. Procedures are described as below:

7.3.1.	Commissioning Procedure shall be carried out in a methodical sequence as follows

a)	 Warming up

b) Start up

c)	 Initial running

d) Operability adjustment

e)	 Stable operation

f)	 Final adjustment

7.3.2.	At all stages of commissioning sequence, the plant shall be operated at optimum plant conditions. To ensure this, the contractor may make minor adjustment to the conditions indicated in the operation and maintenance manual as necessary.

7.3.3.	The contractor shall check the operating conditions of the plant by constantly monitoring operating data.

7.3.4.	The contractor shall specify for each discrete part of the plant the operational data to be recorded and the manner in which the data is to be taken.

7.3.5.	All the operating data shall be recorded by the Employer on the forms to be mutually agreed. A copy of the operating log and analytical data from initial operation through to the completion of performance test shall be made available by the Employer to the contractor for evaluation.

###### INSTALLATION, TESTING & COMMISSIONING – ELECTRICAL EQUIPMENT

6.1	Equipment Installation, Testing & Commissioning

Installation of Equipment

a)	In accordance with the specific installation instructions, as shown in contractor’s drawings or as directed by the EIC’s representative the contractor shall unload, erect, install, wire, test and place into commercial use of all electrical equipment included in the contract.  Equipment shall be installed in a neat, workmanlike manner so that it is level, plumb, square, and properly aligned and oriented.

b)	The contractor shall furnish all supervision, labour, tools, equipment, rigging materials and incidental materials such as bolts, wedges, anchors, concrete inserts etc. required to completely install, test and adjust the equipment.

c)	Drawings, instructions and recommendations shall be correctly followed in handling, settling, testing and commissioning of all equipment and care shall be exercised in handling to avoid distortion to stationary structures, the marring of finish or damaging of delicate instruments or other electrical parts.

d)	The contractor shall erect and commission the equipment as per the instructions of the EIC representative and shall extend all cooperation to him.

e)	In case of any doubt / misunderstanding as to correct interpretation of drawings or instructions, necessary clarification shall be obtained from the EIC’s representative.  The contractor shall be held responsible for any damage to the equipment consequent to not following instructions correctly.

f)	The contractor shall move all equipment into the respective buildings through regular doors or floor openings provided specifically for the equipment. The contractor shall make his own arrangement for lifting of equipment.

g)	Where assemblies are supplied in more than one section, the contractor shall make all necessary mechanical and electrical connections between sections including the connections between bus bars / wires.  The contractor shall also carry out the adjustments / alignments necessary for proper operation of the circuit breakers.  All insulators and bushings shall be protected against damage during installation.  Insulators or bushings chipped, cracked or damaged due to negligence or carelessness shall be replaced by the contractor at his own expenses.

h)	The contractor shall take utmost care in handling instruments, relays and other delicate mechanisms.  Wherever the instruments or relays are supplied separately, they shall be mounted only after the associated control panels have been erected and aligned. The blocking material / mechanism employed for the safe transit of the instruments and relays shall be removed after ensuring that the panels have been completely installed and no further movement of the same would be necessary.  Any damage to relays and instruments shall be immediately reported to the EIC’s representative.

i)	Inspection, storage, installation, testing and commissioning of transformers shall be in accordance with the latest Indian Standards Code of Practice IS: 10028. All commissioning tests as applicable, vide Appendix B of IS: 10028 (Part II) shall be carried out.

j)	Switchgear control panels shall be installed in accordance with the latest Indian Standard Code of Practice 10118. The switchgear panels shall be installed on finished surface or concrete or steel sills.  The contractor shall be required to install and align any channel sills which form part of the foundations.  Tape or compound shall be applied where called for.  The base of outdoor type units shall be sealed in an approved manner to prevent ingress of moisture.

k)	After installation of all power and control wiring, the contractor shall perform operating tests on all switchgear and panels to verify the proper operation of switchgear / panels and the correctness of the interconnections between various items of equipment.  This shall be done by applying normal ac or dc voltage to the circuits and operating the equipment.  Megger tests for insulation, polarity checks on the instrument transformers, operation tests on equipment, and installation tests shall be carried out by the contractor who shall also make all necessary for proper functioning of the equipment.

l)	Installation and testing of the battery and battery chargers shall be done in strict compliance with the applicable standards.  Each cell shall be inspected for breakage and condition of cover seals as soon as received at site. The battery shall be set up on racks as soon as possible after receipt, utilising lifting devices.  The cells shall not be lifted by the terminals.  Contact surface of the battery terminals and inter cell connectors shall be cleaned, coated with protective grease and assembled.  Each connection shall be properly tightened.  Each cell shall be tested with a hydrometer and thermometer and the results logged.  A freshening charge, if required, shall be added.  When handed over to the Employer, the battery shall be fully charged and the electrolyte shall be at the full level and of the specified specific gravity.

m)	 Equipment furnished with finished coats of paint shall be touched up by the contractor if their surface is spoiled or marred while handling.

r)	Foundation work and grouting in of fixing bolts or channels for all transformers, HT panels will be carried out by the contractor.

6.2	Installation Work for Earthing and Lightning Protection System

a)	The Contractor shall install copper /steel conductors, braids, etc. required for the system and individual equipment earthing.  All work such as cutting, bending, supporting, painting / coating, drilling, brazing /soldering / welding, clamping, bolting and connecting onto structures, equipment frames, terminals, rails or other devices shall be in the contractor’s scope of work.  All incidental hardware and consumables such as fixing cleats / clamps, anchor fasteners, lugs, bolts, nuts, washers, bituminous compound, welding rods, anti corrosive paint as required for the complete work shall be deemed to be included by the contractor as part of the installation work.

b)	The quantities, sizes, material of earthing conductors and electrodes to be installed as per requirement. Routes of the conductors and locations of electrodes shall be as shown on the project drawings.

c)	The work of embedment of earthing conductor in RCC floors / walls along with provision of earth plate inserts / pads / earth risers shall be done by the civil contractor when the floors are cast or during construction of walls.  However when required to do so in those areas where flooring will be done after the Contractor is at site, the Contractor shall coordinate with civil contractor and shall install the earthing conductors before the commencement of the concrete work.  In such cases the contractor’s scope of installation shall include laying the conductors in position with 50 mm concrete cover, making welded connections to inserts / pads / risers above the floor near the equipments.  The embedded conductors shall be connected to reinforcing rods wherever necessary.

d)	If the tap connections (earthing leads) from the floor embedded main earthing grid to the equipment are more than 500 mm long then the same shall be embedded in floor by the Contractor where required, together with associated civil work such as excavation / chipping, concreting and surfacing, if not already done by the civil contractor.  The concrete cover over the conductor shall not be less than 50 mm.

e)	Installation of earth conductors in outdoor areas, buried in ground, shall include excavation of earth up to 600 mm deep 450 mm wide, laying of conductors at 600 mm depth, brazing / welding as required, of main grid conductor joints as well as risers of length 500 mm above ground at required locations and then backfilling material to be placed over buried conductor shall be free from stones and other harmful mixtures.  Back fill shall be placed in layers of 150 mm, uniformly spread along the ditch, and tampered utilising pneumatic tampers or other approved means.  If the excavated soil is found unsuitable for backfilling, the contractor shall arrange for suitable material from outside.

f)	Installation of earth connection leads to equipment and risers on steel structures / walls shall include laying the conductors, welding / cleating at specified intervals, welding / brazing to the main earth grids risers, bolting at equipment terminals and coating welded / brazed joints by bituminous paint.  Galvanized conductors shall be touched up with zinc rich paint where holes are drilled at site for bolting to equipment / structure.

g)	Electrodes shall be installed (a) directly in earth or (b) in constructed earth pits, and connected to main buried earth grid, The scope of work shall include excavation, construction of the earth pits including all materials required for construction of earth pits, placing the rod and fixing test links on those pipe / rod / plate electrodes in test pits and connecting to main earth conductors.

h)	Installation of lightning conductors on the roofs of buildings shall include laying, anchoring, fastening and cleating of horizontal conductors, grouting of vertical rods wherever necessary, laying fastening / cleating / welding of the down comers on the walls/columns of the building and connection to the test links to be provided above ground level.

i)	Installation of the test links shall include mounting of the same at specified height on wall/column by suitable brackets and connections of the test link to the earth electrode.

j)	Whenever main earthing conductor crosses cable trenches, they shall be buried below the trench floor.

k)	Suitable earth risers shall be provided above finished floor / ground level.  If the equipment is not available at time of laying of the main earth conductors. The minimum length of such riser inside the building shall be 200 mm and outdoors shall be 500 mm above ground level.  The risers to be provided will be marked in project drawings.

l)	Earth leads and risers between equipment earthing terminals and the earthing grid shall follow as direct and short a path as possible.

m)	An earthing mat shall be provided under each operating handle of the isolator and operating mechanism of H.V. breakers.  Operating handle of the isolator and supporting structure shall be bonded together by a flexible connection and connected to the earthing grid.

n)	A separate earth electrode bed shall be provided adjacent to structure supporting lightning arrestors.  Each connection shall be as short and as straight as practicable.  For arrestors mounted near transformers, earth conductors shall be located clear off the tank and coolers.

o)	Wherever earthing conductors passes through walls galvanized iron sleeves shall be provided for the passage of earthing conductor. The pipe ends shall be sealed by the contractor by suitable water proof compound.

6.3	Earthing Connections

a)	All connections in the main earth conductors buried in earth / concrete and connection between main earthing conductor and earth leads shall be of welded type.

b)	Connection between earth leads and earthing terminal provided on the equipment shall be bolted type.

c)	All bimetallic connections shall be treated with suitable compound to prevent moisture ingression.

d)	Metallic conduits and pipes shall be connected to the earthing system.

e)	Lightning protection system down conductors shall not be connected to other earthing conductors above ground level.  Also no intermediate earthing connection shall be made to lightning arrester and transformer earthing leads which shall be directly connected to pipe electrode.

6.4		Earth Electrodes

- Electrodes shall as far as practicable be embedded below permanent moisture level.

- Test pits with concrete covers shall be provided for periodic testing of earth resistance. Installation of pipe electrodes in test pits shall be suitable for watering.  The necessary materials required for installation of test pits shall be supplied and installed by contractor.  The installation work shall also include civil work such as excavation and connection to main earth grid.

- Earth pits shall be treated with salt and charcoal if average resistivity of soil is more than 20 ohm metre.

- Soil, salt and charcoal placed around the electrode shall be finely graded, free from stones and other harmful mixtures.  Back fill shall be placed in layers of 250 mm thick uniformly spread and compacted. If excavated soil is found unsuitable for backfilling, the contractor shall arrange for a suitable soil from outside.

6.5	Lightning Protection System

a)	The lightning protection air termination rods and/or horizontal air termination conductors shall be fixed in such a way that they remain in their installed position even during severe weather conditions.  The necessary accessories such as cleats, clamps, welding materials, bolts, nuts, shall be supplied by contractor.

b)	Air termination systems shall be connected to earthing system by down conductors as shown in project drawings.  The down conductors shall follow a direct path to earth.  There shall not be any sharp bends, turns and kinks in the down conductors.

c)	All joints in the down conductors shall be of welded type.  All metallic structure within 2 metres of down conductors shall be bonded to lightening protection system.

d)	Every down conductor shall be provided with a ‘test link’ at about 1000 mm above ground level housed in a suitable GI enclosure made of adequate thickness steel sheet and hot dip galvanised.  The test joint shall be directly connected to the earthing system electrode.

e)	The lightning protection system shall not be in direct contact with underground metallic service ducts, cables, cable conduits and metal enclosures of electrical equipment.  However, all metal projections, railings, vents, tanks, etc. above the roof shall be bonded together to form a part of roof grid.

6.6	Installation of Cable Racks and Trays

a)	Lines and grade for trays may be measured from building steel and finished floor elevations.  Change in line or grade, or the addition of offsets by means of cutting standard tray sections and inserting additional tray fittings to match with the existing arrangement shall be considered as a normal part of the work.

b)	Where embedded steel inserts in concrete floors / walls for welding the supports for cable racks / trays are not available, Contractor shall provide suitable anchor fasteners at no extra cost.

c)	Cable shall be clamped to the cable trays at regular intervals.

d)	Flexible metallic conduits shall be used for termination of connection to equipment such as motors, limit switches and other apparatus.

6.7      Installation of Cables

a)	The installation of cable shall be on tray and other support as per standard engineering practice.

b)	The contractor shall install, test and commission the cables specified in the specification in accordance with drawings and instructions issued by the EIC’s representative. Cables shall be laid directly buried in earth, on cable racks, in built up trenches, on cable trays and supports, in conduits and ducts or bare on walls, ceiling etc. as per drawings.  Contractor’s scope of work includes unloading, laying, fixing, jointing, bending, and termination of the cables.  The contractor shall also supply the necessary materials and equipment required for jointing and termination or the cables.

c)	All apparatus, connections and cable work shall be designed and arranged to minimise risk of fire and any damage which might be caused in the event of fire.  Wherever cables pass through floor or wall openings or other partitions, suitable bushes of an approved type shall be supplied and put into position by the contractor.

d)	Standard cable grips and reels shall be utilised for cable pulling. If unduly difficult pulling occurs, the contractor shall check the pull required and suspend pulling until further procedure has been approved by the EIC’s representative.  The maximum pull tension shall not exceed the recommended value for the cable measured by the tension dynamometer.  In general, any lubricant that does not injure the overall covering and does not set up undesirable conditions of electrostatic stress or electrostatic charge may be used to assist in the pulling of insulated cables in conduits and ducts.

e)	After pulling the cable, the contractor shall record cable identification with date pulled neatly with waterproof ink in linen tags. Identification tags shall be attached securely to each end of each cable with non corrosive wire.  The said wire must be non ferrous material on single conductor power cable.  Tags shall further be attached at intervals on long runs of cables on cable trays and in pull boxes.  Cable and joint markers and RCC warning covers shall be provided wherever required.

All cables shall be allocated a unique number which shall be fixed to each end of the cable using a corrosion resistant label.  Cables of different categories shall be tagged with the following subscripts and three digit numbers.

| LV power | P |
| --- | --- |
| Control | C |
| Instrumentation | I |
| Protection | PR |

- Sharp bending and kinking of cables shall be avoided.  The bending radii for various types of cables shall not be less than those specified below:

| 650 / 1100 V PVC insulated | 12 times the overall armoured cables dia of the cable |
| --- | --- |

If shorter radius appears necessary, no bend shall be made until clearance and instructions have been received from the EIC’s representative.

g)	Power, control and instrumentation cables shall be laid in separate cable racks / trays.

h)	Where groups of HV, LV and control cables are to be laid along the same route, suitable barriers to segregate them physically shall be provided.

i)	Cables of different categories shall be installed so as to maintain satisfactory clearances for safety and in order to reduce the possibility of electrical interference.  The following table gives the distances in mm that shall be maintained between the different categories of cable.

| Cable Category | HV Power | LV Power | C & I Protection |
| --- | --- | --- | --- |
| LV Power | 275 | N/A | 275 |
| C & I / Protection | 550 | 275 | N/A |

j)	Where cables cross roads and water, oil, gas or sewage pipes, the cables shall be laid in reinforced spun concrete or steel pipes.  For road crossings the pipe for the cables shall be buried at no less than one metre depth.

k) Cables laid in ground shall be laid on a 50 mm riddled earth bed.  The cables shall then be covered on top and at their sides with riddled earth of depth of about 150 mm.   This is then gently filled up to a depth of about 100 mm above the top of uppermost cable to provide bedding for the protective cable covers which are placed centrally over the cables. The protective cable covers for LV cables may be of earthenware and for HV cables of reinforced concrete.  The RCC covers shall have one hole at each end, to tie them to each other with GI wires to prevent displacement.  The trench is then backfilled with the excavated soil and well rammed in successive layer of not more than 300 mm in depth, with the trenches being watered to improve consolidation wherever necessary. To allow for subsidence, it is advisable to allow a crown of earth not less than 50 mm in the centre and tapering towards the sides of the trench.

l)	In each cable run some extra length shall be kept at a suitable point to enable one or two straight through joints to be made, should the cable develop a fault at a letter date.

m) Cables on cable racks, on cable trays and conduits shall be formed to avoid bearing against edges of trays, racks, conduits or their supports upon entering or leaving trays, racks or conduits.  Cables shall be racked or laid directory into cantilevered cable trays where practicable, but in some cases it may be necessary that cables are pulled or threaded into trays.  To facilitate visual tracing, cables in trays shall be laid only in single layers and unnecessary crossing of cables shall be avoided.  Cables on trays shall finally be clamped in an approved manner.

n) Cable splices will not be permitted except where permitted by the EIC’s representative.  Splices shall be made by contractor for each type of wire or cable in accordance with the instructions issued by cable manufacturer’s and the EIC’s representative. Before splicing, insulated cables shall have conductor insulation stepped and bound or pencilled for recommended distance back from splices to provide a long leakage path. After splicing, insulation equal to that on the spliced conductors shall be applied at each splice.

o) Jointing of cables shall be in accordance with relevant Indian Standards Codes of Practice.  Materials and tools required for cable jointing work, including cold setting bituminous compound shall be supplied by the contractor.  Cables shall be firmly clamped on either side of a straight through joint at a distance of not more than 300 mm away from the joints.  Identification tags shall be provided at each joint at all cable terminations.

p) At cable terminal points where the conductor and cable insulation will be terminated, terminations shall be made in a neat, workmanlike and approved manner by men specialised in this class of work.

q) Control cable termination shall be made in accordance with wiring diagrams, using colour codes established by the EIC’s representative for the various control circuit, by code marked wiring diagram.

r)	 When control cables are to be fanned out and cabled together with cord, the contractor shall make connections to terminal blocks, and test the equipment for proper operation before cables are corded together. If there is any question as to the proper connection, the contractor shall make a temporary connection with sufficient length of cable so that the cable can be switched to another terminal without splicing.  After correct connections are established through operating the equipment, cables shall be cut to their correct lengths, connected to terminals in the specified manner, and corded together where necessary to hold them in place in a workmanlike manner.

s)	 Cable seals shall be examined to ascertain if they are intact and that cable ends are not damaged.  If the seals are found to be broken the cable ends shall not be jointed until after due examination and testing by the EIC’s representative. Insulation resistance of both sections of cables to be jointed shall be checked by megger before jointing is commenced.

t)	After installation and alignment of motors, the contractor shall complete the conduit installation, including a section of flexible conduit between motor terminal box and trench / tray.  The contractor shall install and connect the power, control and heater supply cables as per equipment manufacturer’s drawings, if any.

u) Metal sheath and armour of the cable shall be bonded to the earthing system of the station.  The size of conductor for bonding shall be appropriate with the system fault current

DATA SHEETS

| Sr. No. | Particular |  | Details | Confirm/Data to be filled by the bidder |
| --- | --- | --- | --- | --- |
| 1.0 | General: |  |  |  |
| 1.1 | Make |  | As per Approved vendor list |  |
| 1.2 | Model and Type no. |  | Pl. furnish |  |
| 1.3 | Design Ambient temperature |  | 50°C |  |
| 1.4 | Atmosphere |  | Corrosive, Humid, Dusty |  |
| 1.5 | Location |  | Indoor/Outdoor |  |
| 1.6 | Degree of Protection |  | IP-5X |  |
| 2.0 | Electrical Data: |  |  |  |
| 2.1 | Type of breaker |  | Vacuum Circuit Breaker |  |
| 2.2 | Service |  | Continuous |  |
| 2.3 | Voltage |  | 11kV+10% |  |
| 2.4 | System Earthing |  | Solidly earthed |  |
| 2.5 | Frequency |  | 50Hz.+5%to-5% |  |
| 2.6 | No. of phase |  | 3 |  |
| 2.7 | System fault level |  | 350MVA |  |
| 2.8 |  | Rated short time current | 18.37kA(1sec.) |  |
| 2.9 |  | Max. system voltage | 12kV |  |
| 2.10 |  | Auxiliary supply: (Battery backup Power Pack required) | 110V D.C derived from Power Pack connected on 110V AC P.T. supply. |  |
| 2.11 |  | Making capacity | 46KA(peak) |  |
| 2.12 |  | Busbar material and current rating | Aluminum and As per approved CDR |  |
| 2.13 |  | Cable entry | Bottom |  |
| 2.14 |  | Cable size | 3C , XLPE armoured cable (UE) ,size as per approved CDR |  |
| 2.15 |  | Breaker particulars: |  |  |
|  |  | (a)Operating duty | Pl. furnish/show catalogue /IS |  |
|  |  | (b)Operatingmechanism | Motor charged spring /manual trip and close |  |
|  |  | (c)Spring charging motor | 230VAC,200W |  |
|  |  | (d)Trip/Closing coil | 110VDC,180W |  |
|  |  | (e) Anti pumping feature/relay | Required. |  |
|  |  | (f)Latching requirement | Trip free |  |
|  |  | (g) Emergency trip push button | Required. |  |
|  |  | (h)Space heater and cubicle lamp | Required. |  |
| 2.16 |  | Constructional requirements |  |  |
|  |  | (a) Thickness of sheet steel for frame, enclosure, doors, covers and partitions | CRCA sheet- 2mm, hinge type door with neoprene rubber gasket |  |
|  |  | (b)Colour | Epoxy powder coating Light Gray RAL 7035 or Two coats epoxy primer and two coats of epoxy paint Shade631asperIS:5 |  |
|  |  | (c)Earth bus size | 50x6mmGI Strip/Cu |  |
|  |  | (d)Foundation frame | ISMC-100, Suitable for three breakers or as per BOQ, with necessary bed plate and foundations bolt. |  |
|  |  | (e)Overall dimension | Provide dimensions |  |
|  |  | (f)Overload of equipment | Provide as per tender |  |
|  |  | (g)Minimum clear space required (i)front side as well as (ii)rear side | Provide dimensions |  |
| 2.17 |  | Annunciation Provided | To be Provided as per tender |  |
| 2.18 |  | Relays | As per Specifications |  |
|  |  | (a)Relay no. and detail | Shall be as per tender |  |
|  |  | (b)Type of relay | Shall be as per tender |  |
|  |  | (c)Make of relay | Shall be as per tender |  |
|  |  | (d)Model no of relay | Provide details |  |
| 2.19 |  | Current Transformer |  |  |
|  |  | (a)Type of CT | Cast Resin |  |
|  |  | (b)Accuracy class | Provide details as per tender |  |
|  |  | (c)VA burden | Provide details as per tender |  |
|  |  | (d)CT ratio | Provide details as per tender |  |
| 2.20 |  | Potential Transformer |  |  |
|  |  | (a)Type of PT | Cast Resin |  |
|  |  | (b)Accuracy class | Provide details as per tender |  |
|  |  | (c)VA burden | Provide details as per tender |  |
|  |  | (d)PT ratio | Provide details as per tender |  |
| 2.21 |  | Panel Accessories |  |  |
| 1 |  | Toggle switch for space heater and socket | 230VA.C,6A |  |
| 2 |  | (b)Socket | 6pin5/15AwithDPMCB |  |
| 3 |  | (c)MCB for spring charging motor circuit | 6A, DPMCB |  |
| 4 |  | (d)MCB for ON/OFF | Doublepole,16A,110V D.C for D.C ckt. Doublepole,16A,230V A.C forA.C ckt. |  |
| 5 |  | Local / Remote selector switch | 4 ways, 2 positions, lock able in any position, angular movement, stay put, lever type handle. |  |
| 6 |  | Trip–Neutral–Close (TNC) Switch. | 6ways, 3position, spring return to neutral, angular movement, lockable pistol grip type handle. |  |
| 7 |  | Space Heater | 230 VA.C , 100 W (LT Supply from LT Panel) |  |
| 8 |  | Limit switch for test and service position. | Required |  |

| POWER, CONTROL & INSTRUMENTATION CABLES |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Sr. No. |  | Description |  |  | Unit |  | Particulars |  | Bidder to Specify |  |
| 1 |  | 11 kV (E), Stranded Aluminium XLPE insulated, inner & outer extruded PVC sheathed, G I flat / strip armoured heavy duty power cable |  |  | LS |  | As per Tender Specifications of Required Core, Size & Amperage |  |  |  |
| 1.1 |  | Make |  |  |  |  | As per Vendor List |  |  |  |
| 1.2 |  | Applicable Standards |  |  |  |  | As per IS 7098 Part – II |  |  |  |
| 2 |  | 1.1 kV Grade, Stranded Aluminium XLPE insulated, inner & outer extruded PVC sheathed, G I flat / strip armoured heavy duty power cable |  |  | LS |  | As per Tender Specifications of Required Core, Size & Amperage |  |  |  |
| 2.1 |  | Make |  |  |  |  | As per Vendor List |  |  |  |
| 2.2 |  | Applicable Standards |  |  |  |  | As per IS 7098 Part – I |  |  |  |
| 3 |  | 1.1 KV, Flat PVC sheathed Copper Submersible Cable (for Drain Pump) |  |  | LS |  | As per Tender Specifications of Required Core, Size & Amperage |  |  |  |
| 3.1 |  | Make |  |  |  |  | As per Vendor List |  |  |  |
| 3.2 |  | Applicable Standards |  |  |  |  | As per IS 694 |  |  |  |
| 4 |  | Cable Accessories |  |  |  |  |  |  |  |  |
| 4.1 |  | Cable Gland |  |  |  |  | Double Compression Brass type to suit the size of cable & of required MOC |  |  |  |
| 4.2 |  | Cable Lugs |  |  |  |  | Crimping type to suit the size of cable & of required MOC |  |  |  |
| 4.3 |  | Cable Accessories |  |  |  |  | To be provided as per specifications & requirements |  |  |  |
| EARTHING AND LIGHTNING PROTECTION SYSTEM |  |  |  |  |  |  |  |  |
| Sr. No. |  | Description | Unit |  | Particulars |  | Bidder to Specify |  |
| 1 |  | Main Earthing Grid |  |  | To suit as per maximum S. C. rating & design criteria |  |  |  |
| 2 |  | Conductor leads to Equipment |  |  | Minimum 2 distinct earthing leads for equipment having > 125 V & 1 earthing lead for equipment |  |  |  |
| 3 |  | Other Items |  |  |  |  |  |  |
| 3.1 |  | Main Lighting D.B, Control Panels and Sub Lighting Distribution Boards | LS |  | GI, 25 x 6 mm |  |  |  |
| 3.2 |  | Hand Rails | LS |  | GI, 25 x 3 mm |  |  |  |
| 3.3 |  | Cable Trays | LS |  | GI, 25 x 3 mm |  |  |  |
| 3.4 |  | Tanks | LS |  | GI, 25 x 3 mm |  |  |  |
| 3.5 |  | Street lighting, flood lighting poles and junctions’ boxes, | LS |  | GI wire, 8 SWG |  |  |  |
| 3.6 |  | Lighting Fixtures, Single Phase Receptacles, Lighting Conduits | LS |  | GI wire, 12 SWG |  |  |  |
| 3.6 |  | Push Button Stations, Limit Switches | LS |  | GI wire, 12 SWG |  |  |  |
| 3.7 |  | Crane rail, | LS |  | GI, 25 x 3 mm |  |  |  |
| 3.8 |  | Metallic Non-Current Carrying Structures | LS |  | GI, 25 x 3 mm |  |  |  |
| 4 |  | Lightning Conductors | LS |  |  |  |  |  |
| 4.1 |  | Lightning Protection Down Comers for Building | LS |  | GI, 25 x 6 mm |  |  |  |
| 4.2 |  | Lightning Protection Horizontal Roof Conductor for Building | LS |  | GI, 25 x 6 mm |  |  |  |
| 5 |  | Earth Electrodes |  |  |  |  |  |  |
| 5.1 |  | Pipe in Pipe Technology (Earth Pit | Min. 14 |  | Pipe in pipe outer dia. |  |  |  |

|  | of Minimum bore dia. of 150 mm) | No. | 50 mm & inner dia. 25 mm with GI pipe 2000 mm long with back filling compound minimum 25 Kg per each job as per relevant IS for two pole structure with transformer with Gate + Fencing, HV & LV MCC-APFC Panels & Motors etc. |  |
| --- | --- | --- | --- | --- |
| 5.2 | Maintenance Free UL Listed Earthing System | Min. 08 Nos. | Copper bonded rod 17.2 mm dia. with 3000 mm length & minimum copper bonding of 0.25 mm with 95% Carbon based earth enhancement material of 30 Kg for each job with pit cover as per relevant IS for LA of two pole structure and transformer neutral with copper strip of 25 x 6 mm. |  |
| 5.3 | Maintenance Free UL Listed Earthing System | 01 No. | Copper bonded rod 17.2 mm dia. with 3000 mm length & minimum copper bonding of 0.25 mm with 95% Carbon based earth enhancement material of 30 Kg for each job with pit cover as per relevant IS for Instrumentation Panels with copper strip of 25 x 6 mm. |  |
| 6 | Earthing Resistance to be achieved |  | As per IEEE Std. 80 - 2000 |  |
| 6.1 | Transmission substation | Ohm | ≤1 |  |
| 6.2 | Distribution substation | Ohm | ≤5 |  |

APPROVED VENDOR LISTS

(Electrical Items)

- The make of HT panel-VCB shall be GETCO approved only.

- The lists of approved vendors as prevailing on the date of submission of the BID will hold true. However subsequent addition / deletion in above vendors’ lists by the competent authority of GETCO shall also be applicable at the time of approval of QAPs. However, decision of the competent authority of GWSSB shall be final & binding in this regard.