| Sl. no. | Item code | Specification | Unit | Qty | Quoted Make |
| --- | --- | --- | --- | --- | --- |
| 1 | 661021510C | DRAKE TO DRAKE WEDGE CONNECTOR C Type Wedge Connector suitable for DRAKE to DRAKE ACSR Conductor conforming to Technical Specifications: 1.Technical specification:- Conductor Compatibility; : ACSR Drake 26/7, 795 kcmil ( Drake; Diameter ≈ 28.14 mm). Type; C-Type Wedge Connector. Application; jumper connection (Drake → Drake). Conductor Size Range; 795-795 (26/7 ACSR equivalent). Material – Connector Body; High-conductivity aluminium alloy (Al 6101-T6 or Al 6061-T6). Material – Wedge Insert; Tempered aluminium alloy or compatible high-strength alloy. Surface Finish; Oxide-inhibiting grease coating / anti-corrosion finish. Electrical Performance; Contact resistance ≤ 50 µΩ; no significant increase after 500 current cy cycles. Mechanical Strength; ≥ 95 % of conductor rated tensile strength (RTS). Temperature Rating; –10 °C to +90 °C continuous operation. Installation; Wedge driven by hand tool. Corrosion Resistance; Must pass 30-day salt spray & thermal cycling test per ANSI C119.4. Standards Compliance; ANSI C119.4 (Class AA, Class 3), IS 5561, BS 3288 Part 1. 2. MODEL:-QW-C-795-795 / C-Type Drake-Drake / Equivalent 3. MAKE:- SUN ELECTRIC (QuickWej)(India) / AMP/ UTILEX / RAYCHEM RPG / VOLTAMPZ / ROX. For ACSR 795 MCM (Drake) to Drake connection; tested per IS 5561 / ANSI C119.4. | Nos | 50 |  |
| 2 | 664070811V | 4 HOLE PADDLE 4 HOLE UNDRILLED PADDLE ,SUITABLE FOR CONNECTING ACSR DRAKE CONDUCTOR ALONG WITH C-CLAMP . 1. Technical Specifications Parameter; Specification / Requirement. Conductor Compatibility; ACSR Drake – 26/7, 795 kcmil (Dia. ≈ 28.14 mm). Type; 4-Hole Undrilled Paddle / Flat Terminal Pad. Material; High-conductivity aluminum alloy (Al 6101-T6 / Al 6061-T6 or equivalent). Finish; Smooth, burr-free surface; optionally tinned or anti-oxidation coated. Thickness; Typically 12 mm – 16 mm (as per system rating). Width x Length; As per 4-hole NEMA spacing or project-specific drawing (e.g., 50 mm hole pitch). Holes; 4 holes (undrilled) – to be drilled per site bolt pattern or NEMA pad dimensions. Hole Diameter (after drilling); Normally 13 mm – 14 mm for M12 bolts (or per site requirement). Bolt Spacing; Standard NEMA 2" × 1.75" (or per equipment terminal requirement). Current Carrying Capacity; ≥ 1000 A continuous (suitable for ACSR Drake conductor). Operating Temperature; –10 °C to +90 °C continuous. Tensile Strength; ≥ 250 MPa (Al 6101-T6). Surface Flatness; ≤ 0.3 mm deviation across pad face. Corrosion Resistance; Must withstand 30 days salt-spray test; no pitting or discoloration. Connection Method; Paddle connected to conductor using approved aluminum C-Clamp (QuickWej / Burndy / Hubbell). Standards Compliance; IS 5561 / IEC 61238-1 / ANSI C119.4 / BS 3288 Part 1. Marking; Manufacturer name, batch no., and conductor size (“Drake 795 ACSR”). Service Life; ≥ 20 years outdoor duty. Model / Series: QW-PAD-795-4H / Equivalent 2. Manufacturer/make: SUN ELECTRIC (QuickWej)(India) / AMP/ UTILEX / RAYCHEM RPG/ VOLTAMPZ / ROX Description / Notes: 4-Hole aluminum paddle for ACSR 795 Drake; undrilled, clamp-type termination | Numbers | 50 |  |

Note: Bidders should compulsorily mention the make they will supply in the Quoted Make column.

-Sd-

Executive Engineer (MSP) Jog,

Karnataka Power Corporation Ltd

Jogfalls-577435